## Revisions
Rev No. | Date | Model No. | Description | 84-YR Avg MWH | Δ MWH | Δ MWH | Δ MWH | Δ MWH | Δ MWH
0 | 2018-01-22 | 1 | Updated Uncalibrated Model to 2018 | 992.0525
0 | 2018-01-22 | 2 | Calibrated model, existing plant | 834 | -52
0 | 2018-01-22 | 2a | Model existing plant, new License | 782 |  | 546.3015 |  | 573 | -52
0 | 2018-01-22 | 3 | Model upgraded plant | 1407 | -78.6985
0 | 2018-01-22 | 3a | Model upgraded plant, new License | 1328.3015 |  |  |  | 546
0 | 2018-01-22 |  | Model upgraded plant, new License | Refined formatting | 782
Formulas:
Date = [Date, row above]

## Environmental Flows
Month | Flow (CFS)
1 | 5
2 | 5
3 | 25
4 | 25
5 | 25
6 | 25
7 | 5
8 | 5
9 | 15
10 | 15
11 | 15
12 | 5

## Head Water Tail Water
Flow (CFS) | Head Water | Tail Water | Gross H (FT) | Equation
0 | 230 | 200 | 30 | 30 | 0.2
100 | 230.2 | 200.4 | 29.8 | 29.8
200 | 230.4 | 200.8 | 29.6 | 29.6
300 | 230.6 | 201.2 | 29.4 | 29.4
400 | 230.8 | 201.6 | 29.2 | 29.2
500 | 231 | 202 | 29 | 29
600 | 231.2 | 202.4 | 28.8 | 28.8
700 | 231.4 | 202.8 | 28.6 | 28.6
800 | 231.6 | 203.2 | 28.4 | 28.4
900 | 231.8 | 203.6 | 28.2 | 28.2
1000 | 232 | 204 | 28 | 28
1100 | 232.2 | 204.4 | 27.8 | 27.8
1200 | 232.4 | 204.8 | 27.6 | 27.6
1300 | 232.6 | 205.2 | 27.4 | 27.4
1400 | 232.8 | 205.6 | 27.2 | 27.2
1500 | 233 | 206 | 27 | 27
1600 | 233.2 | 206.4 | 26.8
1700 | 233.4 | 206.8 | 26.6
1800 | 233.6 | 207.2 | 26.4
1900 | 233.8 | 207.6 | 26.2
2000 | 234 | 208 | 26
2100 | 234.2 | 208.4 | 25.8
2200 | 234.4 | 208.8 | 25.6
2300 | 234.6 | 209.2 | 25.4
2400 | 234.8 | 209.6 | 25.2
2500 | 235 | 210 | 25
2600 | 235.2 | 210.4 | 24.8
2700 | 235.4 | 210.8 | 24.6
2800 | 235.6 | 211.2 | 24.4
2900 | 235.8 | 211.6 | 24.2
3000 | 236 | 212 | 24
3100 | 236.2 | 212.4 | 23.8
3200 | 236.4 | 212.8 | 23.6
3300 | 236.6 | 213.2 | 23.4
3400 | 236.8 | 213.6 | 23.2
3500 | 237 | 214 | 23
3600 | 237.2 | 214.4 | 22.8
3700 | 237.4 | 214.8 | 22.6
3800 | 237.6 | 215.2 | 22.4
3900 | 237.8 | 215.6 | 22.2
4000 | 238 | 216 | 22
4100 | 238.2 | 216.4 | 21.8
4200 | 238.4 | 216.8 | 21.6
4300 | 238.6 | 217.2 | 21.4
4400 | 238.8 | 217.6 | 21.2
4500 | 239 | 218 | 21
4600 | 239.2 | 218.4 | 20.8
4700 | 239.4 | 218.8 | 20.6
4800 | 239.6 | 219.2 | 20.4
4900 | 239.8 | 219.6 | 20.2
5000 | 240 | 220 | 20
5100 | 240.2 | 220.4 | 19.8
5200 | 240.4 | 220.8 | 19.6
5300 | 240.6 | 221.2 | 19.4
5400 | 240.8 | 221.6 | 19.2
5500 | 241 | 222 | 19
5600 | 241.2 | 222.4 | 18.8
5700 | 241.4 | 222.8 | 18.6
5800 | 241.6 | 223.2 | 18.4
5900 | 241.8 | 223.6 | 18.2
6000 | 242 | 224 | 18
6100 | 242.2 | 224.4 | 17.8
6200 | 242.4 | 224.8 | 17.6
6300 | 242.6 | 225.2 | 17.4
6400 | 242.8 | 225.6 | 17.2
6500 | 243 | 226 | 17
6600 | 243.2 | 226.4 | 16.8
6700 | 243.4 | 226.8 | 16.6
6800 | 243.6 | 227.2 | 16.4
6900 | 243.8 | 227.6 | 16.2
7000 | 244 | 228 | 16
7100 | 244.2 | 228.4 | 15.8
7200 | 244.4 | 228.8 | 15.6
7300 | 244.6 | 229.2 | 15.4
7400 | 244.8 | 229.6 | 15.2
7500 | 245 | 230 | 15
7600 | 245.2 | 230.4 | 14.8
7700 | 245.4 | 230.8 | 14.6
7800 | 245.6 | 231.2 | 14.4
7900 | 245.8 | 231.6 | 14.2
8000 | 246 | 232 | 14
8100 | 246.2 | 232.4 | 13.8
8200 | 246.4 | 232.8 | 13.6
8300 | 246.6 | 233.2 | 13.4
8400 | 246.8 | 233.6 | 13.2
8500 | 247 | 234 | 13
8600 | 247.2 | 234.4 | 12.8
8700 | 247.4 | 234.8 | 12.6
8800 | 247.6 | 235.2 | 12.4
8900 | 247.8 | 235.6 | 12.2
9000 | 248 | 236 | 12

## HeadLoss
Headloss Calculations, f(k*Q2)
Equation | HL =k*Q2
Turbine Flow (CFS) | 0 | 112
HL (FT) | 0 | 0.5
k | 3.986e-05
Check
Turbine Flow (CFS) | 112
HL (FT) | 0.5

## Turbine Efficency
Parameter | English | SI
Site Elevation | 200 | 60.9756
Gross Head | 30 | 9.1463
Net Head | 29 | 8.8415
Min Head | 25 | 7.622
Rated Head | 26.896 | 8.2
Max Gate | 100 | 2.8339
Setting | 2 | 0.60976
Temperature | 80 | 26.6667
| New Propeller |  | As-Is Propeller |  | New Kaplan
| Flow | Eff (%) | Flow | Eff (%) | Flow | Eff (%)
| 56.1072 | 57.14% | 56.1072 | 47.14% | 6.3518 | 40.05%
As-Is efficiency | 65.282 | 66.63% | 65.282 | 56.63% | 13.4093 | 70.08%
adjustment | 74.8096 | 76.68% | 74.8096 | 66.68% | 22.9369 | 80.09%
10% | 80.4556 | 82.3% | 80.4556 | 72.3% | 37.7577 | 87.1%
| 83.9844 | 85.71% | 83.9844 | 75.71% | 45.5209 | 88.6%
| 85.7488 | 87.55% | 85.7488 | 77.55% | 51.5198 | 89.6%
| 87.866 | 89.12% | 87.866 | 79.12% | 59.636 | 90.6%
| 89.6304 | 90.59% | 89.6304 | 80.59% | 69.8694 | 91.6%
| 91.3948 | 91.61% | 91.3948 | 81.61% | 79.7499 | 92.11%
| 93.512 | 92.16% | 93.512 | 82.16% | 85.043 | 92.21%
| 93.512 | 92.16% | 93.512 | 82.16% | 87.1603 | 92.22%
| 95.2764 | 91.97% | 95.2764 | 81.97% | 91.7476 | 92.2%
| 97.0408 | 91.51% | 97.0408 | 81.51% | 96.335 | 92.08%
| 99.158 | 90.78% | 99.158 | 80.78% | 104.804 | 91.77%
| 100.9224 | 89.95% | 100.9224 | 79.95% | 113.273 | 91.43%
| 102.6868 | 88.93% | 102.6868 | 78.93% | 119.6248 | 91.08%
| 106.5684 | 86.81% | 106.5684 | 76.81% | 124.9179 | 90.74%
| 108.3328 | 85.52% | 108.3328 | 75.52% | 132.3283 | 90.08%
| 112.2144 | 82.94% | 112.2144 | 72.94% | 139.3858 | 89.27%

## Energy
Inputs | Min Head | 25 | Min Gate | 6.3518 | Max Gate | 139.3858 |  | Gen Efficency | 94% | Forced Outage Factor | 2% | Transformer Efficency | 98%
Outputs |  | Avg Gross Gen MWH | 1383.0711 |  | Net Gen MWH | 1355.4097 |  | Revenue Gen MWH | 1328.3015
|  | Max kW | 288.5223 |  | Avg kW | 176.9862 |  | Capacity Factor | 53.63%
Year | Month | Day | CFS @ Dam | Environmental Flow | CFS @ Powerhouse | Gross Head (FT) | Turbine Flow | Headloss (FT) | Net Head (FT) | Turbine Eff (%) | Turbine Power (kW) | Generated Power (kW) | Energy (kWH)
1932 | 1 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1932 | 1 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1932 | 1 | 3 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1932 | 1 | 4 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1932 | 1 | 5 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1932 | 1 | 6 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1932 | 1 | 7 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1932 | 1 | 8 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1932 | 1 | 9 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1932 | 1 | 10 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1932 | 1 | 11 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1932 | 1 | 12 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1932 | 1 | 13 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1932 | 1 | 14 | 320 | 5 | 315 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1932 | 1 | 15 | 394.449 | 5 | 389.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1932 | 1 | 16 | 363.102 | 5 | 358.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1932 | 1 | 17 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1932 | 1 | 18 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1932 | 1 | 19 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1932 | 1 | 20 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1932 | 1 | 21 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1932 | 1 | 22 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1932 | 1 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1932 | 1 | 24 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1932 | 1 | 25 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1932 | 1 | 26 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1932 | 1 | 27 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1932 | 1 | 28 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1932 | 1 | 29 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1932 | 1 | 30 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1932 | 1 | 31 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1932 | 2 | 1 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1932 | 2 | 2 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1932 | 2 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1932 | 2 | 4 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1932 | 2 | 5 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1932 | 2 | 6 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1932 | 2 | 7 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1932 | 2 | 8 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1932 | 2 | 9 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1932 | 2 | 10 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1932 | 2 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1932 | 2 | 12 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1932 | 2 | 13 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1932 | 2 | 14 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1932 | 2 | 15 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1932 | 2 | 16 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1932 | 2 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1932 | 2 | 18 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1932 | 2 | 19 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1932 | 2 | 20 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1932 | 2 | 21 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1932 | 2 | 22 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1932 | 2 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1932 | 2 | 24 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1932 | 2 | 25 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1932 | 2 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1932 | 2 | 27 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1932 | 2 | 28 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1932 | 2 | 29 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1932 | 3 | 1 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1932 | 3 | 2 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1932 | 3 | 3 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1932 | 3 | 4 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1932 | 3 | 5 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1932 | 3 | 6 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1932 | 3 | 7 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1932 | 3 | 8 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1932 | 3 | 9 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1932 | 3 | 10 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1932 | 3 | 11 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1932 | 3 | 12 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1932 | 3 | 13 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1932 | 3 | 14 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1932 | 3 | 15 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1932 | 3 | 16 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1932 | 3 | 17 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1932 | 3 | 18 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1932 | 3 | 19 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1932 | 3 | 20 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1932 | 3 | 21 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1932 | 3 | 22 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1932 | 3 | 23 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1932 | 3 | 24 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1932 | 3 | 25 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1932 | 3 | 26 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1932 | 3 | 27 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1932 | 3 | 28 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1932 | 3 | 29 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1932 | 3 | 30 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1932 | 3 | 31 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1932 | 4 | 1 | 953.4694 | 25 | 928.4694 | 28.0931 | 139.3858 | 0.77441 | 27.3187 | 89.27% | 287.8771 | 270.6044 | 6494.5065
1932 | 4 | 2 | 1018.7755 | 25 | 993.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
1932 | 4 | 3 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1932 | 4 | 4 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1932 | 4 | 5 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1932 | 4 | 6 | 613.8776 | 25 | 588.8776 | 28.7722 | 139.3858 | 0.77441 | 27.9978 | 89.27% | 295.0341 | 277.3321 | 6655.97
1932 | 4 | 7 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1932 | 4 | 8 | 1227.7551 | 25 | 1202.7551 | 27.5445 | 139.3858 | 0.77441 | 26.7701 | 89.27% | 282.0964 | 265.1706 | 6364.0938
1932 | 4 | 9 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1932 | 4 | 10 | 875.102 | 25 | 850.102 | 28.2498 | 139.3858 | 0.77441 | 27.4754 | 89.27% | 289.5287 | 272.157 | 6531.7673
1932 | 4 | 11 | 953.4694 | 25 | 928.4694 | 28.0931 | 139.3858 | 0.77441 | 27.3187 | 89.27% | 287.8771 | 270.6044 | 6494.5065
1932 | 4 | 12 | 1724.0816 | 25 | 1699.0816 | 26.5518 | 139.3858 | 0.77441 | 25.7774 | 89.27% | 271.636 | 255.3379 | 6128.1088
1932 | 4 | 13 | 1959.1837 | 25 | 1934.1837 | 26.0816 | 139.3858 | 0.77441 | 25.3072 | 89.27% | 266.6811 | 250.6803 | 6016.3264
1932 | 4 | 14 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1932 | 4 | 15 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1932 | 4 | 16 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1932 | 4 | 17 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
1932 | 4 | 18 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1932 | 4 | 19 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1932 | 4 | 20 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
1932 | 4 | 21 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1932 | 4 | 22 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
1932 | 4 | 23 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1932 | 4 | 24 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1932 | 4 | 25 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1932 | 4 | 26 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1932 | 4 | 27 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1932 | 4 | 28 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1932 | 4 | 29 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1932 | 4 | 30 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1932 | 5 | 1 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1932 | 5 | 2 | 408.8163 | 25 | 383.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
1932 | 5 | 3 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
1932 | 5 | 4 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1932 | 5 | 5 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1932 | 5 | 6 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1932 | 5 | 7 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1932 | 5 | 8 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1932 | 5 | 9 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1932 | 5 | 10 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1932 | 5 | 11 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1932 | 5 | 12 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1932 | 5 | 13 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1932 | 5 | 14 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1932 | 5 | 15 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1932 | 5 | 16 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1932 | 5 | 17 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1932 | 5 | 18 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1932 | 5 | 19 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1932 | 5 | 20 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1932 | 5 | 21 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1932 | 5 | 22 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1932 | 5 | 23 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1932 | 5 | 24 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1932 | 5 | 25 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1932 | 5 | 26 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1932 | 5 | 27 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1932 | 5 | 28 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1932 | 5 | 29 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1932 | 5 | 30 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1932 | 5 | 31 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1932 | 6 | 1 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1932 | 6 | 2 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1932 | 6 | 3 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1932 | 6 | 4 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1932 | 6 | 5 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1932 | 6 | 6 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1932 | 6 | 7 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1932 | 6 | 8 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1932 | 6 | 9 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1932 | 6 | 10 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1932 | 6 | 11 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1932 | 6 | 12 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1932 | 6 | 13 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1932 | 6 | 14 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1932 | 6 | 15 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1932 | 6 | 16 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1932 | 6 | 17 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1932 | 6 | 18 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1932 | 6 | 19 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1932 | 6 | 20 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1932 | 6 | 21 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1932 | 6 | 22 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1932 | 6 | 23 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1932 | 6 | 24 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1932 | 6 | 25 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1932 | 6 | 26 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1932 | 6 | 27 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1932 | 6 | 28 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1932 | 6 | 29 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1932 | 6 | 30 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1932 | 7 | 1 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 7 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1932 | 7 | 3 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1932 | 7 | 4 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1932 | 7 | 5 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1932 | 7 | 6 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1932 | 7 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1932 | 7 | 8 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1932 | 7 | 9 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1932 | 7 | 10 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1932 | 7 | 11 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1932 | 7 | 12 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1932 | 7 | 13 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1932 | 7 | 14 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1932 | 7 | 15 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1932 | 7 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1932 | 7 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1932 | 7 | 18 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1932 | 7 | 19 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1932 | 7 | 20 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1932 | 7 | 21 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1932 | 7 | 22 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1932 | 7 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1932 | 7 | 24 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 7 | 25 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1932 | 7 | 26 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 7 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1932 | 7 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1932 | 7 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1932 | 7 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 7 | 31 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1932 | 8 | 1 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1932 | 8 | 2 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1932 | 8 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 8 | 4 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1932 | 8 | 5 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1932 | 8 | 6 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1932 | 8 | 7 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1932 | 8 | 8 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1932 | 8 | 9 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1932 | 8 | 10 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1932 | 8 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1932 | 8 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1932 | 8 | 13 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1932 | 8 | 14 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1932 | 8 | 15 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1932 | 8 | 16 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1932 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1932 | 8 | 18 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1932 | 8 | 19 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1932 | 8 | 20 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1932 | 8 | 21 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1932 | 8 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1932 | 8 | 23 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1932 | 8 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1932 | 8 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1932 | 8 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1932 | 8 | 27 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1932 | 8 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1932 | 8 | 29 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 8 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1932 | 8 | 31 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1932 | 9 | 1 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1932 | 9 | 2 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1932 | 9 | 3 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1932 | 9 | 4 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1932 | 9 | 5 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1932 | 9 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1932 | 9 | 7 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1932 | 9 | 8 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1932 | 9 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1932 | 9 | 10 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1932 | 9 | 11 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1932 | 9 | 12 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1932 | 9 | 13 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1932 | 9 | 14 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1932 | 9 | 15 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1932 | 9 | 16 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1932 | 9 | 17 | 2442.449 | 15 | 2427.449 | 25.1151 | 139.3858 | 0.77441 | 24.3407 | 89.27% | 256.4961 | 241.1063 | 5786.5515
1932 | 9 | 18 | 1234.2857 | 15 | 1219.2857 | 27.5314 | 139.3858 | 0.77441 | 26.757 | 89.27% | 281.9587 | 265.0412 | 6360.9887
1932 | 9 | 19 | 444.0816 | 15 | 429.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1932 | 9 | 20 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1932 | 9 | 21 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1932 | 9 | 22 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1932 | 9 | 23 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1932 | 9 | 24 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1932 | 9 | 25 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1932 | 9 | 26 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1932 | 9 | 27 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1932 | 9 | 28 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1932 | 9 | 29 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1932 | 9 | 30 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1932 | 10 | 1 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1932 | 10 | 2 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1932 | 10 | 3 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1932 | 10 | 4 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1932 | 10 | 5 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1932 | 10 | 6 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1932 | 10 | 7 | 347.4286 | 15 | 332.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1932 | 10 | 8 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1932 | 10 | 9 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1932 | 10 | 10 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1932 | 10 | 11 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1932 | 10 | 12 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1932 | 10 | 13 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1932 | 10 | 14 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1932 | 10 | 15 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1932 | 10 | 16 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1932 | 10 | 17 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1932 | 10 | 18 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1932 | 10 | 19 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1932 | 10 | 20 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1932 | 10 | 21 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1932 | 10 | 22 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1932 | 10 | 23 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1932 | 10 | 24 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1932 | 10 | 25 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1932 | 10 | 26 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1932 | 10 | 27 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1932 | 10 | 28 | 291.2653 | 15 | 276.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1932 | 10 | 29 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1932 | 10 | 30 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1932 | 10 | 31 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1932 | 11 | 1 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1932 | 11 | 2 | 933.8776 | 15 | 918.8776 | 28.1322 | 139.3858 | 0.77441 | 27.3578 | 89.27% | 288.29 | 270.9926 | 6503.8217
1932 | 11 | 3 | 467.5918 | 15 | 452.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1932 | 11 | 4 | 297.7959 | 15 | 282.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1932 | 11 | 5 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1932 | 11 | 6 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1932 | 11 | 7 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1932 | 11 | 8 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1932 | 11 | 9 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1932 | 11 | 10 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1932 | 11 | 11 | 467.5918 | 15 | 452.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1932 | 11 | 12 | 372.2449 | 15 | 357.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1932 | 11 | 13 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1932 | 11 | 14 | 219.4286 | 15 | 204.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1932 | 11 | 15 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1932 | 11 | 16 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1932 | 11 | 17 | 711.8367 | 15 | 696.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1932 | 11 | 18 | 672.6531 | 15 | 657.6531 | 28.6547 | 139.3858 | 0.77441 | 27.8803 | 89.27% | 293.7954 | 276.1677 | 6628.0244
1932 | 11 | 19 | 574.6939 | 15 | 559.6939 | 28.8506 | 139.3858 | 0.77441 | 28.0762 | 89.27% | 295.8599 | 278.1083 | 6674.6004
1932 | 11 | 20 | 2168.1633 | 15 | 2153.1633 | 25.6637 | 139.3858 | 0.77441 | 24.8893 | 89.27% | 262.2768 | 246.5402 | 5916.9643
1932 | 11 | 21 | 973.0612 | 15 | 958.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1932 | 11 | 22 | 532.898 | 15 | 517.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1932 | 11 | 23 | 372.2449 | 15 | 357.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1932 | 11 | 24 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1932 | 11 | 25 | 279.5102 | 15 | 264.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1932 | 11 | 26 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1932 | 11 | 27 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1932 | 11 | 28 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1932 | 11 | 29 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1932 | 11 | 30 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1932 | 12 | 1 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1932 | 12 | 2 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1932 | 12 | 3 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1932 | 12 | 4 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1932 | 12 | 5 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1932 | 12 | 6 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1932 | 12 | 7 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1932 | 12 | 8 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1932 | 12 | 9 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1932 | 12 | 10 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1932 | 12 | 11 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1932 | 12 | 12 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1932 | 12 | 13 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1932 | 12 | 14 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1932 | 12 | 15 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1932 | 12 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1932 | 12 | 17 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1932 | 12 | 18 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1932 | 12 | 19 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1932 | 12 | 20 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1932 | 12 | 21 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1932 | 12 | 22 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1932 | 12 | 23 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1932 | 12 | 24 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1932 | 12 | 25 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1932 | 12 | 26 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1932 | 12 | 27 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1932 | 12 | 28 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1932 | 12 | 29 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1932 | 12 | 30 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1932 | 12 | 31 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1933 | 1 | 1 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1933 | 1 | 2 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1933 | 1 | 3 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1933 | 1 | 4 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1933 | 1 | 5 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 1 | 6 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 1 | 7 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1933 | 1 | 8 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1933 | 1 | 9 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 1 | 10 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 1 | 11 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 1 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 1 | 13 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 1 | 14 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1933 | 1 | 15 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1933 | 1 | 16 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1933 | 1 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 1 | 18 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1933 | 1 | 19 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1933 | 1 | 20 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 1 | 21 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1933 | 1 | 22 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1933 | 1 | 23 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1933 | 1 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1933 | 1 | 25 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1933 | 1 | 26 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 1 | 27 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1933 | 1 | 28 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1933 | 1 | 29 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 1 | 30 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1933 | 1 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 2 | 1 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1933 | 2 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1933 | 2 | 3 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1933 | 2 | 4 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1933 | 2 | 5 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1933 | 2 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1933 | 2 | 7 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1933 | 2 | 8 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1933 | 2 | 9 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1933 | 2 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 2 | 11 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 2 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1933 | 2 | 13 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1933 | 2 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1933 | 2 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1933 | 2 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1933 | 2 | 17 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1933 | 2 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1933 | 2 | 19 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 2 | 20 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1933 | 2 | 21 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1933 | 2 | 22 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1933 | 2 | 23 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1933 | 2 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1933 | 2 | 25 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1933 | 2 | 26 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1933 | 2 | 27 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1933 | 2 | 28 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1933 | 3 | 1 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1933 | 3 | 2 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1933 | 3 | 3 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1933 | 3 | 4 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1933 | 3 | 5 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1933 | 3 | 6 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1933 | 3 | 7 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1933 | 3 | 8 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1933 | 3 | 9 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1933 | 3 | 10 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1933 | 3 | 11 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1933 | 3 | 12 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1933 | 3 | 13 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1933 | 3 | 14 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1933 | 3 | 15 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1933 | 3 | 16 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1933 | 3 | 17 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1933 | 3 | 18 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1933 | 3 | 19 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1933 | 3 | 20 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1933 | 3 | 21 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1933 | 3 | 22 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1933 | 3 | 23 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1933 | 3 | 24 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1933 | 3 | 25 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1933 | 3 | 26 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1933 | 3 | 27 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1933 | 3 | 28 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1933 | 3 | 29 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1933 | 3 | 30 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1933 | 3 | 31 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1933 | 4 | 1 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1933 | 4 | 2 | 356.5714 | 25 | 331.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1933 | 4 | 3 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1933 | 4 | 4 | 467.5918 | 25 | 442.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1933 | 4 | 5 | 982.2041 | 25 | 957.2041 | 28.0356 | 139.3858 | 0.77441 | 27.2612 | 89.27% | 287.2715 | 270.0352 | 6480.8443
1933 | 4 | 6 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
1933 | 4 | 7 | 1280 | 25 | 1255 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
1933 | 4 | 8 | 1920 | 25 | 1895 | 26.16 | 139.3858 | 0.77441 | 25.3856 | 89.27% | 267.507 | 251.4565 | 6034.9568
1933 | 4 | 9 | 1488.9796 | 25 | 1463.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1933 | 4 | 10 | 1280 | 25 | 1255 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
1933 | 4 | 11 | 1051.4286 | 25 | 1026.4286 | 27.8971 | 139.3858 | 0.77441 | 27.1227 | 89.27% | 285.8125 | 268.6638 | 6447.9306
1933 | 4 | 12 | 757.551 | 25 | 732.551 | 28.4849 | 139.3858 | 0.77441 | 27.7105 | 89.27% | 292.0061 | 274.4858 | 6587.6585
1933 | 4 | 13 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1933 | 4 | 14 | 450.6122 | 25 | 425.6122 | 29.0988 | 139.3858 | 0.77441 | 28.3244 | 89.27% | 298.475 | 280.5665 | 6733.5966
1933 | 4 | 15 | 737.9592 | 25 | 712.9592 | 28.5241 | 139.3858 | 0.77441 | 27.7497 | 89.27% | 292.419 | 274.8739 | 6596.9737
1933 | 4 | 16 | 1123.2653 | 25 | 1098.2653 | 27.7535 | 139.3858 | 0.77441 | 26.9791 | 89.27% | 284.2985 | 267.2406 | 6413.7748
1933 | 4 | 17 | 1920 | 25 | 1895 | 26.16 | 139.3858 | 0.77441 | 25.3856 | 89.27% | 267.507 | 251.4565 | 6034.9568
1933 | 4 | 18 | 3213.0612 | 25 | 3188.0612 | 23.5739 | 0 | 0 | 23.5739 | 0% | 0 | 0 | 0
1933 | 4 | 19 | 3056.3265 | 25 | 3031.3265 | 23.8873 | 0 | 0 | 23.8873 | 0% | 0 | 0 | 0
1933 | 4 | 20 | 1920 | 25 | 1895 | 26.16 | 139.3858 | 0.77441 | 25.3856 | 89.27% | 267.507 | 251.4565 | 6034.9568
1933 | 4 | 21 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
1933 | 4 | 22 | 1201.6327 | 25 | 1176.6327 | 27.5967 | 139.3858 | 0.77441 | 26.8223 | 89.27% | 282.6469 | 265.6881 | 6376.514
1933 | 4 | 23 | 777.1429 | 25 | 752.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1933 | 4 | 24 | 629.551 | 25 | 604.551 | 28.7409 | 139.3858 | 0.77441 | 27.9665 | 89.27% | 294.7038 | 277.0216 | 6648.5178
1933 | 4 | 25 | 757.551 | 25 | 732.551 | 28.4849 | 139.3858 | 0.77441 | 27.7105 | 89.27% | 292.0061 | 274.4858 | 6587.6585
1933 | 4 | 26 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1933 | 4 | 27 | 1029.2245 | 25 | 1004.2245 | 27.9416 | 139.3858 | 0.77441 | 27.1671 | 89.27% | 286.2805 | 269.1037 | 6458.4878
1933 | 4 | 28 | 598.2041 | 25 | 573.2041 | 28.8036 | 139.3858 | 0.77441 | 28.0292 | 89.27% | 295.3645 | 277.6426 | 6663.4221
1933 | 4 | 29 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
1933 | 4 | 30 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
1933 | 5 | 1 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1933 | 5 | 2 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1933 | 5 | 3 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1933 | 5 | 4 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1933 | 5 | 5 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1933 | 5 | 6 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1933 | 5 | 7 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1933 | 5 | 8 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1933 | 5 | 9 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1933 | 5 | 10 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1933 | 5 | 11 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1933 | 5 | 12 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1933 | 5 | 13 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1933 | 5 | 14 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1933 | 5 | 15 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1933 | 5 | 16 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1933 | 5 | 17 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1933 | 5 | 18 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1933 | 5 | 19 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1933 | 5 | 20 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1933 | 5 | 21 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1933 | 5 | 22 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1933 | 5 | 23 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1933 | 5 | 24 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1933 | 5 | 25 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1933 | 5 | 26 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1933 | 5 | 27 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1933 | 5 | 28 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1933 | 5 | 29 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1933 | 5 | 30 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1933 | 5 | 31 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1933 | 6 | 1 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1933 | 6 | 2 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1933 | 6 | 3 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1933 | 6 | 4 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1933 | 6 | 5 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1933 | 6 | 6 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1933 | 6 | 7 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1933 | 6 | 8 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1933 | 6 | 9 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1933 | 6 | 10 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1933 | 6 | 11 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1933 | 6 | 12 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1933 | 6 | 13 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1933 | 6 | 14 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1933 | 6 | 15 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1933 | 6 | 16 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1933 | 6 | 17 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1933 | 6 | 18 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1933 | 6 | 19 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1933 | 6 | 20 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1933 | 6 | 21 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1933 | 6 | 22 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1933 | 6 | 23 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1933 | 6 | 24 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1933 | 6 | 25 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1933 | 6 | 26 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1933 | 6 | 27 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1933 | 6 | 28 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1933 | 6 | 29 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1933 | 6 | 30 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1933 | 7 | 1 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 2 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1933 | 7 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 4 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1933 | 7 | 5 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 6 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1933 | 7 | 7 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 8 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 9 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1933 | 7 | 10 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 11 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 13 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 16 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1933 | 7 | 17 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1933 | 7 | 18 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1933 | 7 | 19 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1933 | 7 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1933 | 7 | 21 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1933 | 7 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1933 | 7 | 23 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1933 | 7 | 24 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1933 | 7 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 26 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1933 | 7 | 27 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1933 | 7 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1933 | 7 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 7 | 30 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 7 | 31 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1933 | 8 | 1 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1933 | 8 | 2 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1933 | 8 | 3 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1933 | 8 | 4 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1933 | 8 | 5 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1933 | 8 | 6 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1933 | 8 | 7 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1933 | 8 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1933 | 8 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1933 | 8 | 10 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1933 | 8 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1933 | 8 | 12 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1933 | 8 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1933 | 8 | 14 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1933 | 8 | 15 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1933 | 8 | 16 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1933 | 8 | 17 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1933 | 8 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1933 | 8 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1933 | 8 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1933 | 8 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1933 | 8 | 22 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1933 | 8 | 23 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1933 | 8 | 24 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1933 | 8 | 25 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1933 | 8 | 26 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1933 | 8 | 27 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1933 | 8 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1933 | 8 | 29 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1933 | 8 | 30 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1933 | 8 | 31 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1933 | 9 | 1 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1933 | 9 | 2 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1933 | 9 | 3 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1933 | 9 | 4 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1933 | 9 | 5 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1933 | 9 | 6 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1933 | 9 | 7 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1933 | 9 | 8 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1933 | 9 | 9 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1933 | 9 | 10 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1933 | 9 | 11 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1933 | 9 | 12 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1933 | 9 | 13 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1933 | 9 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1933 | 9 | 15 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1933 | 9 | 16 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1933 | 9 | 17 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1933 | 9 | 18 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1933 | 9 | 19 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1933 | 9 | 20 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1933 | 9 | 21 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1933 | 9 | 22 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1933 | 9 | 23 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1933 | 9 | 24 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1933 | 9 | 25 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1933 | 9 | 26 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1933 | 9 | 27 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1933 | 9 | 28 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1933 | 9 | 29 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1933 | 9 | 30 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1933 | 10 | 1 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1933 | 10 | 2 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1933 | 10 | 3 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1933 | 10 | 4 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1933 | 10 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1933 | 10 | 6 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1933 | 10 | 7 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1933 | 10 | 8 | 385.3061 | 15 | 370.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1933 | 10 | 9 | 424.4898 | 15 | 409.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1933 | 10 | 10 | 372.2449 | 15 | 357.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1933 | 10 | 11 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1933 | 10 | 12 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1933 | 10 | 13 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1933 | 10 | 14 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1933 | 10 | 15 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1933 | 10 | 16 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1933 | 10 | 17 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1933 | 10 | 18 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1933 | 10 | 19 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1933 | 10 | 20 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1933 | 10 | 21 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1933 | 10 | 22 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1933 | 10 | 23 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1933 | 10 | 24 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1933 | 10 | 25 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1933 | 10 | 26 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1933 | 10 | 27 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1933 | 10 | 28 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1933 | 10 | 29 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1933 | 10 | 30 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1933 | 10 | 31 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1933 | 11 | 1 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1933 | 11 | 2 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1933 | 11 | 3 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1933 | 11 | 4 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1933 | 11 | 5 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1933 | 11 | 6 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1933 | 11 | 7 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1933 | 11 | 8 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1933 | 11 | 9 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1933 | 11 | 10 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1933 | 11 | 11 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1933 | 11 | 12 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1933 | 11 | 13 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1933 | 11 | 14 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1933 | 11 | 15 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1933 | 11 | 16 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1933 | 11 | 17 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1933 | 11 | 18 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1933 | 11 | 19 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1933 | 11 | 20 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1933 | 11 | 21 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1933 | 11 | 22 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1933 | 11 | 23 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1933 | 11 | 24 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1933 | 11 | 25 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1933 | 11 | 26 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1933 | 11 | 27 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1933 | 11 | 28 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1933 | 11 | 29 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1933 | 11 | 30 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1933 | 12 | 1 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1933 | 12 | 2 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1933 | 12 | 3 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1933 | 12 | 4 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1933 | 12 | 5 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1933 | 12 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1933 | 12 | 7 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1933 | 12 | 8 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1933 | 12 | 9 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1933 | 12 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 12 | 11 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1933 | 12 | 12 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1933 | 12 | 13 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1933 | 12 | 14 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1933 | 12 | 15 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1933 | 12 | 16 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1933 | 12 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1933 | 12 | 18 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1933 | 12 | 19 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1933 | 12 | 20 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1933 | 12 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1933 | 12 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1933 | 12 | 23 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1933 | 12 | 24 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 12 | 25 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1933 | 12 | 26 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1933 | 12 | 27 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1933 | 12 | 28 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1933 | 12 | 29 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1933 | 12 | 30 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1933 | 12 | 31 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1934 | 1 | 1 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1934 | 1 | 2 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1934 | 1 | 3 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1934 | 1 | 4 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1934 | 1 | 5 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1934 | 1 | 6 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1934 | 1 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1934 | 1 | 8 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1934 | 1 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1934 | 1 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1934 | 1 | 11 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 12 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 15 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 16 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 17 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 1 | 18 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1934 | 1 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1934 | 1 | 20 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1934 | 1 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1934 | 1 | 22 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1934 | 1 | 23 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1934 | 1 | 24 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1934 | 1 | 25 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1934 | 1 | 26 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1934 | 1 | 27 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1934 | 1 | 28 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1934 | 1 | 29 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1934 | 1 | 30 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1934 | 1 | 31 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1934 | 2 | 1 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1934 | 2 | 2 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1934 | 2 | 3 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1934 | 2 | 4 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1934 | 2 | 5 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1934 | 2 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1934 | 2 | 7 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1934 | 2 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1934 | 2 | 9 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1934 | 2 | 10 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1934 | 2 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1934 | 2 | 12 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1934 | 2 | 13 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1934 | 2 | 14 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1934 | 2 | 15 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1934 | 2 | 16 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1934 | 2 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1934 | 2 | 18 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1934 | 2 | 19 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1934 | 2 | 20 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1934 | 2 | 21 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 22 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 24 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 25 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 2 | 28 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1934 | 3 | 1 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1934 | 3 | 2 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1934 | 3 | 3 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1934 | 3 | 4 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1934 | 3 | 5 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1934 | 3 | 6 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1934 | 3 | 7 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1934 | 3 | 8 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1934 | 3 | 9 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1934 | 3 | 10 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1934 | 3 | 11 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1934 | 3 | 12 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1934 | 3 | 13 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1934 | 3 | 14 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1934 | 3 | 15 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1934 | 3 | 16 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1934 | 3 | 17 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1934 | 3 | 18 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1934 | 3 | 19 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1934 | 3 | 20 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1934 | 3 | 21 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1934 | 3 | 22 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1934 | 3 | 23 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1934 | 3 | 24 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1934 | 3 | 25 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1934 | 3 | 26 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1934 | 3 | 27 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1934 | 3 | 28 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1934 | 3 | 29 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1934 | 3 | 30 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1934 | 3 | 31 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1934 | 4 | 1 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1934 | 4 | 2 | 640 | 25 | 615 | 28.72 | 139.3858 | 0.77441 | 27.9456 | 89.27% | 294.4836 | 276.8146 | 6643.5497
1934 | 4 | 3 | 1005.7143 | 25 | 980.7143 | 27.9886 | 139.3858 | 0.77441 | 27.2142 | 89.27% | 286.776 | 269.5694 | 6469.666
1934 | 4 | 4 | 1097.1429 | 25 | 1072.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
1934 | 4 | 5 | 835.9184 | 25 | 810.9184 | 28.3282 | 139.3858 | 0.77441 | 27.5538 | 89.27% | 290.3545 | 272.9332 | 6550.3977
1934 | 4 | 6 | 698.7755 | 25 | 673.7755 | 28.6024 | 139.3858 | 0.77441 | 27.828 | 89.27% | 293.2449 | 275.6502 | 6615.6041
1934 | 4 | 7 | 564.2449 | 25 | 539.2449 | 28.8715 | 139.3858 | 0.77441 | 28.0971 | 89.27% | 296.0802 | 278.3154 | 6679.5685
1934 | 4 | 8 | 598.2041 | 25 | 573.2041 | 28.8036 | 139.3858 | 0.77441 | 28.0292 | 89.27% | 295.3645 | 277.6426 | 6663.4221
1934 | 4 | 9 | 705.3061 | 25 | 680.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1934 | 4 | 10 | 937.7959 | 25 | 912.7959 | 28.1244 | 139.3858 | 0.77441 | 27.35 | 89.27% | 288.2074 | 270.9149 | 6501.9587
1934 | 4 | 11 | 914.2857 | 25 | 889.2857 | 28.1714 | 139.3858 | 0.77441 | 27.397 | 89.27% | 288.7029 | 271.3807 | 6513.1369
1934 | 4 | 12 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1934 | 4 | 13 | 3696.3265 | 25 | 3671.3265 | 22.6073 | 0 | 0 | 22.6073 | 0% | 0 | 0 | 0
1934 | 4 | 14 | 2050.6122 | 25 | 2025.6122 | 25.8988 | 139.3858 | 0.77441 | 25.1244 | 89.27% | 264.7542 | 248.869 | 5972.8555
1934 | 4 | 15 | 1175.5102 | 25 | 1150.5102 | 27.649 | 139.3858 | 0.77441 | 26.8746 | 89.27% | 283.1974 | 266.2056 | 6388.9343
1934 | 4 | 16 | 937.7959 | 25 | 912.7959 | 28.1244 | 139.3858 | 0.77441 | 27.35 | 89.27% | 288.2074 | 270.9149 | 6501.9587
1934 | 4 | 17 | 1697.9592 | 25 | 1672.9592 | 26.6041 | 139.3858 | 0.77441 | 25.8297 | 89.27% | 272.1866 | 255.8554 | 6140.529
1934 | 4 | 18 | 1488.9796 | 25 | 1463.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1934 | 4 | 19 | 960 | 25 | 935 | 28.08 | 139.3858 | 0.77441 | 27.3056 | 89.27% | 287.7394 | 270.4751 | 6491.4015
1934 | 4 | 20 | 1221.2245 | 25 | 1196.2245 | 27.5576 | 139.3858 | 0.77441 | 26.7831 | 89.27% | 282.234 | 265.3 | 6367.1988
1934 | 4 | 21 | 1090.6122 | 25 | 1065.6122 | 27.8188 | 139.3858 | 0.77441 | 27.0444 | 89.27% | 284.9867 | 267.8875 | 6429.3002
1934 | 4 | 22 | 646.5306 | 25 | 621.5306 | 28.7069 | 139.3858 | 0.77441 | 27.9325 | 89.27% | 294.346 | 276.6852 | 6640.4446
1934 | 4 | 23 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1934 | 4 | 24 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1934 | 4 | 25 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1934 | 4 | 26 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1934 | 4 | 27 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1934 | 4 | 28 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1934 | 4 | 29 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1934 | 4 | 30 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1934 | 5 | 1 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1934 | 5 | 2 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1934 | 5 | 3 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1934 | 5 | 4 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1934 | 5 | 5 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1934 | 5 | 6 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1934 | 5 | 7 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1934 | 5 | 8 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1934 | 5 | 9 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1934 | 5 | 10 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1934 | 5 | 11 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1934 | 5 | 12 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1934 | 5 | 13 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1934 | 5 | 14 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1934 | 5 | 15 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1934 | 5 | 16 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1934 | 5 | 17 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1934 | 5 | 18 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1934 | 5 | 19 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1934 | 5 | 20 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1934 | 5 | 21 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1934 | 5 | 22 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1934 | 5 | 23 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1934 | 5 | 24 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1934 | 5 | 25 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1934 | 5 | 26 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1934 | 5 | 27 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1934 | 5 | 28 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1934 | 5 | 29 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1934 | 5 | 30 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1934 | 5 | 31 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1934 | 6 | 1 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1934 | 6 | 2 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1934 | 6 | 3 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1934 | 6 | 4 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1934 | 6 | 5 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1934 | 6 | 6 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1934 | 6 | 7 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1934 | 6 | 8 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1934 | 6 | 9 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1934 | 6 | 10 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1934 | 6 | 11 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1934 | 6 | 12 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1934 | 6 | 13 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1934 | 6 | 14 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1934 | 6 | 15 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1934 | 6 | 16 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1934 | 6 | 17 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1934 | 6 | 18 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1934 | 6 | 19 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1934 | 6 | 20 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1934 | 6 | 21 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1934 | 6 | 22 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1934 | 6 | 23 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1934 | 6 | 24 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1934 | 6 | 25 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1934 | 6 | 26 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1934 | 6 | 27 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1934 | 6 | 28 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1934 | 6 | 29 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1934 | 6 | 30 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1934 | 7 | 1 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1934 | 7 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1934 | 7 | 3 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 7 | 4 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1934 | 7 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 7 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 7 | 7 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1934 | 7 | 8 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1934 | 7 | 9 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1934 | 7 | 10 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1934 | 7 | 11 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1934 | 7 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 7 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1934 | 7 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1934 | 7 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1934 | 7 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1934 | 7 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1934 | 7 | 18 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1934 | 7 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1934 | 7 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1934 | 7 | 21 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1934 | 7 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1934 | 7 | 23 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1934 | 7 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1934 | 7 | 25 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1934 | 7 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1934 | 7 | 27 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1934 | 7 | 28 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1934 | 7 | 29 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1934 | 7 | 30 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1934 | 7 | 31 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1934 | 8 | 1 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1934 | 8 | 2 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1934 | 8 | 3 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1934 | 8 | 4 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1934 | 8 | 5 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1934 | 8 | 6 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1934 | 8 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 8 | 8 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1934 | 8 | 9 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1934 | 8 | 10 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 8 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1934 | 8 | 12 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1934 | 8 | 13 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 8 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1934 | 8 | 15 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1934 | 8 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1934 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1934 | 8 | 18 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1934 | 8 | 19 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1934 | 8 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1934 | 8 | 21 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1934 | 8 | 22 | 10.7102 | 5 | 5.7102 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1934 | 8 | 23 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1934 | 8 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 8 | 25 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1934 | 8 | 26 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1934 | 8 | 27 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1934 | 8 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1934 | 8 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1934 | 8 | 30 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1934 | 8 | 31 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1934 | 9 | 1 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1934 | 9 | 2 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1934 | 9 | 3 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1934 | 9 | 4 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1934 | 9 | 5 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1934 | 9 | 6 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1934 | 9 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1934 | 9 | 8 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1934 | 9 | 9 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1934 | 9 | 10 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1934 | 9 | 11 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1934 | 9 | 12 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1934 | 9 | 13 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1934 | 9 | 14 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1934 | 9 | 15 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1934 | 9 | 16 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1934 | 9 | 17 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1934 | 9 | 18 | 666.1224 | 15 | 651.1224 | 28.6678 | 139.3858 | 0.77441 | 27.8933 | 89.27% | 293.933 | 276.2971 | 6631.1294
1934 | 9 | 19 | 352.6531 | 15 | 337.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1934 | 9 | 20 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1934 | 9 | 21 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1934 | 9 | 22 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1934 | 9 | 23 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1934 | 9 | 24 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1934 | 9 | 25 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1934 | 9 | 26 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1934 | 9 | 27 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1934 | 9 | 28 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1934 | 9 | 29 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1934 | 9 | 30 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1934 | 10 | 1 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1934 | 10 | 2 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1934 | 10 | 3 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1934 | 10 | 4 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1934 | 10 | 5 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1934 | 10 | 6 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1934 | 10 | 7 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1934 | 10 | 8 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1934 | 10 | 9 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1934 | 10 | 10 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1934 | 10 | 11 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1934 | 10 | 12 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1934 | 10 | 13 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1934 | 10 | 14 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1934 | 10 | 15 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1934 | 10 | 16 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1934 | 10 | 17 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1934 | 10 | 18 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1934 | 10 | 19 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1934 | 10 | 20 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1934 | 10 | 21 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1934 | 10 | 22 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1934 | 10 | 23 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1934 | 10 | 24 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1934 | 10 | 25 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1934 | 10 | 26 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1934 | 10 | 27 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1934 | 10 | 28 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1934 | 10 | 29 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1934 | 10 | 30 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1934 | 10 | 31 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1934 | 11 | 1 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1934 | 11 | 2 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1934 | 11 | 3 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1934 | 11 | 4 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1934 | 11 | 5 | 316.0816 | 15 | 301.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1934 | 11 | 6 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1934 | 11 | 7 | 438.8571 | 15 | 423.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1934 | 11 | 8 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1934 | 11 | 9 | 216.8163 | 15 | 201.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1934 | 11 | 10 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1934 | 11 | 11 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1934 | 11 | 12 | 249.4694 | 15 | 234.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1934 | 11 | 13 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1934 | 11 | 14 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1934 | 11 | 15 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1934 | 11 | 16 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1934 | 11 | 17 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1934 | 11 | 18 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1934 | 11 | 19 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1934 | 11 | 20 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1934 | 11 | 21 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1934 | 11 | 22 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1934 | 11 | 23 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1934 | 11 | 24 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1934 | 11 | 25 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1934 | 11 | 26 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1934 | 11 | 27 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1934 | 11 | 28 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1934 | 11 | 29 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1934 | 11 | 30 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1934 | 12 | 1 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1934 | 12 | 2 | 417.9592 | 5 | 412.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1934 | 12 | 3 | 297.7959 | 5 | 292.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1934 | 12 | 4 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1934 | 12 | 5 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1934 | 12 | 6 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1934 | 12 | 7 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1934 | 12 | 8 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1934 | 12 | 9 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1934 | 12 | 10 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1934 | 12 | 11 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1934 | 12 | 12 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1934 | 12 | 13 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1934 | 12 | 14 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1934 | 12 | 15 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1934 | 12 | 16 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1934 | 12 | 17 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1934 | 12 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1934 | 12 | 19 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1934 | 12 | 20 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1934 | 12 | 21 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1934 | 12 | 22 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1934 | 12 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1934 | 12 | 24 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1934 | 12 | 25 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1934 | 12 | 26 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1934 | 12 | 27 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1934 | 12 | 28 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1934 | 12 | 29 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1934 | 12 | 30 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1934 | 12 | 31 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1935 | 1 | 1 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1935 | 1 | 2 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1935 | 1 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1935 | 1 | 4 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1935 | 1 | 5 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1935 | 1 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 1 | 7 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 1 | 8 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 1 | 9 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1935 | 1 | 10 | 783.6735 | 5 | 778.6735 | 28.4327 | 139.3858 | 0.77441 | 27.6582 | 89.27% | 291.4556 | 273.9683 | 6575.2383
1935 | 1 | 11 | 933.8776 | 5 | 928.8776 | 28.1322 | 139.3858 | 0.77441 | 27.3578 | 89.27% | 288.29 | 270.9926 | 6503.8217
1935 | 1 | 12 | 518.5306 | 5 | 513.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1935 | 1 | 13 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1935 | 1 | 14 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1935 | 1 | 15 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1935 | 1 | 16 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1935 | 1 | 17 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1935 | 1 | 18 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1935 | 1 | 19 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1935 | 1 | 20 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1935 | 1 | 21 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1935 | 1 | 22 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1935 | 1 | 23 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1935 | 1 | 24 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1935 | 1 | 25 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1935 | 1 | 26 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1935 | 1 | 27 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1935 | 1 | 28 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1935 | 1 | 29 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1935 | 1 | 30 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1935 | 1 | 31 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1935 | 2 | 1 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1935 | 2 | 2 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1935 | 2 | 3 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1935 | 2 | 4 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1935 | 2 | 5 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1935 | 2 | 6 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1935 | 2 | 7 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1935 | 2 | 8 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1935 | 2 | 9 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 10 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1935 | 2 | 12 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1935 | 2 | 13 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1935 | 2 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1935 | 2 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1935 | 2 | 16 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 17 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1935 | 2 | 18 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1935 | 2 | 19 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1935 | 2 | 20 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 21 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 22 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 23 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 24 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 25 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 26 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1935 | 2 | 27 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 2 | 28 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 3 | 1 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1935 | 3 | 2 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1935 | 3 | 3 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1935 | 3 | 4 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1935 | 3 | 5 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1935 | 3 | 6 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1935 | 3 | 7 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1935 | 3 | 8 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1935 | 3 | 9 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1935 | 3 | 10 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1935 | 3 | 11 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1935 | 3 | 12 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1935 | 3 | 13 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1935 | 3 | 14 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1935 | 3 | 15 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1935 | 3 | 16 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1935 | 3 | 17 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1935 | 3 | 18 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1935 | 3 | 19 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1935 | 3 | 20 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1935 | 3 | 21 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1935 | 3 | 22 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1935 | 3 | 23 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1935 | 3 | 24 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1935 | 3 | 25 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1935 | 3 | 26 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1935 | 3 | 27 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1935 | 3 | 28 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1935 | 3 | 29 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1935 | 3 | 30 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1935 | 3 | 31 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1935 | 4 | 1 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1935 | 4 | 2 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1935 | 4 | 3 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1935 | 4 | 4 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1935 | 4 | 5 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1935 | 4 | 6 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1935 | 4 | 7 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1935 | 4 | 8 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1935 | 4 | 9 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1935 | 4 | 10 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1935 | 4 | 11 | 569.4694 | 25 | 544.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
1935 | 4 | 12 | 611.2653 | 25 | 586.2653 | 28.7775 | 139.3858 | 0.77441 | 28.0031 | 89.27% | 295.0892 | 277.3838 | 6657.212
1935 | 4 | 13 | 625.6327 | 25 | 600.6327 | 28.7487 | 139.3858 | 0.77441 | 27.9743 | 89.27% | 294.7864 | 277.0992 | 6650.3808
1935 | 4 | 14 | 1114.1224 | 25 | 1089.1224 | 27.7718 | 139.3858 | 0.77441 | 26.9973 | 89.27% | 284.4912 | 267.4217 | 6418.1219
1935 | 4 | 15 | 956.0816 | 25 | 931.0816 | 28.0878 | 139.3858 | 0.77441 | 27.3134 | 89.27% | 287.822 | 270.5527 | 6493.2645
1935 | 4 | 16 | 1090.6122 | 25 | 1065.6122 | 27.8188 | 139.3858 | 0.77441 | 27.0444 | 89.27% | 284.9867 | 267.8875 | 6429.3002
1935 | 4 | 17 | 956.0816 | 25 | 931.0816 | 28.0878 | 139.3858 | 0.77441 | 27.3134 | 89.27% | 287.822 | 270.5527 | 6493.2645
1935 | 4 | 18 | 734.0408 | 25 | 709.0408 | 28.5319 | 139.3858 | 0.77441 | 27.7575 | 89.27% | 292.5016 | 274.9515 | 6598.8368
1935 | 4 | 19 | 1021.3878 | 25 | 996.3878 | 27.9572 | 139.3858 | 0.77441 | 27.1828 | 89.27% | 286.4456 | 269.2589 | 6462.2139
1935 | 4 | 20 | 1090.6122 | 25 | 1065.6122 | 27.8188 | 139.3858 | 0.77441 | 27.0444 | 89.27% | 284.9867 | 267.8875 | 6429.3002
1935 | 4 | 21 | 1044.898 | 25 | 1019.898 | 27.9102 | 139.3858 | 0.77441 | 27.1358 | 89.27% | 285.9502 | 268.7932 | 6451.0356
1935 | 4 | 22 | 999.1837 | 25 | 974.1837 | 28.0016 | 139.3858 | 0.77441 | 27.2272 | 89.27% | 286.9136 | 269.6988 | 6472.7711
1935 | 4 | 23 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1935 | 4 | 24 | 734.0408 | 25 | 709.0408 | 28.5319 | 139.3858 | 0.77441 | 27.7575 | 89.27% | 292.5016 | 274.9515 | 6598.8368
1935 | 4 | 25 | 655.6735 | 25 | 630.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1935 | 4 | 26 | 582.5306 | 25 | 557.5306 | 28.8349 | 139.3858 | 0.77441 | 28.0605 | 89.27% | 295.6948 | 277.9531 | 6670.8743
1935 | 4 | 27 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1935 | 4 | 28 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1935 | 4 | 29 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1935 | 4 | 30 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1935 | 5 | 1 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1935 | 5 | 2 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1935 | 5 | 3 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1935 | 5 | 4 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1935 | 5 | 5 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1935 | 5 | 6 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1935 | 5 | 7 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1935 | 5 | 8 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1935 | 5 | 9 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1935 | 5 | 10 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1935 | 5 | 11 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1935 | 5 | 12 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1935 | 5 | 13 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1935 | 5 | 14 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1935 | 5 | 15 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1935 | 5 | 16 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1935 | 5 | 17 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1935 | 5 | 18 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1935 | 5 | 19 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1935 | 5 | 20 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1935 | 5 | 21 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1935 | 5 | 22 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1935 | 5 | 23 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1935 | 5 | 24 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1935 | 5 | 25 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1935 | 5 | 26 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1935 | 5 | 27 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1935 | 5 | 28 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1935 | 5 | 29 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1935 | 5 | 30 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1935 | 5 | 31 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1935 | 6 | 1 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1935 | 6 | 2 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1935 | 6 | 3 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1935 | 6 | 4 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1935 | 6 | 5 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1935 | 6 | 6 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1935 | 6 | 7 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1935 | 6 | 8 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1935 | 6 | 9 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1935 | 6 | 10 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1935 | 6 | 11 | 1044.898 | 25 | 1019.898 | 27.9102 | 139.3858 | 0.77441 | 27.1358 | 89.27% | 285.9502 | 268.7932 | 6451.0356
1935 | 6 | 12 | 582.5306 | 25 | 557.5306 | 28.8349 | 139.3858 | 0.77441 | 28.0605 | 89.27% | 295.6948 | 277.9531 | 6670.8743
1935 | 6 | 13 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1935 | 6 | 14 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1935 | 6 | 15 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1935 | 6 | 16 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1935 | 6 | 17 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1935 | 6 | 18 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1935 | 6 | 19 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1935 | 6 | 20 | 506.7755 | 25 | 481.7755 | 28.9864 | 139.3858 | 0.77441 | 28.212 | 89.27% | 297.2914 | 279.4539 | 6706.893
1935 | 6 | 21 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1935 | 6 | 22 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1935 | 6 | 23 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1935 | 6 | 24 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1935 | 6 | 25 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1935 | 6 | 26 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1935 | 6 | 27 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1935 | 6 | 28 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1935 | 6 | 29 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1935 | 6 | 30 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1935 | 7 | 1 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1935 | 7 | 2 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1935 | 7 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1935 | 7 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 7 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1935 | 7 | 6 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1935 | 7 | 7 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 7 | 8 | 376.1633 | 5 | 371.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1935 | 7 | 9 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1935 | 7 | 10 | 218.1224 | 5 | 213.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1935 | 7 | 11 | 355.2653 | 5 | 350.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1935 | 7 | 12 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1935 | 7 | 13 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1935 | 7 | 14 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1935 | 7 | 15 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1935 | 7 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1935 | 7 | 17 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1935 | 7 | 18 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1935 | 7 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1935 | 7 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 7 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1935 | 7 | 22 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1935 | 7 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1935 | 7 | 24 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1935 | 7 | 25 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1935 | 7 | 26 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1935 | 7 | 27 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1935 | 7 | 28 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1935 | 7 | 29 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1935 | 7 | 30 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1935 | 7 | 31 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1935 | 8 | 1 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1935 | 8 | 2 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1935 | 8 | 3 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1935 | 8 | 4 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1935 | 8 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1935 | 8 | 6 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1935 | 8 | 7 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1935 | 8 | 8 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1935 | 8 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1935 | 8 | 10 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1935 | 8 | 11 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1935 | 8 | 12 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1935 | 8 | 13 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1935 | 8 | 14 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1935 | 8 | 15 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1935 | 8 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1935 | 8 | 17 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1935 | 8 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1935 | 8 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1935 | 8 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1935 | 8 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1935 | 8 | 22 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1935 | 8 | 23 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1935 | 8 | 24 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1935 | 8 | 25 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1935 | 8 | 26 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1935 | 8 | 27 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1935 | 8 | 28 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1935 | 8 | 29 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1935 | 8 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1935 | 8 | 31 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1935 | 9 | 1 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1935 | 9 | 2 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1935 | 9 | 3 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1935 | 9 | 4 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1935 | 9 | 5 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1935 | 9 | 6 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1935 | 9 | 7 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1935 | 9 | 8 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1935 | 9 | 9 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1935 | 9 | 10 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1935 | 9 | 11 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1935 | 9 | 12 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1935 | 9 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1935 | 9 | 14 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1935 | 9 | 15 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1935 | 9 | 16 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1935 | 9 | 17 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1935 | 9 | 18 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1935 | 9 | 19 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1935 | 9 | 20 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1935 | 9 | 21 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1935 | 9 | 22 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1935 | 9 | 23 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1935 | 9 | 24 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1935 | 9 | 25 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1935 | 9 | 26 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1935 | 9 | 27 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1935 | 9 | 28 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1935 | 9 | 29 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1935 | 9 | 30 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1935 | 10 | 1 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1935 | 10 | 2 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1935 | 10 | 3 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1935 | 10 | 4 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1935 | 10 | 5 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1935 | 10 | 6 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1935 | 10 | 7 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1935 | 10 | 8 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1935 | 10 | 9 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1935 | 10 | 10 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1935 | 10 | 11 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1935 | 10 | 12 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1935 | 10 | 13 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1935 | 10 | 14 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1935 | 10 | 15 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1935 | 10 | 16 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1935 | 10 | 17 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1935 | 10 | 18 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1935 | 10 | 19 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1935 | 10 | 20 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1935 | 10 | 21 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1935 | 10 | 22 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1935 | 10 | 23 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1935 | 10 | 24 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1935 | 10 | 25 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1935 | 10 | 26 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1935 | 10 | 27 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1935 | 10 | 28 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1935 | 10 | 29 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1935 | 10 | 30 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1935 | 10 | 31 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1935 | 11 | 1 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1935 | 11 | 2 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1935 | 11 | 3 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1935 | 11 | 4 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1935 | 11 | 5 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1935 | 11 | 6 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1935 | 11 | 7 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1935 | 11 | 8 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1935 | 11 | 9 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1935 | 11 | 10 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1935 | 11 | 11 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1935 | 11 | 12 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1935 | 11 | 13 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1935 | 11 | 14 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1935 | 11 | 15 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1935 | 11 | 16 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1935 | 11 | 17 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1935 | 11 | 18 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1935 | 11 | 19 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1935 | 11 | 20 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1935 | 11 | 21 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1935 | 11 | 22 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1935 | 11 | 23 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1935 | 11 | 24 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1935 | 11 | 25 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1935 | 11 | 26 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1935 | 11 | 27 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1935 | 11 | 28 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1935 | 11 | 29 | 1025.3061 | 15 | 1010.3061 | 27.9494 | 139.3858 | 0.77441 | 27.175 | 89.27% | 286.3631 | 269.1813 | 6460.3508
1935 | 11 | 30 | 711.8367 | 15 | 696.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1935 | 12 | 1 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1935 | 12 | 2 | 249.4694 | 5 | 244.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1935 | 12 | 3 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1935 | 12 | 4 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1935 | 12 | 5 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1935 | 12 | 6 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1935 | 12 | 7 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1935 | 12 | 8 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1935 | 12 | 9 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1935 | 12 | 10 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1935 | 12 | 11 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1935 | 12 | 12 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1935 | 12 | 13 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1935 | 12 | 14 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1935 | 12 | 15 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1935 | 12 | 16 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1935 | 12 | 17 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1935 | 12 | 18 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1935 | 12 | 19 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1935 | 12 | 20 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1935 | 12 | 21 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1935 | 12 | 22 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1935 | 12 | 23 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1935 | 12 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1935 | 12 | 25 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1935 | 12 | 26 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1935 | 12 | 27 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1935 | 12 | 28 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1935 | 12 | 29 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1935 | 12 | 30 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1935 | 12 | 31 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1936 | 1 | 1 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1936 | 1 | 2 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1936 | 1 | 3 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1936 | 1 | 4 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1936 | 1 | 5 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1936 | 1 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1936 | 1 | 7 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1936 | 1 | 8 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1936 | 1 | 9 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1936 | 1 | 10 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1936 | 1 | 11 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1936 | 1 | 12 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1936 | 1 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1936 | 1 | 14 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 1 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1936 | 1 | 16 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1936 | 1 | 17 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1936 | 1 | 18 | 280.8163 | 5 | 275.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1936 | 1 | 19 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1936 | 1 | 20 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1936 | 1 | 21 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1936 | 1 | 22 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1936 | 1 | 23 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1936 | 1 | 24 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1936 | 1 | 25 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1936 | 1 | 26 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1936 | 1 | 27 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1936 | 1 | 28 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1936 | 1 | 29 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1936 | 1 | 30 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1936 | 1 | 31 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1936 | 2 | 1 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1936 | 2 | 2 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1936 | 2 | 3 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1936 | 2 | 4 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1936 | 2 | 5 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1936 | 2 | 6 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1936 | 2 | 7 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1936 | 2 | 8 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 10 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 11 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 12 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 13 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1936 | 2 | 14 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 15 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 17 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 2 | 18 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1936 | 2 | 19 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1936 | 2 | 20 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1936 | 2 | 21 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1936 | 2 | 22 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1936 | 2 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1936 | 2 | 24 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1936 | 2 | 25 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1936 | 2 | 26 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1936 | 2 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1936 | 2 | 28 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1936 | 2 | 29 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1936 | 3 | 1 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1936 | 3 | 2 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1936 | 3 | 3 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1936 | 3 | 4 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1936 | 3 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1936 | 3 | 6 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1936 | 3 | 7 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1936 | 3 | 8 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1936 | 3 | 9 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1936 | 3 | 10 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1936 | 3 | 11 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1936 | 3 | 12 | 2285.7143 | 25 | 2260.7143 | 25.4286 | 139.3858 | 0.77441 | 24.6542 | 89.27% | 259.7993 | 244.2114 | 5861.0731
1936 | 3 | 13 | 5707.7551 | 25 | 5682.7551 | 18.5845 | 0 | 0 | 18.5845 | 0% | 0 | 0 | 0
1936 | 3 | 14 | 2612.2449 | 25 | 2587.2449 | 24.7755 | 0 | 0 | 24.7755 | 0% | 0 | 0 | 0
1936 | 3 | 15 | 1410.6122 | 25 | 1385.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1936 | 3 | 16 | 1114.1224 | 25 | 1089.1224 | 27.7718 | 139.3858 | 0.77441 | 26.9973 | 89.27% | 284.4912 | 267.4217 | 6418.1219
1936 | 3 | 17 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1936 | 3 | 18 | 3082.449 | 25 | 3057.449 | 23.8351 | 0 | 0 | 23.8351 | 0% | 0 | 0 | 0
1936 | 3 | 19 | 7497.1429 | 25 | 7472.1429 | 15.0057 | 0 | 0 | 15.0057 | 0% | 0 | 0 | 0
1936 | 3 | 20 | 4075.102 | 25 | 4050.102 | 21.8498 | 0 | 0 | 21.8498 | 0% | 0 | 0 | 0
1936 | 3 | 21 | 2377.1429 | 25 | 2352.1429 | 25.2457 | 139.3858 | 0.77441 | 24.4713 | 89.27% | 257.8724 | 242.4001 | 5817.6022
1936 | 3 | 22 | 3617.9592 | 25 | 3592.9592 | 22.7641 | 0 | 0 | 22.7641 | 0% | 0 | 0 | 0
1936 | 3 | 23 | 1789.3878 | 25 | 1764.3878 | 26.4212 | 139.3858 | 0.77441 | 25.6468 | 89.27% | 270.2597 | 254.0441 | 6097.0581
1936 | 3 | 24 | 1216 | 25 | 1191 | 27.568 | 139.3858 | 0.77441 | 26.7936 | 89.27% | 282.3441 | 265.4035 | 6369.6829
1936 | 3 | 25 | 1007.0204 | 25 | 982.0204 | 27.986 | 139.3858 | 0.77441 | 27.2115 | 89.27% | 286.7484 | 269.5435 | 6469.045
1936 | 3 | 26 | 856.8163 | 25 | 831.8163 | 28.2864 | 139.3858 | 0.77441 | 27.512 | 89.27% | 289.9141 | 272.5192 | 6540.4615
1936 | 3 | 27 | 893.3878 | 25 | 868.3878 | 28.2132 | 139.3858 | 0.77441 | 27.4388 | 89.27% | 289.1433 | 271.7947 | 6523.0731
1936 | 3 | 28 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
1936 | 3 | 29 | 1086.6939 | 25 | 1061.6939 | 27.8266 | 139.3858 | 0.77441 | 27.0522 | 89.27% | 285.0693 | 267.9651 | 6431.1632
1936 | 3 | 30 | 838.5306 | 25 | 813.5306 | 28.3229 | 139.3858 | 0.77441 | 27.5485 | 89.27% | 290.2995 | 272.8815 | 6549.1557
1936 | 3 | 31 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1936 | 4 | 1 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1936 | 4 | 2 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1936 | 4 | 3 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1936 | 4 | 4 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1936 | 4 | 5 | 440.1633 | 25 | 415.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
1936 | 4 | 6 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
1936 | 4 | 7 | 2063.6735 | 25 | 2038.6735 | 25.8727 | 139.3858 | 0.77441 | 25.0982 | 89.27% | 264.479 | 248.6102 | 5966.6454
1936 | 4 | 8 | 1128.4898 | 25 | 1103.4898 | 27.743 | 139.3858 | 0.77441 | 26.9686 | 89.27% | 284.1884 | 267.1371 | 6411.2908
1936 | 4 | 9 | 821.551 | 25 | 796.551 | 28.3569 | 139.3858 | 0.77441 | 27.5825 | 89.27% | 290.6573 | 273.2179 | 6557.2289
1936 | 4 | 10 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1936 | 4 | 11 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1936 | 4 | 12 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1936 | 4 | 13 | 629.551 | 25 | 604.551 | 28.7409 | 139.3858 | 0.77441 | 27.9665 | 89.27% | 294.7038 | 277.0216 | 6648.5178
1936 | 4 | 14 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1936 | 4 | 15 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1936 | 4 | 16 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1936 | 4 | 17 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1936 | 4 | 18 | 544.6531 | 25 | 519.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
1936 | 4 | 19 | 504.1633 | 25 | 479.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
1936 | 4 | 20 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1936 | 4 | 21 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1936 | 4 | 22 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1936 | 4 | 23 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1936 | 4 | 24 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1936 | 4 | 25 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1936 | 4 | 26 | 246.8571 | 25 | 221.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
1936 | 4 | 27 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1936 | 4 | 28 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1936 | 4 | 29 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1936 | 4 | 30 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1936 | 5 | 1 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1936 | 5 | 2 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1936 | 5 | 3 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1936 | 5 | 4 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1936 | 5 | 5 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1936 | 5 | 6 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1936 | 5 | 7 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1936 | 5 | 8 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1936 | 5 | 9 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1936 | 5 | 10 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1936 | 5 | 11 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1936 | 5 | 12 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1936 | 5 | 13 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1936 | 5 | 14 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1936 | 5 | 15 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1936 | 5 | 16 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1936 | 5 | 17 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1936 | 5 | 18 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1936 | 5 | 19 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1936 | 5 | 20 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1936 | 5 | 21 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1936 | 5 | 22 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1936 | 5 | 23 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1936 | 5 | 24 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1936 | 5 | 25 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1936 | 5 | 26 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1936 | 5 | 27 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1936 | 5 | 28 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1936 | 5 | 29 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1936 | 5 | 30 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1936 | 5 | 31 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1936 | 6 | 1 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1936 | 6 | 2 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1936 | 6 | 3 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1936 | 6 | 4 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1936 | 6 | 5 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1936 | 6 | 6 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1936 | 6 | 7 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1936 | 6 | 8 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1936 | 6 | 9 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1936 | 6 | 10 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1936 | 6 | 11 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1936 | 6 | 12 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1936 | 6 | 13 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1936 | 6 | 14 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1936 | 6 | 15 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1936 | 6 | 16 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1936 | 6 | 17 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1936 | 6 | 18 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1936 | 6 | 19 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1936 | 6 | 20 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1936 | 6 | 21 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1936 | 6 | 22 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1936 | 6 | 23 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1936 | 6 | 24 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1936 | 6 | 25 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1936 | 6 | 26 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1936 | 6 | 27 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1936 | 6 | 28 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1936 | 6 | 29 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1936 | 6 | 30 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1936 | 7 | 1 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1936 | 7 | 2 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1936 | 7 | 3 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1936 | 7 | 4 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1936 | 7 | 5 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1936 | 7 | 6 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1936 | 7 | 7 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1936 | 7 | 8 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1936 | 7 | 9 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1936 | 7 | 10 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1936 | 7 | 11 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1936 | 7 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1936 | 7 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1936 | 7 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1936 | 7 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1936 | 7 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1936 | 7 | 17 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1936 | 7 | 18 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1936 | 7 | 19 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1936 | 7 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1936 | 7 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1936 | 7 | 22 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1936 | 7 | 23 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1936 | 7 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1936 | 7 | 25 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1936 | 7 | 26 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1936 | 7 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1936 | 7 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1936 | 7 | 29 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1936 | 7 | 30 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1936 | 7 | 31 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1936 | 8 | 1 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1936 | 8 | 2 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1936 | 8 | 3 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1936 | 8 | 4 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1936 | 8 | 5 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1936 | 8 | 6 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 8 | 7 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1936 | 8 | 8 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 8 | 9 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1936 | 8 | 10 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 8 | 11 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1936 | 8 | 12 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 8 | 13 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1936 | 8 | 14 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1936 | 8 | 15 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 8 | 16 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1936 | 8 | 17 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1936 | 8 | 18 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1936 | 8 | 19 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1936 | 8 | 20 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 8 | 21 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 8 | 22 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1936 | 8 | 23 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1936 | 8 | 24 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 8 | 25 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1936 | 8 | 26 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 8 | 27 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1936 | 8 | 28 | 4.8327 | 5 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1936 | 8 | 29 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1936 | 8 | 30 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1936 | 8 | 31 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1936 | 9 | 1 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 9 | 2 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1936 | 9 | 3 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1936 | 9 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1936 | 9 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1936 | 9 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1936 | 9 | 7 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1936 | 9 | 8 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1936 | 9 | 9 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1936 | 9 | 10 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1936 | 9 | 11 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 9 | 12 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1936 | 9 | 13 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1936 | 9 | 14 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1936 | 9 | 15 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1936 | 9 | 16 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1936 | 9 | 17 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 9 | 18 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1936 | 9 | 19 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1936 | 9 | 20 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1936 | 9 | 21 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1936 | 9 | 22 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1936 | 9 | 23 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1936 | 9 | 24 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 9 | 25 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1936 | 9 | 26 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1936 | 9 | 27 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1936 | 9 | 28 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1936 | 9 | 29 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1936 | 9 | 30 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1936 | 10 | 1 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1936 | 10 | 2 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1936 | 10 | 3 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1936 | 10 | 4 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1936 | 10 | 5 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1936 | 10 | 6 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1936 | 10 | 7 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1936 | 10 | 8 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1936 | 10 | 9 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1936 | 10 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1936 | 10 | 11 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1936 | 10 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1936 | 10 | 13 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1936 | 10 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1936 | 10 | 15 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1936 | 10 | 16 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1936 | 10 | 17 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1936 | 10 | 18 | 417.9592 | 15 | 402.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1936 | 10 | 19 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1936 | 10 | 20 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1936 | 10 | 21 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1936 | 10 | 22 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1936 | 10 | 23 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1936 | 10 | 24 | 352.6531 | 15 | 337.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1936 | 10 | 25 | 323.9184 | 15 | 308.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1936 | 10 | 26 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1936 | 10 | 27 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1936 | 10 | 28 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1936 | 10 | 29 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1936 | 10 | 30 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1936 | 10 | 31 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1936 | 11 | 1 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1936 | 11 | 2 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1936 | 11 | 3 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1936 | 11 | 4 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1936 | 11 | 5 | 261.2245 | 15 | 246.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1936 | 11 | 6 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1936 | 11 | 7 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1936 | 11 | 8 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1936 | 11 | 9 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1936 | 11 | 10 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1936 | 11 | 11 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1936 | 11 | 12 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1936 | 11 | 13 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1936 | 11 | 14 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1936 | 11 | 15 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1936 | 11 | 16 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1936 | 11 | 17 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1936 | 11 | 18 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1936 | 11 | 19 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1936 | 11 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1936 | 11 | 21 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1936 | 11 | 22 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1936 | 11 | 23 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1936 | 11 | 24 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1936 | 11 | 25 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1936 | 11 | 26 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1936 | 11 | 27 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1936 | 11 | 28 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1936 | 11 | 29 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1936 | 11 | 30 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1936 | 12 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1936 | 12 | 2 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1936 | 12 | 3 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1936 | 12 | 4 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1936 | 12 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1936 | 12 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1936 | 12 | 7 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1936 | 12 | 8 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1936 | 12 | 9 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1936 | 12 | 10 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1936 | 12 | 11 | 626.9388 | 5 | 621.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1936 | 12 | 12 | 1128.4898 | 5 | 1123.4898 | 27.743 | 139.3858 | 0.77441 | 26.9686 | 89.27% | 284.1884 | 267.1371 | 6411.2908
1936 | 12 | 13 | 659.5918 | 5 | 654.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1936 | 12 | 14 | 357.8776 | 5 | 352.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1936 | 12 | 15 | 271.6735 | 5 | 266.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1936 | 12 | 16 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1936 | 12 | 17 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1936 | 12 | 18 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1936 | 12 | 19 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1936 | 12 | 20 | 999.1837 | 5 | 994.1837 | 28.0016 | 139.3858 | 0.77441 | 27.2272 | 89.27% | 286.9136 | 269.6988 | 6472.7711
1936 | 12 | 21 | 1763.2653 | 5 | 1758.2653 | 26.4735 | 139.3858 | 0.77441 | 25.6991 | 89.27% | 270.8102 | 254.5616 | 6109.4784
1936 | 12 | 22 | 751.0204 | 5 | 746.0204 | 28.498 | 139.3858 | 0.77441 | 27.7235 | 89.27% | 292.1438 | 274.6151 | 6590.7636
1936 | 12 | 23 | 437.551 | 5 | 432.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1936 | 12 | 24 | 320 | 5 | 315 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1936 | 12 | 25 | 214.2041 | 5 | 209.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1936 | 12 | 26 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1936 | 12 | 27 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1936 | 12 | 28 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1936 | 12 | 29 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1936 | 12 | 30 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1936 | 12 | 31 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1937 | 1 | 1 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1937 | 1 | 2 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1937 | 1 | 3 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1937 | 1 | 4 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1937 | 1 | 5 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1937 | 1 | 6 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1937 | 1 | 7 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1937 | 1 | 8 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1937 | 1 | 9 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1937 | 1 | 10 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1937 | 1 | 11 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1937 | 1 | 12 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1937 | 1 | 13 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1937 | 1 | 14 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1937 | 1 | 15 | 378.7755 | 5 | 373.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1937 | 1 | 16 | 417.9592 | 5 | 412.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1937 | 1 | 17 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1937 | 1 | 18 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1937 | 1 | 19 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1937 | 1 | 20 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1937 | 1 | 21 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1937 | 1 | 22 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1937 | 1 | 23 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1937 | 1 | 24 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1937 | 1 | 25 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1937 | 1 | 26 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1937 | 1 | 27 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1937 | 1 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1937 | 1 | 29 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1937 | 1 | 30 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1937 | 1 | 31 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1937 | 2 | 1 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1937 | 2 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1937 | 2 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1937 | 2 | 4 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1937 | 2 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1937 | 2 | 6 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1937 | 2 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1937 | 2 | 8 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1937 | 2 | 9 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1937 | 2 | 10 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1937 | 2 | 11 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1937 | 2 | 12 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1937 | 2 | 13 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1937 | 2 | 14 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1937 | 2 | 15 | 1711.0204 | 5 | 1706.0204 | 26.578 | 139.3858 | 0.77441 | 25.8035 | 89.27% | 271.9113 | 255.5966 | 6134.3189
1937 | 2 | 16 | 620.4082 | 5 | 615.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1937 | 2 | 17 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1937 | 2 | 18 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1937 | 2 | 19 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1937 | 2 | 20 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1937 | 2 | 21 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1937 | 2 | 22 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1937 | 2 | 23 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1937 | 2 | 24 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1937 | 2 | 25 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1937 | 2 | 26 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1937 | 2 | 27 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1937 | 2 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1937 | 3 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1937 | 3 | 2 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1937 | 3 | 3 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1937 | 3 | 4 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1937 | 3 | 5 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1937 | 3 | 6 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1937 | 3 | 7 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1937 | 3 | 8 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1937 | 3 | 9 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1937 | 3 | 10 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1937 | 3 | 11 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1937 | 3 | 12 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1937 | 3 | 13 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1937 | 3 | 14 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1937 | 3 | 15 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1937 | 3 | 16 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1937 | 3 | 17 | 927.3469 | 25 | 902.3469 | 28.1453 | 139.3858 | 0.77441 | 27.3709 | 89.27% | 288.4276 | 271.122 | 6506.9268
1937 | 3 | 18 | 770.6122 | 25 | 745.6122 | 28.4588 | 139.3858 | 0.77441 | 27.6844 | 89.27% | 291.7309 | 274.227 | 6581.4484
1937 | 3 | 19 | 504.1633 | 25 | 479.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
1937 | 3 | 20 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1937 | 3 | 21 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1937 | 3 | 22 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1937 | 3 | 23 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1937 | 3 | 24 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1937 | 3 | 25 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1937 | 3 | 26 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1937 | 3 | 27 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1937 | 3 | 28 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1937 | 3 | 29 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1937 | 3 | 30 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1937 | 3 | 31 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1937 | 4 | 1 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1937 | 4 | 2 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1937 | 4 | 3 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1937 | 4 | 4 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1937 | 4 | 5 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1937 | 4 | 6 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1937 | 4 | 7 | 770.6122 | 25 | 745.6122 | 28.4588 | 139.3858 | 0.77441 | 27.6844 | 89.27% | 291.7309 | 274.227 | 6581.4484
1937 | 4 | 8 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1937 | 4 | 9 | 856.8163 | 25 | 831.8163 | 28.2864 | 139.3858 | 0.77441 | 27.512 | 89.27% | 289.9141 | 272.5192 | 6540.4615
1937 | 4 | 10 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1937 | 4 | 11 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1937 | 4 | 12 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1937 | 4 | 13 | 689.6327 | 25 | 664.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
1937 | 4 | 14 | 1107.5918 | 25 | 1082.5918 | 27.7848 | 139.3858 | 0.77441 | 27.0104 | 89.27% | 284.6289 | 267.5511 | 6421.227
1937 | 4 | 15 | 1193.7959 | 25 | 1168.7959 | 27.6124 | 139.3858 | 0.77441 | 26.838 | 89.27% | 282.8121 | 265.8433 | 6380.2401
1937 | 4 | 16 | 1260.4082 | 25 | 1235.4082 | 27.4792 | 139.3858 | 0.77441 | 26.7048 | 89.27% | 281.4082 | 264.5237 | 6348.5684
1937 | 4 | 17 | 1216 | 25 | 1191 | 27.568 | 139.3858 | 0.77441 | 26.7936 | 89.27% | 282.3441 | 265.4035 | 6369.6829
1937 | 4 | 18 | 929.9592 | 25 | 904.9592 | 28.1401 | 139.3858 | 0.77441 | 27.3657 | 89.27% | 288.3726 | 271.0702 | 6505.6848
1937 | 4 | 19 | 893.3878 | 25 | 868.3878 | 28.2132 | 139.3858 | 0.77441 | 27.4388 | 89.27% | 289.1433 | 271.7947 | 6523.0731
1937 | 4 | 20 | 1086.6939 | 25 | 1061.6939 | 27.8266 | 139.3858 | 0.77441 | 27.0522 | 89.27% | 285.0693 | 267.9651 | 6431.1632
1937 | 4 | 21 | 893.3878 | 25 | 868.3878 | 28.2132 | 139.3858 | 0.77441 | 27.4388 | 89.27% | 289.1433 | 271.7947 | 6523.0731
1937 | 4 | 22 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1937 | 4 | 23 | 544.6531 | 25 | 519.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
1937 | 4 | 24 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
1937 | 4 | 25 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1937 | 4 | 26 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1937 | 4 | 27 | 804.5714 | 25 | 779.5714 | 28.3909 | 139.3858 | 0.77441 | 27.6164 | 89.27% | 291.0152 | 273.5543 | 6565.302
1937 | 4 | 28 | 804.5714 | 25 | 779.5714 | 28.3909 | 139.3858 | 0.77441 | 27.6164 | 89.27% | 291.0152 | 273.5543 | 6565.302
1937 | 4 | 29 | 1397.551 | 25 | 1372.551 | 27.2049 | 139.3858 | 0.77441 | 26.4305 | 89.27% | 278.5178 | 261.8068 | 6283.3621
1937 | 4 | 30 | 1240.8163 | 25 | 1215.8163 | 27.5184 | 139.3858 | 0.77441 | 26.744 | 89.27% | 281.8211 | 264.9118 | 6357.8836
1937 | 5 | 1 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1937 | 5 | 2 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1937 | 5 | 3 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1937 | 5 | 4 | 428.4082 | 25 | 403.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
1937 | 5 | 5 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1937 | 5 | 6 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1937 | 5 | 7 | 646.5306 | 25 | 621.5306 | 28.7069 | 139.3858 | 0.77441 | 27.9325 | 89.27% | 294.346 | 276.6852 | 6640.4446
1937 | 5 | 8 | 1384.4898 | 25 | 1359.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
1937 | 5 | 9 | 804.5714 | 25 | 779.5714 | 28.3909 | 139.3858 | 0.77441 | 27.6164 | 89.27% | 291.0152 | 273.5543 | 6565.302
1937 | 5 | 10 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1937 | 5 | 11 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1937 | 5 | 12 | 380.0816 | 25 | 355.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1937 | 5 | 13 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1937 | 5 | 14 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1937 | 5 | 15 | 1528.1633 | 25 | 1503.1633 | 26.9437 | 139.3858 | 0.77441 | 26.1693 | 89.27% | 275.7651 | 259.2192 | 6221.2608
1937 | 5 | 16 | 1397.551 | 25 | 1372.551 | 27.2049 | 139.3858 | 0.77441 | 26.4305 | 89.27% | 278.5178 | 261.8068 | 6283.3621
1937 | 5 | 17 | 736.6531 | 25 | 711.6531 | 28.5267 | 139.3858 | 0.77441 | 27.7523 | 89.27% | 292.4466 | 274.8998 | 6597.5947
1937 | 5 | 18 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1937 | 5 | 19 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1937 | 5 | 20 | 1528.1633 | 25 | 1503.1633 | 26.9437 | 139.3858 | 0.77441 | 26.1693 | 89.27% | 275.7651 | 259.2192 | 6221.2608
1937 | 5 | 21 | 1528.1633 | 25 | 1503.1633 | 26.9437 | 139.3858 | 0.77441 | 26.1693 | 89.27% | 275.7651 | 259.2192 | 6221.2608
1937 | 5 | 22 | 753.6327 | 25 | 728.6327 | 28.4927 | 139.3858 | 0.77441 | 27.7183 | 89.27% | 292.0887 | 274.5634 | 6589.5216
1937 | 5 | 23 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1937 | 5 | 24 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1937 | 5 | 25 | 380.0816 | 25 | 355.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1937 | 5 | 26 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1937 | 5 | 27 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1937 | 5 | 28 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1937 | 5 | 29 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1937 | 5 | 30 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1937 | 5 | 31 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1937 | 6 | 1 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1937 | 6 | 2 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1937 | 6 | 3 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1937 | 6 | 4 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1937 | 6 | 5 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1937 | 6 | 6 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1937 | 6 | 7 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1937 | 6 | 8 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1937 | 6 | 9 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1937 | 6 | 10 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1937 | 6 | 11 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1937 | 6 | 12 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1937 | 6 | 13 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1937 | 6 | 14 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1937 | 6 | 15 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1937 | 6 | 16 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1937 | 6 | 17 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1937 | 6 | 18 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1937 | 6 | 19 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1937 | 6 | 20 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1937 | 6 | 21 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1937 | 6 | 22 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1937 | 6 | 23 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1937 | 6 | 24 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1937 | 6 | 25 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1937 | 6 | 26 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1937 | 6 | 27 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1937 | 6 | 28 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1937 | 6 | 29 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1937 | 6 | 30 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1937 | 7 | 1 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1937 | 7 | 2 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1937 | 7 | 3 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1937 | 7 | 4 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1937 | 7 | 5 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1937 | 7 | 6 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1937 | 7 | 7 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1937 | 7 | 8 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1937 | 7 | 9 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1937 | 7 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1937 | 7 | 11 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1937 | 7 | 12 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1937 | 7 | 13 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1937 | 7 | 14 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1937 | 7 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1937 | 7 | 16 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1937 | 7 | 17 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1937 | 7 | 18 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1937 | 7 | 19 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1937 | 7 | 20 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1937 | 7 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1937 | 7 | 22 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1937 | 7 | 23 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1937 | 7 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1937 | 7 | 25 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1937 | 7 | 26 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1937 | 7 | 27 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1937 | 7 | 28 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1937 | 7 | 29 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1937 | 7 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1937 | 7 | 31 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1937 | 8 | 1 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1937 | 8 | 2 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1937 | 8 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1937 | 8 | 4 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1937 | 8 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1937 | 8 | 6 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1937 | 8 | 7 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1937 | 8 | 8 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1937 | 8 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1937 | 8 | 10 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1937 | 8 | 11 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1937 | 8 | 12 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1937 | 8 | 13 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1937 | 8 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1937 | 8 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1937 | 8 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1937 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1937 | 8 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1937 | 8 | 19 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1937 | 8 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1937 | 8 | 21 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1937 | 8 | 22 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1937 | 8 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1937 | 8 | 24 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1937 | 8 | 25 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1937 | 8 | 26 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1937 | 8 | 27 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1937 | 8 | 28 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1937 | 8 | 29 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1937 | 8 | 30 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1937 | 8 | 31 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1937 | 9 | 1 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1937 | 9 | 2 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1937 | 9 | 3 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1937 | 9 | 4 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1937 | 9 | 5 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1937 | 9 | 6 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1937 | 9 | 7 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1937 | 9 | 8 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1937 | 9 | 9 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1937 | 9 | 10 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1937 | 9 | 11 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1937 | 9 | 12 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1937 | 9 | 13 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1937 | 9 | 14 | 261.2245 | 15 | 246.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1937 | 9 | 15 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1937 | 9 | 16 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1937 | 9 | 17 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1937 | 9 | 18 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1937 | 9 | 19 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1937 | 9 | 20 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1937 | 9 | 21 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1937 | 9 | 22 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1937 | 9 | 23 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1937 | 9 | 24 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1937 | 9 | 25 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1937 | 9 | 26 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1937 | 9 | 27 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1937 | 9 | 28 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1937 | 9 | 29 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1937 | 9 | 30 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1937 | 10 | 1 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1937 | 10 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1937 | 10 | 3 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1937 | 10 | 4 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1937 | 10 | 5 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1937 | 10 | 6 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1937 | 10 | 7 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1937 | 10 | 8 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1937 | 10 | 9 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1937 | 10 | 10 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1937 | 10 | 11 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1937 | 10 | 12 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1937 | 10 | 13 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1937 | 10 | 14 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1937 | 10 | 15 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1937 | 10 | 16 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1937 | 10 | 17 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1937 | 10 | 18 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1937 | 10 | 19 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1937 | 10 | 20 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1937 | 10 | 21 | 705.3061 | 15 | 690.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1937 | 10 | 22 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1937 | 10 | 23 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1937 | 10 | 24 | 1221.2245 | 15 | 1206.2245 | 27.5576 | 139.3858 | 0.77441 | 26.7831 | 89.27% | 282.234 | 265.3 | 6367.1988
1937 | 10 | 25 | 561.6327 | 15 | 546.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1937 | 10 | 26 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1937 | 10 | 27 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1937 | 10 | 28 | 203.7551 | 15 | 188.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1937 | 10 | 29 | 491.102 | 15 | 476.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1937 | 10 | 30 | 357.8776 | 15 | 342.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1937 | 10 | 31 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1937 | 11 | 1 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1937 | 11 | 2 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1937 | 11 | 3 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1937 | 11 | 4 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1937 | 11 | 5 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1937 | 11 | 6 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1937 | 11 | 7 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1937 | 11 | 8 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1937 | 11 | 9 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1937 | 11 | 10 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1937 | 11 | 11 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1937 | 11 | 12 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1937 | 11 | 13 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1937 | 11 | 14 | 1182.0408 | 15 | 1167.0408 | 27.6359 | 139.3858 | 0.77441 | 26.8615 | 89.27% | 283.0598 | 266.0762 | 6385.8292
1937 | 11 | 15 | 1247.3469 | 15 | 1232.3469 | 27.5053 | 139.3858 | 0.77441 | 26.7309 | 89.27% | 281.6834 | 264.7824 | 6354.7786
1937 | 11 | 16 | 705.3061 | 15 | 690.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1937 | 11 | 17 | 464.9796 | 15 | 449.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1937 | 11 | 18 | 346.1224 | 15 | 331.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1937 | 11 | 19 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1937 | 11 | 20 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1937 | 11 | 21 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1937 | 11 | 22 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1937 | 11 | 23 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1937 | 11 | 24 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1937 | 11 | 25 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1937 | 11 | 26 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1937 | 11 | 27 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1937 | 11 | 28 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1937 | 11 | 29 | 2246.5306 | 15 | 2231.5306 | 25.5069 | 139.3858 | 0.77441 | 24.7325 | 89.27% | 260.6252 | 244.9876 | 5879.7035
1937 | 11 | 30 | 1162.449 | 15 | 1147.449 | 27.6751 | 139.3858 | 0.77441 | 26.9007 | 89.27% | 283.4727 | 266.4644 | 6395.1444
1937 | 12 | 1 | 620.4082 | 5 | 615.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1937 | 12 | 2 | 403.5918 | 5 | 398.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1937 | 12 | 3 | 292.5714 | 5 | 287.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1937 | 12 | 4 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1937 | 12 | 5 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1937 | 12 | 6 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1937 | 12 | 7 | 1162.449 | 5 | 1157.449 | 27.6751 | 139.3858 | 0.77441 | 26.9007 | 89.27% | 283.4727 | 266.4644 | 6395.1444
1937 | 12 | 8 | 1182.0408 | 5 | 1177.0408 | 27.6359 | 139.3858 | 0.77441 | 26.8615 | 89.27% | 283.0598 | 266.0762 | 6385.8292
1937 | 12 | 9 | 633.4694 | 5 | 628.4694 | 28.7331 | 139.3858 | 0.77441 | 27.9587 | 89.27% | 294.6212 | 276.9439 | 6646.6548
1937 | 12 | 10 | 403.5918 | 5 | 398.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1937 | 12 | 11 | 292.5714 | 5 | 287.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1937 | 12 | 12 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1937 | 12 | 13 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1937 | 12 | 14 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1937 | 12 | 15 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1937 | 12 | 16 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1937 | 12 | 17 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1937 | 12 | 18 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1937 | 12 | 19 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1937 | 12 | 20 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1937 | 12 | 21 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1937 | 12 | 22 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1937 | 12 | 23 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1937 | 12 | 24 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1937 | 12 | 25 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1937 | 12 | 26 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1937 | 12 | 27 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1937 | 12 | 28 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1937 | 12 | 29 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1937 | 12 | 30 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1937 | 12 | 31 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1938 | 1 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1938 | 1 | 2 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1938 | 1 | 3 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1938 | 1 | 4 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1938 | 1 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1938 | 1 | 6 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1938 | 1 | 7 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1938 | 1 | 8 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1938 | 1 | 9 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1938 | 1 | 10 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1938 | 1 | 11 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1938 | 1 | 12 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1938 | 1 | 13 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1938 | 1 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1938 | 1 | 15 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1938 | 1 | 16 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1938 | 1 | 17 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1938 | 1 | 18 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1938 | 1 | 19 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1938 | 1 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1938 | 1 | 21 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1938 | 1 | 22 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1938 | 1 | 23 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1938 | 1 | 24 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1938 | 1 | 25 | 1841.6327 | 5 | 1836.6327 | 26.3167 | 139.3858 | 0.77441 | 25.5423 | 89.27% | 269.1586 | 253.0091 | 6072.2176
1938 | 1 | 26 | 2899.5918 | 5 | 2894.5918 | 24.2008 | 0 | 0 | 24.2008 | 0% | 0 | 0 | 0
1938 | 1 | 27 | 1266.9388 | 5 | 1261.9388 | 27.4661 | 139.3858 | 0.77441 | 26.6917 | 89.27% | 281.2705 | 264.3943 | 6345.4634
1938 | 1 | 28 | 659.5918 | 5 | 654.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1938 | 1 | 29 | 421.8776 | 5 | 416.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1938 | 1 | 30 | 318.6939 | 5 | 313.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1938 | 1 | 31 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1938 | 2 | 1 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1938 | 2 | 2 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1938 | 2 | 3 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1938 | 2 | 4 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1938 | 2 | 5 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1938 | 2 | 6 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1938 | 2 | 7 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1938 | 2 | 8 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1938 | 2 | 9 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1938 | 2 | 10 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1938 | 2 | 11 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1938 | 2 | 12 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1938 | 2 | 13 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1938 | 2 | 14 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1938 | 2 | 15 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1938 | 2 | 16 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1938 | 2 | 17 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1938 | 2 | 18 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1938 | 2 | 19 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1938 | 2 | 20 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1938 | 2 | 21 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1938 | 2 | 22 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1938 | 2 | 23 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1938 | 2 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1938 | 2 | 25 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1938 | 2 | 26 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1938 | 2 | 27 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1938 | 2 | 28 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1938 | 3 | 1 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1938 | 3 | 2 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1938 | 3 | 3 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1938 | 3 | 4 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1938 | 3 | 5 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1938 | 3 | 6 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1938 | 3 | 7 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1938 | 3 | 8 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1938 | 3 | 9 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1938 | 3 | 10 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1938 | 3 | 11 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 12 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 13 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 14 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 15 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 16 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 17 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1938 | 3 | 18 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1938 | 3 | 19 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1938 | 3 | 20 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1938 | 3 | 21 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1938 | 3 | 22 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1938 | 3 | 23 | 801.9592 | 25 | 776.9592 | 28.3961 | 139.3858 | 0.77441 | 27.6217 | 89.27% | 291.0702 | 273.606 | 6566.5441
1938 | 3 | 24 | 1010.9388 | 25 | 985.9388 | 27.9781 | 139.3858 | 0.77441 | 27.2037 | 89.27% | 286.6659 | 269.4659 | 6467.182
1938 | 3 | 25 | 1154.6122 | 25 | 1129.6122 | 27.6908 | 139.3858 | 0.77441 | 26.9164 | 89.27% | 283.6379 | 266.6196 | 6398.8705
1938 | 3 | 26 | 796.7347 | 25 | 771.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1938 | 3 | 27 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1938 | 3 | 28 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1938 | 3 | 29 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1938 | 3 | 30 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1938 | 3 | 31 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1938 | 4 | 1 | 607.3469 | 25 | 582.3469 | 28.7853 | 139.3858 | 0.77441 | 28.0109 | 89.27% | 295.1718 | 277.4615 | 6659.075
1938 | 4 | 2 | 820.2449 | 25 | 795.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
1938 | 4 | 3 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1938 | 4 | 4 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1938 | 4 | 5 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1938 | 4 | 6 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1938 | 4 | 7 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1938 | 4 | 8 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1938 | 4 | 9 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1938 | 4 | 10 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1938 | 4 | 11 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1938 | 4 | 12 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1938 | 4 | 13 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1938 | 4 | 14 | 719.6735 | 25 | 694.6735 | 28.5607 | 139.3858 | 0.77441 | 27.7862 | 89.27% | 292.8044 | 275.2362 | 6605.6679
1938 | 4 | 15 | 986.1224 | 25 | 961.1224 | 28.0278 | 139.3858 | 0.77441 | 27.2533 | 89.27% | 287.1889 | 269.9576 | 6478.9812
1938 | 4 | 16 | 1132.4082 | 25 | 1107.4082 | 27.7352 | 139.3858 | 0.77441 | 26.9608 | 89.27% | 284.1058 | 267.0595 | 6409.4277
1938 | 4 | 17 | 820.2449 | 25 | 795.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
1938 | 4 | 18 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1938 | 4 | 19 | 602.1224 | 25 | 577.1224 | 28.7958 | 139.3858 | 0.77441 | 28.0213 | 89.27% | 295.2819 | 277.565 | 6661.5591
1938 | 4 | 20 | 574.6939 | 25 | 549.6939 | 28.8506 | 139.3858 | 0.77441 | 28.0762 | 89.27% | 295.8599 | 278.1083 | 6674.6004
1938 | 4 | 21 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1938 | 4 | 22 | 410.1224 | 25 | 385.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1938 | 4 | 23 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1938 | 4 | 24 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1938 | 4 | 25 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1938 | 4 | 26 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1938 | 4 | 27 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1938 | 4 | 28 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1938 | 4 | 29 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1938 | 4 | 30 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1938 | 5 | 1 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1938 | 5 | 2 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1938 | 5 | 3 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1938 | 5 | 4 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1938 | 5 | 5 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1938 | 5 | 6 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1938 | 5 | 7 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1938 | 5 | 8 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1938 | 5 | 9 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1938 | 5 | 10 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1938 | 5 | 11 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1938 | 5 | 12 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1938 | 5 | 13 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1938 | 5 | 14 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1938 | 5 | 15 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1938 | 5 | 16 | 784.9796 | 25 | 759.9796 | 28.43 | 139.3858 | 0.77441 | 27.6556 | 89.27% | 291.4281 | 273.9424 | 6574.6172
1938 | 5 | 17 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1938 | 5 | 18 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1938 | 5 | 19 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1938 | 5 | 20 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1938 | 5 | 21 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1938 | 5 | 22 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1938 | 5 | 23 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1938 | 5 | 24 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1938 | 5 | 25 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1938 | 5 | 26 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1938 | 5 | 27 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1938 | 5 | 28 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1938 | 5 | 29 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1938 | 5 | 30 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1938 | 5 | 31 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1938 | 6 | 1 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1938 | 6 | 2 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1938 | 6 | 3 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1938 | 6 | 4 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1938 | 6 | 5 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1938 | 6 | 6 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1938 | 6 | 7 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1938 | 6 | 8 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1938 | 6 | 9 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1938 | 6 | 10 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1938 | 6 | 11 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1938 | 6 | 12 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1938 | 6 | 13 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1938 | 6 | 14 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1938 | 6 | 15 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1938 | 6 | 16 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1938 | 6 | 17 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1938 | 6 | 18 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1938 | 6 | 19 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1938 | 6 | 20 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1938 | 6 | 21 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1938 | 6 | 22 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1938 | 6 | 23 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1938 | 6 | 24 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1938 | 6 | 25 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1938 | 6 | 26 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1938 | 6 | 27 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1938 | 6 | 28 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1938 | 6 | 29 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1938 | 6 | 30 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1938 | 7 | 1 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1938 | 7 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1938 | 7 | 3 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1938 | 7 | 4 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1938 | 7 | 5 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1938 | 7 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1938 | 7 | 7 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1938 | 7 | 8 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1938 | 7 | 9 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1938 | 7 | 10 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1938 | 7 | 11 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1938 | 7 | 12 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1938 | 7 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1938 | 7 | 14 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1938 | 7 | 15 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1938 | 7 | 16 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1938 | 7 | 17 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1938 | 7 | 18 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1938 | 7 | 19 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1938 | 7 | 20 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1938 | 7 | 21 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1938 | 7 | 22 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1938 | 7 | 23 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1938 | 7 | 24 | 927.3469 | 5 | 922.3469 | 28.1453 | 139.3858 | 0.77441 | 27.3709 | 89.27% | 288.4276 | 271.122 | 6506.9268
1938 | 7 | 25 | 437.551 | 5 | 432.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1938 | 7 | 26 | 239.0204 | 5 | 234.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1938 | 7 | 27 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1938 | 7 | 28 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1938 | 7 | 29 | 966.5306 | 5 | 961.5306 | 28.0669 | 139.3858 | 0.77441 | 27.2925 | 89.27% | 287.6018 | 270.3457 | 6488.2964
1938 | 7 | 30 | 685.7143 | 5 | 680.7143 | 28.6286 | 139.3858 | 0.77441 | 27.8542 | 89.27% | 293.5201 | 275.9089 | 6621.8142
1938 | 7 | 31 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1938 | 8 | 1 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1938 | 8 | 2 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1938 | 8 | 3 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1938 | 8 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1938 | 8 | 5 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1938 | 8 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1938 | 8 | 7 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1938 | 8 | 8 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1938 | 8 | 9 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1938 | 8 | 10 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1938 | 8 | 11 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1938 | 8 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1938 | 8 | 13 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1938 | 8 | 14 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1938 | 8 | 15 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1938 | 8 | 16 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1938 | 8 | 17 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1938 | 8 | 18 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1938 | 8 | 19 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1938 | 8 | 20 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1938 | 8 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1938 | 8 | 22 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1938 | 8 | 23 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1938 | 8 | 24 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1938 | 8 | 25 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1938 | 8 | 26 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1938 | 8 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1938 | 8 | 28 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1938 | 8 | 29 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1938 | 8 | 30 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1938 | 8 | 31 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1938 | 9 | 1 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1938 | 9 | 2 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1938 | 9 | 3 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1938 | 9 | 4 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1938 | 9 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1938 | 9 | 6 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1938 | 9 | 7 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1938 | 9 | 8 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1938 | 9 | 9 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1938 | 9 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1938 | 9 | 11 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1938 | 9 | 12 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1938 | 9 | 13 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1938 | 9 | 14 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1938 | 9 | 15 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1938 | 9 | 16 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1938 | 9 | 17 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1938 | 9 | 18 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1938 | 9 | 19 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1938 | 9 | 20 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1938 | 9 | 21 | 816.3265 | 15 | 801.3265 | 28.3673 | 139.3858 | 0.77441 | 27.5929 | 89.27% | 290.7674 | 273.3214 | 6559.7129
1938 | 9 | 22 | 803.2653 | 15 | 788.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1938 | 9 | 23 | 398.3673 | 15 | 383.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1938 | 9 | 24 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1938 | 9 | 25 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1938 | 9 | 26 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1938 | 9 | 27 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1938 | 9 | 28 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1938 | 9 | 29 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1938 | 9 | 30 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1938 | 10 | 1 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1938 | 10 | 2 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1938 | 10 | 3 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1938 | 10 | 4 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1938 | 10 | 5 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1938 | 10 | 6 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1938 | 10 | 7 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1938 | 10 | 8 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1938 | 10 | 9 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1938 | 10 | 10 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1938 | 10 | 11 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1938 | 10 | 12 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1938 | 10 | 13 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1938 | 10 | 14 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1938 | 10 | 15 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1938 | 10 | 16 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1938 | 10 | 17 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1938 | 10 | 18 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1938 | 10 | 19 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1938 | 10 | 20 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1938 | 10 | 21 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1938 | 10 | 22 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1938 | 10 | 23 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1938 | 10 | 24 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1938 | 10 | 25 | 809.7959 | 15 | 794.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
1938 | 10 | 26 | 404.898 | 15 | 389.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1938 | 10 | 27 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1938 | 10 | 28 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1938 | 10 | 29 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1938 | 10 | 30 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1938 | 10 | 31 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1938 | 11 | 1 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1938 | 11 | 2 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1938 | 11 | 3 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1938 | 11 | 4 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1938 | 11 | 5 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1938 | 11 | 6 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1938 | 11 | 7 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1938 | 11 | 8 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1938 | 11 | 9 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1938 | 11 | 10 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1938 | 11 | 11 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1938 | 11 | 12 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1938 | 11 | 13 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1938 | 11 | 14 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1938 | 11 | 15 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1938 | 11 | 16 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1938 | 11 | 17 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1938 | 11 | 18 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1938 | 11 | 19 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1938 | 11 | 20 | 339.5918 | 15 | 324.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1938 | 11 | 21 | 239.0204 | 15 | 224.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1938 | 11 | 22 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1938 | 11 | 23 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1938 | 11 | 24 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1938 | 11 | 25 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1938 | 11 | 26 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1938 | 11 | 27 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1938 | 11 | 28 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1938 | 11 | 29 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1938 | 11 | 30 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1938 | 12 | 1 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1938 | 12 | 2 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1938 | 12 | 3 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1938 | 12 | 4 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1938 | 12 | 5 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1938 | 12 | 6 | 1221.2245 | 5 | 1216.2245 | 27.5576 | 139.3858 | 0.77441 | 26.7831 | 89.27% | 282.234 | 265.3 | 6367.1988
1938 | 12 | 7 | 894.6939 | 5 | 889.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1938 | 12 | 8 | 672.6531 | 5 | 667.6531 | 28.6547 | 139.3858 | 0.77441 | 27.8803 | 89.27% | 293.7954 | 276.1677 | 6628.0244
1938 | 12 | 9 | 633.4694 | 5 | 628.4694 | 28.7331 | 139.3858 | 0.77441 | 27.9587 | 89.27% | 294.6212 | 276.9439 | 6646.6548
1938 | 12 | 10 | 1155.9184 | 5 | 1150.9184 | 27.6882 | 139.3858 | 0.77441 | 26.9138 | 89.27% | 283.6104 | 266.5937 | 6398.2495
1938 | 12 | 11 | 1051.4286 | 5 | 1046.4286 | 27.8971 | 139.3858 | 0.77441 | 27.1227 | 89.27% | 285.8125 | 268.6638 | 6447.9306
1938 | 12 | 12 | 633.4694 | 5 | 628.4694 | 28.7331 | 139.3858 | 0.77441 | 27.9587 | 89.27% | 294.6212 | 276.9439 | 6646.6548
1938 | 12 | 13 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1938 | 12 | 14 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1938 | 12 | 15 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1938 | 12 | 16 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1938 | 12 | 17 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1938 | 12 | 18 | 214.2041 | 5 | 209.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1938 | 12 | 19 | 214.2041 | 5 | 209.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1938 | 12 | 20 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1938 | 12 | 21 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1938 | 12 | 22 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1938 | 12 | 23 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1938 | 12 | 24 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1938 | 12 | 25 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1938 | 12 | 26 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1938 | 12 | 27 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1938 | 12 | 28 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1938 | 12 | 29 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1938 | 12 | 30 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1938 | 12 | 31 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1939 | 1 | 1 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1939 | 1 | 2 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1939 | 1 | 3 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1939 | 1 | 4 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1939 | 1 | 5 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1939 | 1 | 6 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1939 | 1 | 7 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1939 | 1 | 8 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1939 | 1 | 9 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1939 | 1 | 10 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1939 | 1 | 11 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1939 | 1 | 12 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1939 | 1 | 13 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1939 | 1 | 14 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1939 | 1 | 15 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1939 | 1 | 16 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1939 | 1 | 17 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1939 | 1 | 18 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1939 | 1 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1939 | 1 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1939 | 1 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1939 | 1 | 22 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1939 | 1 | 23 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1939 | 1 | 24 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1939 | 1 | 25 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1939 | 1 | 26 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1939 | 1 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1939 | 1 | 28 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1939 | 1 | 29 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1939 | 1 | 30 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1939 | 1 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1939 | 2 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 2 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1939 | 2 | 3 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 4 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 5 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1939 | 2 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1939 | 2 | 7 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1939 | 2 | 8 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1939 | 2 | 9 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 10 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 11 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 12 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 13 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 14 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1939 | 2 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1939 | 2 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1939 | 2 | 17 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1939 | 2 | 18 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1939 | 2 | 19 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1939 | 2 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1939 | 2 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1939 | 2 | 22 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1939 | 2 | 23 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1939 | 2 | 24 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1939 | 2 | 25 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1939 | 2 | 26 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1939 | 2 | 27 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1939 | 2 | 28 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1939 | 3 | 1 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1939 | 3 | 2 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1939 | 3 | 3 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1939 | 3 | 4 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1939 | 3 | 5 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1939 | 3 | 6 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1939 | 3 | 7 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1939 | 3 | 8 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1939 | 3 | 9 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1939 | 3 | 10 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1939 | 3 | 11 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1939 | 3 | 12 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1939 | 3 | 13 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1939 | 3 | 14 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1939 | 3 | 15 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1939 | 3 | 16 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1939 | 3 | 17 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1939 | 3 | 18 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1939 | 3 | 19 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1939 | 3 | 20 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1939 | 3 | 21 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1939 | 3 | 22 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1939 | 3 | 23 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1939 | 3 | 24 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1939 | 3 | 25 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1939 | 3 | 26 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1939 | 3 | 27 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1939 | 3 | 28 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1939 | 3 | 29 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1939 | 3 | 30 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1939 | 3 | 31 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1939 | 4 | 1 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1939 | 4 | 2 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1939 | 4 | 3 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1939 | 4 | 4 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1939 | 4 | 5 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1939 | 4 | 6 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1939 | 4 | 7 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1939 | 4 | 8 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1939 | 4 | 9 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1939 | 4 | 10 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1939 | 4 | 11 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1939 | 4 | 12 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1939 | 4 | 13 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1939 | 4 | 14 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1939 | 4 | 15 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1939 | 4 | 16 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1939 | 4 | 17 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1939 | 4 | 18 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
1939 | 4 | 19 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1939 | 4 | 20 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
1939 | 4 | 21 | 1684.898 | 25 | 1659.898 | 26.6302 | 139.3858 | 0.77441 | 25.8558 | 89.27% | 272.4618 | 256.1141 | 6146.7392
1939 | 4 | 22 | 1802.449 | 25 | 1777.449 | 26.3951 | 139.3858 | 0.77441 | 25.6207 | 89.27% | 269.9844 | 253.7853 | 6090.848
1939 | 4 | 23 | 2037.551 | 25 | 2012.551 | 25.9249 | 139.3858 | 0.77441 | 25.1505 | 89.27% | 265.0295 | 249.1277 | 5979.0656
1939 | 4 | 24 | 1946.1224 | 25 | 1921.1224 | 26.1078 | 139.3858 | 0.77441 | 25.3333 | 89.27% | 266.9564 | 250.939 | 6022.5365
1939 | 4 | 25 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1939 | 4 | 26 | 1246.0408 | 25 | 1221.0408 | 27.5079 | 139.3858 | 0.77441 | 26.7335 | 89.27% | 281.711 | 264.8083 | 6355.3996
1939 | 4 | 27 | 991.3469 | 25 | 966.3469 | 28.0173 | 139.3858 | 0.77441 | 27.2429 | 89.27% | 287.0788 | 269.854 | 6476.4972
1939 | 4 | 28 | 1018.7755 | 25 | 993.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
1939 | 4 | 29 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1939 | 4 | 30 | 1269.551 | 25 | 1244.551 | 27.4609 | 139.3858 | 0.77441 | 26.6865 | 89.27% | 281.2155 | 264.3426 | 6344.2214
1939 | 5 | 1 | 1111.5102 | 25 | 1086.5102 | 27.777 | 139.3858 | 0.77441 | 27.0026 | 89.27% | 284.5463 | 267.4735 | 6419.3639
1939 | 5 | 2 | 971.7551 | 25 | 946.7551 | 28.0565 | 139.3858 | 0.77441 | 27.2821 | 89.27% | 287.4917 | 270.2422 | 6485.8124
1939 | 5 | 3 | 952.1633 | 25 | 927.1633 | 28.0957 | 139.3858 | 0.77441 | 27.3213 | 89.27% | 287.9046 | 270.6303 | 6495.1276
1939 | 5 | 4 | 991.3469 | 25 | 966.3469 | 28.0173 | 139.3858 | 0.77441 | 27.2429 | 89.27% | 287.0788 | 269.854 | 6476.4972
1939 | 5 | 5 | 932.5714 | 25 | 907.5714 | 28.1349 | 139.3858 | 0.77441 | 27.3604 | 89.27% | 288.3175 | 271.0184 | 6504.4428
1939 | 5 | 6 | 820.2449 | 25 | 795.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
1939 | 5 | 7 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1939 | 5 | 8 | 820.2449 | 25 | 795.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
1939 | 5 | 9 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1939 | 5 | 10 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1939 | 5 | 11 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1939 | 5 | 12 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1939 | 5 | 13 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1939 | 5 | 14 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1939 | 5 | 15 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1939 | 5 | 16 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1939 | 5 | 17 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1939 | 5 | 18 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1939 | 5 | 19 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1939 | 5 | 20 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1939 | 5 | 21 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1939 | 5 | 22 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1939 | 5 | 23 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1939 | 5 | 24 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1939 | 5 | 25 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1939 | 5 | 26 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1939 | 5 | 27 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1939 | 5 | 28 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1939 | 5 | 29 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1939 | 5 | 30 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1939 | 5 | 31 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1939 | 6 | 1 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1939 | 6 | 2 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1939 | 6 | 3 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1939 | 6 | 4 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1939 | 6 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1939 | 6 | 6 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1939 | 6 | 7 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1939 | 6 | 8 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1939 | 6 | 9 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1939 | 6 | 10 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1939 | 6 | 11 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1939 | 6 | 12 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1939 | 6 | 13 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1939 | 6 | 14 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1939 | 6 | 15 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1939 | 6 | 16 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1939 | 6 | 17 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1939 | 6 | 18 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1939 | 6 | 19 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1939 | 6 | 20 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1939 | 6 | 21 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1939 | 6 | 22 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1939 | 6 | 23 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1939 | 6 | 24 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1939 | 6 | 25 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1939 | 6 | 26 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1939 | 6 | 27 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1939 | 6 | 28 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1939 | 6 | 29 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1939 | 6 | 30 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1939 | 7 | 1 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1939 | 7 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1939 | 7 | 3 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1939 | 7 | 4 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1939 | 7 | 5 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1939 | 7 | 6 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1939 | 7 | 7 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1939 | 7 | 8 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1939 | 7 | 9 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1939 | 7 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1939 | 7 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1939 | 7 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1939 | 7 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 7 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1939 | 7 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 7 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1939 | 7 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1939 | 7 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1939 | 7 | 19 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 7 | 20 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 7 | 21 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1939 | 7 | 22 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1939 | 7 | 23 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1939 | 7 | 24 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1939 | 7 | 25 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1939 | 7 | 26 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1939 | 7 | 27 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1939 | 7 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1939 | 7 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 7 | 30 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 7 | 31 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1939 | 8 | 1 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1939 | 8 | 2 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1939 | 8 | 3 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1939 | 8 | 4 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1939 | 8 | 5 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1939 | 8 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1939 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 8 | 8 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 8 | 9 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 8 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1939 | 8 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1939 | 8 | 12 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 8 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1939 | 8 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1939 | 8 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1939 | 8 | 16 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 8 | 17 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 8 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1939 | 8 | 19 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1939 | 8 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1939 | 8 | 21 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1939 | 8 | 22 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1939 | 8 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1939 | 8 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1939 | 8 | 25 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1939 | 8 | 26 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1939 | 8 | 27 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1939 | 8 | 28 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1939 | 8 | 29 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1939 | 8 | 30 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 8 | 31 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1939 | 9 | 1 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1939 | 9 | 2 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1939 | 9 | 3 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 9 | 4 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 9 | 5 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 9 | 6 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1939 | 9 | 7 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1939 | 9 | 8 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 9 | 9 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1939 | 9 | 10 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1939 | 9 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1939 | 9 | 12 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 9 | 13 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 9 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1939 | 9 | 15 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1939 | 9 | 16 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1939 | 9 | 17 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1939 | 9 | 18 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1939 | 9 | 19 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1939 | 9 | 20 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1939 | 9 | 21 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1939 | 9 | 22 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1939 | 9 | 23 | 5.8776 | 15 | 0 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1939 | 9 | 24 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1939 | 9 | 25 | 4.8327 | 15 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1939 | 9 | 26 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1939 | 9 | 27 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1939 | 9 | 28 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1939 | 9 | 29 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 9 | 30 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1939 | 10 | 1 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1939 | 10 | 2 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1939 | 10 | 3 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1939 | 10 | 4 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1939 | 10 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1939 | 10 | 6 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1939 | 10 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1939 | 10 | 8 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1939 | 10 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1939 | 10 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1939 | 10 | 11 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1939 | 10 | 12 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1939 | 10 | 13 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1939 | 10 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1939 | 10 | 15 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 10 | 16 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1939 | 10 | 17 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1939 | 10 | 18 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1939 | 10 | 19 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 10 | 20 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1939 | 10 | 21 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1939 | 10 | 22 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1939 | 10 | 23 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1939 | 10 | 24 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1939 | 10 | 25 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1939 | 10 | 26 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1939 | 10 | 27 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1939 | 10 | 28 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 10 | 29 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1939 | 10 | 30 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1939 | 10 | 31 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1939 | 11 | 1 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1939 | 11 | 2 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1939 | 11 | 3 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1939 | 11 | 4 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1939 | 11 | 5 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1939 | 11 | 6 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1939 | 11 | 7 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1939 | 11 | 8 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1939 | 11 | 9 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1939 | 11 | 10 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1939 | 11 | 11 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1939 | 11 | 12 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1939 | 11 | 13 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1939 | 11 | 14 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1939 | 11 | 15 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1939 | 11 | 16 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1939 | 11 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1939 | 11 | 18 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1939 | 11 | 19 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1939 | 11 | 20 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 11 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 11 | 22 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1939 | 11 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1939 | 11 | 24 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1939 | 11 | 25 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1939 | 11 | 26 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1939 | 11 | 27 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1939 | 11 | 28 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1939 | 11 | 29 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1939 | 11 | 30 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1939 | 12 | 1 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1939 | 12 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1939 | 12 | 3 | 424.4898 | 5 | 419.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1939 | 12 | 4 | 391.8367 | 5 | 386.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1939 | 12 | 5 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1939 | 12 | 6 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1939 | 12 | 7 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1939 | 12 | 8 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1939 | 12 | 9 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1939 | 12 | 10 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1939 | 12 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1939 | 12 | 12 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1939 | 12 | 13 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1939 | 12 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1939 | 12 | 15 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1939 | 12 | 16 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1939 | 12 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1939 | 12 | 18 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1939 | 12 | 19 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1939 | 12 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1939 | 12 | 21 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1939 | 12 | 22 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1939 | 12 | 23 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1939 | 12 | 24 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1939 | 12 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1939 | 12 | 26 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1939 | 12 | 27 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1939 | 12 | 28 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1939 | 12 | 29 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1939 | 12 | 30 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1939 | 12 | 31 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1940 | 1 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1940 | 1 | 2 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1940 | 1 | 3 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1940 | 1 | 4 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1940 | 1 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 1 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 1 | 7 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1940 | 1 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 1 | 9 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 1 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 1 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1940 | 1 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 1 | 13 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 1 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 1 | 15 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 1 | 16 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 1 | 17 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1940 | 1 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1940 | 1 | 19 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1940 | 1 | 20 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1940 | 1 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1940 | 1 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1940 | 1 | 23 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 1 | 24 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1940 | 1 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 1 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 1 | 27 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1940 | 1 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 1 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 1 | 30 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 1 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1940 | 2 | 1 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 2 | 2 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 2 | 3 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1940 | 2 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1940 | 2 | 5 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1940 | 2 | 6 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1940 | 2 | 7 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1940 | 2 | 8 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1940 | 2 | 9 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1940 | 2 | 10 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1940 | 2 | 11 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 2 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1940 | 2 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1940 | 2 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 21 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 24 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 2 | 27 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 28 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 2 | 29 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 3 | 1 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 3 | 2 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 3 | 3 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 3 | 4 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 3 | 5 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1940 | 3 | 6 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1940 | 3 | 7 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1940 | 3 | 8 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1940 | 3 | 9 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1940 | 3 | 10 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1940 | 3 | 11 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1940 | 3 | 12 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1940 | 3 | 13 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1940 | 3 | 14 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1940 | 3 | 15 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 16 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1940 | 3 | 17 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1940 | 3 | 18 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1940 | 3 | 19 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 20 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 21 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 22 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1940 | 3 | 23 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1940 | 3 | 24 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 25 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1940 | 3 | 26 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 27 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 28 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1940 | 3 | 29 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1940 | 3 | 30 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1940 | 3 | 31 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1940 | 4 | 1 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1940 | 4 | 2 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1940 | 4 | 3 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1940 | 4 | 4 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1940 | 4 | 5 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1940 | 4 | 6 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1940 | 4 | 7 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1940 | 4 | 8 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1940 | 4 | 9 | 496.3265 | 25 | 471.3265 | 29.0073 | 139.3858 | 0.77441 | 28.2329 | 89.27% | 297.5116 | 279.6609 | 6711.8611
1940 | 4 | 10 | 838.5306 | 25 | 813.5306 | 28.3229 | 139.3858 | 0.77441 | 27.5485 | 89.27% | 290.2995 | 272.8815 | 6549.1557
1940 | 4 | 11 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1940 | 4 | 12 | 1090.6122 | 25 | 1065.6122 | 27.8188 | 139.3858 | 0.77441 | 27.0444 | 89.27% | 284.9867 | 267.8875 | 6429.3002
1940 | 4 | 13 | 2442.449 | 25 | 2417.449 | 25.1151 | 139.3858 | 0.77441 | 24.3407 | 89.27% | 256.4961 | 241.1063 | 5786.5515
1940 | 4 | 14 | 1475.9184 | 25 | 1450.9184 | 27.0482 | 139.3858 | 0.77441 | 26.2738 | 89.27% | 276.8662 | 260.2542 | 6246.1013
1940 | 4 | 15 | 820.2449 | 25 | 795.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
1940 | 4 | 16 | 587.7551 | 25 | 562.7551 | 28.8245 | 139.3858 | 0.77441 | 28.0501 | 89.27% | 295.5847 | 277.8496 | 6668.3902
1940 | 4 | 17 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1940 | 4 | 18 | 616.4898 | 25 | 591.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
1940 | 4 | 19 | 784.9796 | 25 | 759.9796 | 28.43 | 139.3858 | 0.77441 | 27.6556 | 89.27% | 291.4281 | 273.9424 | 6574.6172
1940 | 4 | 20 | 991.3469 | 25 | 966.3469 | 28.0173 | 139.3858 | 0.77441 | 27.2429 | 89.27% | 287.0788 | 269.854 | 6476.4972
1940 | 4 | 21 | 914.2857 | 25 | 889.2857 | 28.1714 | 139.3858 | 0.77441 | 27.397 | 89.27% | 288.7029 | 271.3807 | 6513.1369
1940 | 4 | 22 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1940 | 4 | 23 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1940 | 4 | 24 | 616.4898 | 25 | 591.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
1940 | 4 | 25 | 751.0204 | 25 | 726.0204 | 28.498 | 139.3858 | 0.77441 | 27.7235 | 89.27% | 292.1438 | 274.6151 | 6590.7636
1940 | 4 | 26 | 856.8163 | 25 | 831.8163 | 28.2864 | 139.3858 | 0.77441 | 27.512 | 89.27% | 289.9141 | 272.5192 | 6540.4615
1940 | 4 | 27 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1940 | 4 | 28 | 971.7551 | 25 | 946.7551 | 28.0565 | 139.3858 | 0.77441 | 27.2821 | 89.27% | 287.4917 | 270.2422 | 6485.8124
1940 | 4 | 29 | 1090.6122 | 25 | 1065.6122 | 27.8188 | 139.3858 | 0.77441 | 27.0444 | 89.27% | 284.9867 | 267.8875 | 6429.3002
1940 | 4 | 30 | 1176.8163 | 25 | 1151.8163 | 27.6464 | 139.3858 | 0.77441 | 26.872 | 89.27% | 283.1699 | 266.1797 | 6388.3133
1940 | 5 | 1 | 1246.0408 | 25 | 1221.0408 | 27.5079 | 139.3858 | 0.77441 | 26.7335 | 89.27% | 281.711 | 264.8083 | 6355.3996
1940 | 5 | 2 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1940 | 5 | 3 | 1606.5306 | 25 | 1581.5306 | 26.7869 | 139.3858 | 0.77441 | 26.0125 | 89.27% | 274.1135 | 257.6667 | 6184
1940 | 5 | 4 | 1541.2245 | 25 | 1516.2245 | 26.9176 | 139.3858 | 0.77441 | 26.1431 | 89.27% | 275.4898 | 258.9604 | 6215.0506
1940 | 5 | 5 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1940 | 5 | 6 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1940 | 5 | 7 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1940 | 5 | 8 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1940 | 5 | 9 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1940 | 5 | 10 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1940 | 5 | 11 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1940 | 5 | 12 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1940 | 5 | 13 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1940 | 5 | 14 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1940 | 5 | 15 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1940 | 5 | 16 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1940 | 5 | 17 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1940 | 5 | 18 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1940 | 5 | 19 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1940 | 5 | 20 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1940 | 5 | 21 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1940 | 5 | 22 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1940 | 5 | 23 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1940 | 5 | 24 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1940 | 5 | 25 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1940 | 5 | 26 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1940 | 5 | 27 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1940 | 5 | 28 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1940 | 5 | 29 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1940 | 5 | 30 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1940 | 5 | 31 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1940 | 6 | 1 | 862.0408 | 25 | 837.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
1940 | 6 | 2 | 633.4694 | 25 | 608.4694 | 28.7331 | 139.3858 | 0.77441 | 27.9587 | 89.27% | 294.6212 | 276.9439 | 6646.6548
1940 | 6 | 3 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1940 | 6 | 4 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1940 | 6 | 5 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1940 | 6 | 6 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1940 | 6 | 7 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1940 | 6 | 8 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1940 | 6 | 9 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1940 | 6 | 10 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1940 | 6 | 11 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1940 | 6 | 12 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1940 | 6 | 13 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1940 | 6 | 14 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1940 | 6 | 15 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1940 | 6 | 16 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1940 | 6 | 17 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1940 | 6 | 18 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1940 | 6 | 19 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1940 | 6 | 20 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1940 | 6 | 21 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1940 | 6 | 22 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1940 | 6 | 23 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1940 | 6 | 24 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1940 | 6 | 25 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1940 | 6 | 26 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1940 | 6 | 27 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1940 | 6 | 28 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1940 | 6 | 29 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1940 | 6 | 30 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1940 | 7 | 1 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1940 | 7 | 2 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1940 | 7 | 3 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1940 | 7 | 4 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1940 | 7 | 5 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1940 | 7 | 6 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1940 | 7 | 7 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1940 | 7 | 8 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1940 | 7 | 9 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1940 | 7 | 10 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1940 | 7 | 11 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1940 | 7 | 12 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1940 | 7 | 13 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1940 | 7 | 14 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1940 | 7 | 15 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1940 | 7 | 16 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1940 | 7 | 17 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1940 | 7 | 18 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1940 | 7 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1940 | 7 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 7 | 21 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1940 | 7 | 22 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 7 | 23 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 7 | 24 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1940 | 7 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 7 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 7 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1940 | 7 | 29 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 7 | 30 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1940 | 7 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1940 | 8 | 1 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1940 | 8 | 2 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1940 | 8 | 3 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1940 | 8 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 8 | 5 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1940 | 8 | 6 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1940 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1940 | 8 | 8 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1940 | 8 | 9 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 8 | 10 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 8 | 11 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1940 | 8 | 12 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1940 | 8 | 13 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1940 | 8 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 8 | 15 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 8 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1940 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 8 | 18 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1940 | 8 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 8 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1940 | 8 | 21 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1940 | 8 | 22 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 8 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 8 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1940 | 8 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1940 | 8 | 26 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1940 | 8 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1940 | 8 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1940 | 8 | 29 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1940 | 8 | 30 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1940 | 8 | 31 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1940 | 9 | 1 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 9 | 2 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 9 | 3 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1940 | 9 | 4 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1940 | 9 | 5 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1940 | 9 | 6 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1940 | 9 | 7 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1940 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1940 | 9 | 9 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1940 | 9 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 9 | 11 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1940 | 9 | 12 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1940 | 9 | 13 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1940 | 9 | 14 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1940 | 9 | 15 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 9 | 16 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 9 | 17 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1940 | 9 | 18 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1940 | 9 | 19 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 9 | 20 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1940 | 9 | 21 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 9 | 22 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 9 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1940 | 9 | 24 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1940 | 9 | 25 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1940 | 9 | 26 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1940 | 9 | 27 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1940 | 9 | 28 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1940 | 9 | 29 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 9 | 30 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 10 | 1 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1940 | 10 | 2 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1940 | 10 | 3 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 10 | 4 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1940 | 10 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 10 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 7 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 8 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 10 | 9 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 10 | 10 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 10 | 11 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 10 | 12 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 10 | 13 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 14 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 16 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 17 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 18 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1940 | 10 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 20 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1940 | 10 | 21 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 10 | 22 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1940 | 10 | 23 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1940 | 10 | 24 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 10 | 25 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 10 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1940 | 10 | 27 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1940 | 10 | 28 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1940 | 10 | 29 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 10 | 30 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 10 | 31 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 11 | 1 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1940 | 11 | 2 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1940 | 11 | 3 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1940 | 11 | 4 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1940 | 11 | 5 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1940 | 11 | 6 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1940 | 11 | 7 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1940 | 11 | 8 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1940 | 11 | 9 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1940 | 11 | 10 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1940 | 11 | 11 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1940 | 11 | 12 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1940 | 11 | 13 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1940 | 11 | 14 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1940 | 11 | 15 | 600.8163 | 15 | 585.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1940 | 11 | 16 | 653.0612 | 15 | 638.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
1940 | 11 | 17 | 397.0612 | 15 | 382.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1940 | 11 | 18 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1940 | 11 | 19 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1940 | 11 | 20 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1940 | 11 | 21 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1940 | 11 | 22 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1940 | 11 | 23 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1940 | 11 | 24 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1940 | 11 | 25 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1940 | 11 | 26 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1940 | 11 | 27 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1940 | 11 | 28 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1940 | 11 | 29 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1940 | 11 | 30 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1940 | 12 | 1 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1940 | 12 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 3 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1940 | 12 | 5 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1940 | 12 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1940 | 12 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1940 | 12 | 8 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1940 | 12 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1940 | 12 | 10 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1940 | 12 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 13 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 14 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 15 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 16 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 17 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 18 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 19 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 20 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 21 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 22 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 23 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 25 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 26 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1940 | 12 | 27 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1940 | 12 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1940 | 12 | 29 | 214.2041 | 5 | 209.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1940 | 12 | 30 | 373.551 | 5 | 368.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1940 | 12 | 31 | 446.6939 | 5 | 441.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1941 | 1 | 1 | 310.8571 | 5 | 305.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1941 | 1 | 2 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1941 | 1 | 3 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1941 | 1 | 4 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1941 | 1 | 5 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1941 | 1 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1941 | 1 | 7 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1941 | 1 | 8 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1941 | 1 | 9 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1941 | 1 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1941 | 1 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1941 | 1 | 12 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1941 | 1 | 13 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1941 | 1 | 14 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1941 | 1 | 15 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1941 | 1 | 16 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1941 | 1 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1941 | 1 | 18 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1941 | 1 | 19 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1941 | 1 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1941 | 1 | 21 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1941 | 1 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1941 | 1 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1941 | 1 | 24 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1941 | 1 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1941 | 1 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1941 | 1 | 27 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1941 | 1 | 28 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1941 | 1 | 29 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1941 | 1 | 30 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1941 | 1 | 31 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1941 | 2 | 1 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1941 | 2 | 2 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1941 | 2 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1941 | 2 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1941 | 2 | 5 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1941 | 2 | 6 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1941 | 2 | 7 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1941 | 2 | 8 | 581.2245 | 5 | 576.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1941 | 2 | 9 | 659.5918 | 5 | 654.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1941 | 2 | 10 | 373.551 | 5 | 368.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1941 | 2 | 11 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1941 | 2 | 12 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1941 | 2 | 13 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1941 | 2 | 14 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1941 | 2 | 15 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1941 | 2 | 16 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1941 | 2 | 17 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1941 | 2 | 18 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1941 | 2 | 19 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1941 | 2 | 20 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1941 | 2 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1941 | 2 | 22 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1941 | 2 | 23 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1941 | 2 | 24 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1941 | 2 | 25 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1941 | 2 | 26 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1941 | 2 | 27 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1941 | 2 | 28 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1941 | 3 | 1 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1941 | 3 | 2 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1941 | 3 | 3 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 3 | 4 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 3 | 5 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1941 | 3 | 6 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1941 | 3 | 7 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1941 | 3 | 8 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1941 | 3 | 9 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1941 | 3 | 10 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 3 | 11 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1941 | 3 | 12 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1941 | 3 | 13 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1941 | 3 | 14 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1941 | 3 | 15 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1941 | 3 | 16 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1941 | 3 | 17 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1941 | 3 | 18 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1941 | 3 | 19 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 3 | 20 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1941 | 3 | 21 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 3 | 22 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1941 | 3 | 23 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1941 | 3 | 24 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1941 | 3 | 25 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1941 | 3 | 26 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1941 | 3 | 27 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1941 | 3 | 28 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1941 | 3 | 29 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1941 | 3 | 30 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1941 | 3 | 31 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1941 | 4 | 1 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1941 | 4 | 2 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1941 | 4 | 3 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1941 | 4 | 4 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1941 | 4 | 5 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1941 | 4 | 6 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1941 | 4 | 7 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1941 | 4 | 8 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1941 | 4 | 9 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1941 | 4 | 10 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1941 | 4 | 11 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1941 | 4 | 12 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1941 | 4 | 13 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1941 | 4 | 14 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1941 | 4 | 15 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1941 | 4 | 16 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1941 | 4 | 17 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1941 | 4 | 18 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1941 | 4 | 19 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1941 | 4 | 20 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1941 | 4 | 21 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1941 | 4 | 22 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1941 | 4 | 23 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1941 | 4 | 24 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1941 | 4 | 25 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1941 | 4 | 26 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1941 | 4 | 27 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1941 | 4 | 28 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1941 | 4 | 29 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1941 | 4 | 30 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1941 | 5 | 1 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1941 | 5 | 2 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1941 | 5 | 3 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1941 | 5 | 4 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1941 | 5 | 5 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1941 | 5 | 6 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1941 | 5 | 7 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1941 | 5 | 8 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1941 | 5 | 9 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1941 | 5 | 10 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1941 | 5 | 11 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1941 | 5 | 12 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1941 | 5 | 13 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1941 | 5 | 14 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1941 | 5 | 15 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1941 | 5 | 16 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1941 | 5 | 17 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1941 | 5 | 18 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 5 | 19 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 5 | 20 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1941 | 5 | 21 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1941 | 5 | 22 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1941 | 5 | 23 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1941 | 5 | 24 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1941 | 5 | 25 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1941 | 5 | 26 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1941 | 5 | 27 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1941 | 5 | 28 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1941 | 5 | 29 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1941 | 5 | 30 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1941 | 5 | 31 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1941 | 6 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1941 | 6 | 2 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1941 | 6 | 3 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 6 | 4 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1941 | 6 | 5 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1941 | 6 | 6 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1941 | 6 | 7 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1941 | 6 | 8 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1941 | 6 | 9 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1941 | 6 | 10 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1941 | 6 | 11 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1941 | 6 | 12 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1941 | 6 | 13 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1941 | 6 | 14 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1941 | 6 | 15 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1941 | 6 | 16 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1941 | 6 | 17 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1941 | 6 | 18 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1941 | 6 | 19 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1941 | 6 | 20 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1941 | 6 | 21 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1941 | 6 | 22 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1941 | 6 | 23 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1941 | 6 | 24 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1941 | 6 | 25 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1941 | 6 | 26 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1941 | 6 | 27 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1941 | 6 | 28 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1941 | 6 | 29 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 6 | 30 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 7 | 1 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 7 | 2 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 7 | 3 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1941 | 7 | 4 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1941 | 7 | 5 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1941 | 7 | 6 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1941 | 7 | 7 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1941 | 7 | 8 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1941 | 7 | 9 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1941 | 7 | 10 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1941 | 7 | 11 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1941 | 7 | 12 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1941 | 7 | 13 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1941 | 7 | 14 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1941 | 7 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1941 | 7 | 16 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1941 | 7 | 17 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1941 | 7 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1941 | 7 | 19 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1941 | 7 | 20 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1941 | 7 | 21 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1941 | 7 | 22 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1941 | 7 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1941 | 7 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1941 | 7 | 25 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1941 | 7 | 26 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1941 | 7 | 27 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1941 | 7 | 28 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1941 | 7 | 29 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1941 | 7 | 30 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1941 | 7 | 31 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1941 | 8 | 1 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1941 | 8 | 2 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 8 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1941 | 8 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1941 | 8 | 5 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 8 | 6 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1941 | 8 | 7 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 8 | 8 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 8 | 9 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 10 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 11 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 12 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 13 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 14 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1941 | 8 | 15 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1941 | 8 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 17 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1941 | 8 | 18 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1941 | 8 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 8 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 8 | 21 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1941 | 8 | 22 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 8 | 23 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 24 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1941 | 8 | 25 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1941 | 8 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 8 | 27 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1941 | 8 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 8 | 29 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1941 | 8 | 30 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1941 | 8 | 31 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1941 | 9 | 1 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1941 | 9 | 2 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1941 | 9 | 3 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1941 | 9 | 4 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1941 | 9 | 5 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1941 | 9 | 6 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1941 | 9 | 7 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1941 | 9 | 8 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1941 | 9 | 9 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1941 | 9 | 10 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1941 | 9 | 11 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 9 | 12 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 9 | 13 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 9 | 14 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1941 | 9 | 15 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 9 | 16 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 9 | 17 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1941 | 9 | 18 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1941 | 9 | 19 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1941 | 9 | 20 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1941 | 9 | 21 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1941 | 9 | 22 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1941 | 9 | 23 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1941 | 9 | 24 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1941 | 9 | 25 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1941 | 9 | 26 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1941 | 9 | 27 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1941 | 9 | 28 | 6.6612 | 15 | 0 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1941 | 9 | 29 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1941 | 9 | 30 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1941 | 10 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1941 | 10 | 2 | 10.7102 | 15 | 0 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1941 | 10 | 3 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1941 | 10 | 4 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 5 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 6 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1941 | 10 | 7 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1941 | 10 | 8 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1941 | 10 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 11 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1941 | 10 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1941 | 10 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1941 | 10 | 14 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1941 | 10 | 15 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1941 | 10 | 16 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1941 | 10 | 17 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1941 | 10 | 18 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 19 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 20 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 21 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1941 | 10 | 22 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 23 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1941 | 10 | 24 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 25 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1941 | 10 | 26 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 10 | 27 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 10 | 28 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1941 | 10 | 29 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1941 | 10 | 30 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1941 | 10 | 31 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1941 | 11 | 1 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1941 | 11 | 2 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1941 | 11 | 3 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1941 | 11 | 4 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1941 | 11 | 5 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1941 | 11 | 6 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1941 | 11 | 7 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1941 | 11 | 8 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1941 | 11 | 9 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1941 | 11 | 10 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1941 | 11 | 11 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1941 | 11 | 12 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1941 | 11 | 13 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1941 | 11 | 14 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1941 | 11 | 15 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1941 | 11 | 16 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1941 | 11 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1941 | 11 | 18 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1941 | 11 | 19 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1941 | 11 | 20 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1941 | 11 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1941 | 11 | 22 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1941 | 11 | 23 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1941 | 11 | 24 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1941 | 11 | 25 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1941 | 11 | 26 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1941 | 11 | 27 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1941 | 11 | 28 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1941 | 11 | 29 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1941 | 11 | 30 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1941 | 12 | 1 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 12 | 2 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1941 | 12 | 3 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 12 | 4 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 12 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1941 | 12 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1941 | 12 | 7 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1941 | 12 | 8 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1941 | 12 | 9 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1941 | 12 | 10 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1941 | 12 | 11 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1941 | 12 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1941 | 12 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 12 | 14 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1941 | 12 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1941 | 12 | 16 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1941 | 12 | 17 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1941 | 12 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1941 | 12 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1941 | 12 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1941 | 12 | 21 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1941 | 12 | 22 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1941 | 12 | 23 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1941 | 12 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1941 | 12 | 25 | 400.9796 | 5 | 395.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1941 | 12 | 26 | 265.1429 | 5 | 260.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1941 | 12 | 27 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1941 | 12 | 28 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1941 | 12 | 29 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1941 | 12 | 30 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1941 | 12 | 31 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1942 | 1 | 1 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1942 | 1 | 2 | 378.7755 | 5 | 373.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1942 | 1 | 3 | 492.4082 | 5 | 487.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1942 | 1 | 4 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1942 | 1 | 5 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1942 | 1 | 6 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1942 | 1 | 7 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1942 | 1 | 8 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1942 | 1 | 9 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1942 | 1 | 10 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1942 | 1 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1942 | 1 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1942 | 1 | 13 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1942 | 1 | 14 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1942 | 1 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1942 | 1 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1942 | 1 | 17 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 1 | 18 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1942 | 1 | 19 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1942 | 1 | 20 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1942 | 1 | 21 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1942 | 1 | 22 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1942 | 1 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1942 | 1 | 24 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1942 | 1 | 25 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1942 | 1 | 26 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1942 | 1 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1942 | 1 | 28 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1942 | 1 | 29 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1942 | 1 | 30 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1942 | 1 | 31 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 2 | 1 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 2 | 2 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1942 | 2 | 3 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1942 | 2 | 4 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 2 | 5 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 2 | 6 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1942 | 2 | 7 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1942 | 2 | 8 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1942 | 2 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1942 | 2 | 10 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1942 | 2 | 11 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1942 | 2 | 12 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1942 | 2 | 13 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1942 | 2 | 14 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 2 | 15 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 2 | 16 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 2 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1942 | 2 | 18 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1942 | 2 | 19 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 2 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 2 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 2 | 22 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1942 | 2 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 2 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 2 | 25 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 2 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 2 | 27 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 2 | 28 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 3 | 1 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1942 | 3 | 2 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1942 | 3 | 3 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1942 | 3 | 4 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1942 | 3 | 5 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1942 | 3 | 6 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1942 | 3 | 7 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1942 | 3 | 8 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1942 | 3 | 9 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1942 | 3 | 10 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1942 | 3 | 11 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1942 | 3 | 12 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1942 | 3 | 13 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1942 | 3 | 14 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1942 | 3 | 15 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1942 | 3 | 16 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1942 | 3 | 17 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1942 | 3 | 18 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1942 | 3 | 19 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1942 | 3 | 20 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1942 | 3 | 21 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1942 | 3 | 22 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1942 | 3 | 23 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1942 | 3 | 24 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1942 | 3 | 25 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1942 | 3 | 26 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1942 | 3 | 27 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1942 | 3 | 28 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1942 | 3 | 29 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1942 | 3 | 30 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1942 | 3 | 31 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1942 | 4 | 1 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1942 | 4 | 2 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1942 | 4 | 3 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1942 | 4 | 4 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1942 | 4 | 5 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1942 | 4 | 6 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1942 | 4 | 7 | 739.2653 | 25 | 714.2653 | 28.5215 | 139.3858 | 0.77441 | 27.7471 | 89.27% | 292.3915 | 274.848 | 6596.3527
1942 | 4 | 8 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1942 | 4 | 9 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1942 | 4 | 10 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1942 | 4 | 11 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1942 | 4 | 12 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1942 | 4 | 13 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1942 | 4 | 14 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1942 | 4 | 15 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1942 | 4 | 16 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1942 | 4 | 17 | 993.9592 | 25 | 968.9592 | 28.0121 | 139.3858 | 0.77441 | 27.2377 | 89.27% | 287.0237 | 269.8023 | 6475.2551
1942 | 4 | 18 | 944.3265 | 25 | 919.3265 | 28.1113 | 139.3858 | 0.77441 | 27.3369 | 89.27% | 288.0698 | 270.7856 | 6498.8536
1942 | 4 | 19 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1942 | 4 | 20 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1942 | 4 | 21 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1942 | 4 | 22 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1942 | 4 | 23 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1942 | 4 | 24 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1942 | 4 | 25 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1942 | 4 | 26 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1942 | 4 | 27 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1942 | 4 | 28 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1942 | 4 | 29 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1942 | 4 | 30 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1942 | 5 | 1 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1942 | 5 | 2 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1942 | 5 | 3 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1942 | 5 | 4 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1942 | 5 | 5 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1942 | 5 | 6 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1942 | 5 | 7 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1942 | 5 | 8 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1942 | 5 | 9 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1942 | 5 | 10 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1942 | 5 | 11 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1942 | 5 | 12 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1942 | 5 | 13 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1942 | 5 | 14 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1942 | 5 | 15 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1942 | 5 | 16 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1942 | 5 | 17 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1942 | 5 | 18 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1942 | 5 | 19 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1942 | 5 | 20 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1942 | 5 | 21 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1942 | 5 | 22 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1942 | 5 | 23 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1942 | 5 | 24 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1942 | 5 | 25 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1942 | 5 | 26 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1942 | 5 | 27 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1942 | 5 | 28 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1942 | 5 | 29 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1942 | 5 | 30 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1942 | 5 | 31 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1942 | 6 | 1 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1942 | 6 | 2 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1942 | 6 | 3 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1942 | 6 | 4 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1942 | 6 | 5 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1942 | 6 | 6 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1942 | 6 | 7 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1942 | 6 | 8 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1942 | 6 | 9 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1942 | 6 | 10 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1942 | 6 | 11 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1942 | 6 | 12 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1942 | 6 | 13 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1942 | 6 | 14 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1942 | 6 | 15 | 2873.4694 | 25 | 2848.4694 | 24.2531 | 0 | 0 | 24.2531 | 0% | 0 | 0 | 0
1942 | 6 | 16 | 1776.3265 | 25 | 1751.3265 | 26.4473 | 139.3858 | 0.77441 | 25.6729 | 89.27% | 270.5349 | 254.3028 | 6103.2683
1942 | 6 | 17 | 2507.7551 | 25 | 2482.7551 | 24.9845 | 0 | 0 | 24.9845 | 0% | 0 | 0 | 0
1942 | 6 | 18 | 2089.7959 | 25 | 2064.7959 | 25.8204 | 139.3858 | 0.77441 | 25.046 | 89.27% | 263.9284 | 248.0927 | 5954.2251
1942 | 6 | 19 | 1044.898 | 25 | 1019.898 | 27.9102 | 139.3858 | 0.77441 | 27.1358 | 89.27% | 285.9502 | 268.7932 | 6451.0356
1942 | 6 | 20 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1942 | 6 | 21 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1942 | 6 | 22 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1942 | 6 | 23 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1942 | 6 | 24 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1942 | 6 | 25 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1942 | 6 | 26 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1942 | 6 | 27 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1942 | 6 | 28 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1942 | 6 | 29 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1942 | 6 | 30 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1942 | 7 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1942 | 7 | 2 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1942 | 7 | 3 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1942 | 7 | 4 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1942 | 7 | 5 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1942 | 7 | 6 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1942 | 7 | 7 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1942 | 7 | 8 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1942 | 7 | 9 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1942 | 7 | 10 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1942 | 7 | 11 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1942 | 7 | 12 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1942 | 7 | 13 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1942 | 7 | 14 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 7 | 15 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1942 | 7 | 16 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 7 | 17 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 7 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 7 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 7 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1942 | 7 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1942 | 7 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1942 | 7 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 7 | 24 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1942 | 7 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1942 | 7 | 26 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1942 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1942 | 7 | 28 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1942 | 7 | 29 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1942 | 7 | 30 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1942 | 7 | 31 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1942 | 8 | 1 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1942 | 8 | 2 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 8 | 3 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1942 | 8 | 4 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1942 | 8 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1942 | 8 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1942 | 8 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1942 | 8 | 8 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1942 | 8 | 9 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1942 | 8 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1942 | 8 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1942 | 8 | 12 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1942 | 8 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1942 | 8 | 14 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1942 | 8 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1942 | 8 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1942 | 8 | 17 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1942 | 8 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 8 | 19 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1942 | 8 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1942 | 8 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1942 | 8 | 22 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1942 | 8 | 23 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1942 | 8 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1942 | 8 | 25 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1942 | 8 | 26 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1942 | 8 | 27 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1942 | 8 | 28 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1942 | 8 | 29 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1942 | 8 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1942 | 8 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1942 | 9 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 9 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 9 | 3 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 9 | 4 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 9 | 5 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 9 | 6 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 9 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1942 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1942 | 9 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1942 | 9 | 10 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1942 | 9 | 11 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1942 | 9 | 12 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1942 | 9 | 13 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1942 | 9 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1942 | 9 | 15 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 9 | 16 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 9 | 17 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1942 | 9 | 18 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1942 | 9 | 19 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1942 | 9 | 20 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1942 | 9 | 21 | 10.7102 | 15 | 0 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1942 | 9 | 22 | 10.7102 | 15 | 0 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1942 | 9 | 23 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1942 | 9 | 24 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1942 | 9 | 25 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1942 | 9 | 26 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1942 | 9 | 27 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1942 | 9 | 28 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1942 | 9 | 29 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1942 | 9 | 30 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1942 | 10 | 1 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1942 | 10 | 2 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1942 | 10 | 3 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1942 | 10 | 4 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1942 | 10 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1942 | 10 | 6 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1942 | 10 | 7 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1942 | 10 | 8 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1942 | 10 | 9 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1942 | 10 | 10 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1942 | 10 | 11 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1942 | 10 | 12 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1942 | 10 | 13 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1942 | 10 | 14 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1942 | 10 | 15 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1942 | 10 | 16 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 10 | 17 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 10 | 18 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1942 | 10 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 10 | 20 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 10 | 21 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1942 | 10 | 22 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1942 | 10 | 23 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1942 | 10 | 24 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1942 | 10 | 25 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1942 | 10 | 26 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1942 | 10 | 27 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1942 | 10 | 28 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1942 | 10 | 29 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1942 | 10 | 30 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1942 | 10 | 31 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1942 | 11 | 1 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1942 | 11 | 2 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1942 | 11 | 3 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1942 | 11 | 4 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1942 | 11 | 5 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1942 | 11 | 6 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1942 | 11 | 7 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1942 | 11 | 8 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1942 | 11 | 9 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1942 | 11 | 10 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1942 | 11 | 11 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1942 | 11 | 12 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1942 | 11 | 13 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1942 | 11 | 14 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1942 | 11 | 15 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1942 | 11 | 16 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1942 | 11 | 17 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1942 | 11 | 18 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1942 | 11 | 19 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1942 | 11 | 20 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1942 | 11 | 21 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1942 | 11 | 22 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1942 | 11 | 23 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1942 | 11 | 24 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1942 | 11 | 25 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1942 | 11 | 26 | 360.4898 | 15 | 345.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1942 | 11 | 27 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1942 | 11 | 28 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1942 | 11 | 29 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1942 | 11 | 30 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1942 | 12 | 1 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1942 | 12 | 2 | 404.898 | 5 | 399.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1942 | 12 | 3 | 677.8776 | 5 | 672.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1942 | 12 | 4 | 373.551 | 5 | 368.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1942 | 12 | 5 | 263.8367 | 5 | 258.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1942 | 12 | 6 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1942 | 12 | 7 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1942 | 12 | 8 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1942 | 12 | 9 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1942 | 12 | 10 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1942 | 12 | 11 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1942 | 12 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1942 | 12 | 13 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1942 | 12 | 14 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1942 | 12 | 15 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1942 | 12 | 16 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1942 | 12 | 17 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1942 | 12 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1942 | 12 | 19 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1942 | 12 | 20 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1942 | 12 | 21 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1942 | 12 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1942 | 12 | 23 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1942 | 12 | 24 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1942 | 12 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 12 | 26 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1942 | 12 | 27 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1942 | 12 | 28 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1942 | 12 | 29 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1942 | 12 | 30 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1942 | 12 | 31 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1943 | 1 | 1 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1943 | 1 | 2 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1943 | 1 | 3 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1943 | 1 | 4 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1943 | 1 | 5 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1943 | 1 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1943 | 1 | 7 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1943 | 1 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1943 | 1 | 9 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1943 | 1 | 10 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1943 | 1 | 11 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1943 | 1 | 12 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 1 | 13 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 1 | 14 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 1 | 15 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1943 | 1 | 16 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 1 | 17 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 1 | 18 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 1 | 19 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 1 | 20 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 1 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 1 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 1 | 23 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1943 | 1 | 24 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1943 | 1 | 25 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1943 | 1 | 26 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1943 | 1 | 27 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1943 | 1 | 28 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1943 | 1 | 29 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1943 | 1 | 30 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 1 | 31 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 2 | 1 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 2 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 2 | 3 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 2 | 4 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1943 | 2 | 5 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 2 | 6 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1943 | 2 | 7 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 2 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 2 | 9 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 2 | 10 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 2 | 11 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 2 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1943 | 2 | 13 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1943 | 2 | 14 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1943 | 2 | 15 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1943 | 2 | 16 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1943 | 2 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1943 | 2 | 18 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 2 | 19 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1943 | 2 | 20 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 2 | 21 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1943 | 2 | 22 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1943 | 2 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1943 | 2 | 24 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1943 | 2 | 25 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1943 | 2 | 26 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1943 | 2 | 27 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1943 | 2 | 28 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1943 | 3 | 1 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1943 | 3 | 2 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1943 | 3 | 3 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1943 | 3 | 4 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1943 | 3 | 5 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1943 | 3 | 6 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1943 | 3 | 7 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1943 | 3 | 8 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1943 | 3 | 9 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1943 | 3 | 10 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1943 | 3 | 11 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1943 | 3 | 12 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1943 | 3 | 13 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1943 | 3 | 14 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1943 | 3 | 15 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1943 | 3 | 16 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1943 | 3 | 17 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1943 | 3 | 18 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1943 | 3 | 19 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1943 | 3 | 20 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1943 | 3 | 21 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1943 | 3 | 22 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1943 | 3 | 23 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1943 | 3 | 24 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1943 | 3 | 25 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1943 | 3 | 26 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1943 | 3 | 27 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1943 | 3 | 28 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1943 | 3 | 29 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1943 | 3 | 30 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1943 | 3 | 31 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1943 | 4 | 1 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1943 | 4 | 2 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1943 | 4 | 3 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1943 | 4 | 4 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1943 | 4 | 5 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1943 | 4 | 6 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1943 | 4 | 7 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1943 | 4 | 8 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1943 | 4 | 9 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1943 | 4 | 10 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1943 | 4 | 11 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1943 | 4 | 12 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1943 | 4 | 13 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1943 | 4 | 14 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1943 | 4 | 15 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1943 | 4 | 16 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1943 | 4 | 17 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1943 | 4 | 18 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1943 | 4 | 19 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1943 | 4 | 20 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1943 | 4 | 21 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1943 | 4 | 22 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1943 | 4 | 23 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1943 | 4 | 24 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1943 | 4 | 25 | 872.4898 | 25 | 847.4898 | 28.255 | 139.3858 | 0.77441 | 27.4806 | 89.27% | 289.5837 | 272.2087 | 6533.0094
1943 | 4 | 26 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1943 | 4 | 27 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1943 | 4 | 28 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1943 | 4 | 29 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1943 | 4 | 30 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1943 | 5 | 1 | 993.9592 | 25 | 968.9592 | 28.0121 | 139.3858 | 0.77441 | 27.2377 | 89.27% | 287.0237 | 269.8023 | 6475.2551
1943 | 5 | 2 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1943 | 5 | 3 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1943 | 5 | 4 | 1071.0204 | 25 | 1046.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
1943 | 5 | 5 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1943 | 5 | 6 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1943 | 5 | 7 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1943 | 5 | 8 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1943 | 5 | 9 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1943 | 5 | 10 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1943 | 5 | 11 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1943 | 5 | 12 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1943 | 5 | 13 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1943 | 5 | 14 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1943 | 5 | 15 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1943 | 5 | 16 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1943 | 5 | 17 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1943 | 5 | 18 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1943 | 5 | 19 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1943 | 5 | 20 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1943 | 5 | 21 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1943 | 5 | 22 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1943 | 5 | 23 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1943 | 5 | 24 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1943 | 5 | 25 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1943 | 5 | 26 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1943 | 5 | 27 | 1097.1429 | 25 | 1072.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
1943 | 5 | 28 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1943 | 5 | 29 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1943 | 5 | 30 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1943 | 5 | 31 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1943 | 6 | 1 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1943 | 6 | 2 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1943 | 6 | 3 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1943 | 6 | 4 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1943 | 6 | 5 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1943 | 6 | 6 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1943 | 6 | 7 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1943 | 6 | 8 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1943 | 6 | 9 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1943 | 6 | 10 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1943 | 6 | 11 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1943 | 6 | 12 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1943 | 6 | 13 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1943 | 6 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1943 | 6 | 15 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1943 | 6 | 16 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1943 | 6 | 17 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1943 | 6 | 18 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1943 | 6 | 19 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1943 | 6 | 20 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1943 | 6 | 21 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1943 | 6 | 22 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1943 | 6 | 23 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1943 | 6 | 24 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1943 | 6 | 25 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1943 | 6 | 26 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1943 | 6 | 27 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1943 | 6 | 28 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1943 | 6 | 29 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1943 | 6 | 30 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1943 | 7 | 1 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1943 | 7 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1943 | 7 | 3 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1943 | 7 | 4 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 7 | 5 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1943 | 7 | 6 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1943 | 7 | 7 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1943 | 7 | 8 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1943 | 7 | 9 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1943 | 7 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 7 | 11 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 7 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1943 | 7 | 13 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1943 | 7 | 14 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1943 | 7 | 15 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 7 | 16 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 7 | 17 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1943 | 7 | 18 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1943 | 7 | 19 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1943 | 7 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1943 | 7 | 21 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1943 | 7 | 22 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 7 | 23 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1943 | 7 | 24 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1943 | 7 | 25 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1943 | 7 | 26 | 280.8163 | 5 | 275.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1943 | 7 | 27 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1943 | 7 | 28 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1943 | 7 | 29 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1943 | 7 | 30 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1943 | 7 | 31 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1943 | 8 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1943 | 8 | 2 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1943 | 8 | 3 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1943 | 8 | 4 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1943 | 8 | 5 | 372.2449 | 5 | 367.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1943 | 8 | 6 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1943 | 8 | 7 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1943 | 8 | 8 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1943 | 8 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1943 | 8 | 10 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1943 | 8 | 11 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1943 | 8 | 12 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1943 | 8 | 13 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1943 | 8 | 14 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1943 | 8 | 15 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1943 | 8 | 16 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1943 | 8 | 17 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1943 | 8 | 18 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1943 | 8 | 19 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1943 | 8 | 20 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1943 | 8 | 21 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1943 | 8 | 22 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1943 | 8 | 23 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1943 | 8 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1943 | 8 | 25 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1943 | 8 | 26 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1943 | 8 | 27 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1943 | 8 | 28 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1943 | 8 | 29 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 8 | 30 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 8 | 31 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1943 | 9 | 1 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1943 | 9 | 2 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1943 | 9 | 3 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1943 | 9 | 4 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1943 | 9 | 5 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1943 | 9 | 6 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1943 | 9 | 7 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1943 | 9 | 8 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1943 | 9 | 9 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1943 | 9 | 10 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1943 | 9 | 11 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1943 | 9 | 12 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1943 | 9 | 13 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1943 | 9 | 14 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1943 | 9 | 15 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1943 | 9 | 16 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1943 | 9 | 17 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1943 | 9 | 18 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1943 | 9 | 19 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1943 | 9 | 20 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1943 | 9 | 21 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1943 | 9 | 22 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1943 | 9 | 23 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1943 | 9 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1943 | 9 | 25 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1943 | 9 | 26 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 9 | 27 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 9 | 28 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 9 | 29 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1943 | 9 | 30 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1943 | 10 | 1 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1943 | 10 | 2 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1943 | 10 | 3 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1943 | 10 | 4 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1943 | 10 | 5 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1943 | 10 | 6 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1943 | 10 | 7 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1943 | 10 | 8 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1943 | 10 | 9 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1943 | 10 | 10 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1943 | 10 | 11 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 10 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1943 | 10 | 13 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 10 | 14 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 10 | 15 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1943 | 10 | 16 | 385.3061 | 15 | 370.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1943 | 10 | 17 | 1234.2857 | 15 | 1219.2857 | 27.5314 | 139.3858 | 0.77441 | 26.757 | 89.27% | 281.9587 | 265.0412 | 6360.9887
1943 | 10 | 18 | 1097.1429 | 15 | 1082.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
1943 | 10 | 19 | 677.8776 | 15 | 662.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1943 | 10 | 20 | 579.9184 | 15 | 564.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1943 | 10 | 21 | 444.0816 | 15 | 429.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1943 | 10 | 22 | 334.3673 | 15 | 319.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1943 | 10 | 23 | 252.0816 | 15 | 237.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1943 | 10 | 24 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1943 | 10 | 25 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1943 | 10 | 26 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1943 | 10 | 27 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1943 | 10 | 28 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1943 | 10 | 29 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1943 | 10 | 30 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1943 | 10 | 31 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1943 | 11 | 1 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1943 | 11 | 2 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1943 | 11 | 3 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1943 | 11 | 4 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1943 | 11 | 5 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1943 | 11 | 6 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1943 | 11 | 7 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1943 | 11 | 8 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1943 | 11 | 9 | 1789.3878 | 15 | 1774.3878 | 26.4212 | 139.3858 | 0.77441 | 25.6468 | 89.27% | 270.2597 | 254.0441 | 6097.0581
1943 | 11 | 10 | 1985.3061 | 15 | 1970.3061 | 26.0294 | 139.3858 | 0.77441 | 25.255 | 89.27% | 266.1306 | 250.1628 | 6003.9061
1943 | 11 | 11 | 868.5714 | 15 | 853.5714 | 28.2629 | 139.3858 | 0.77441 | 27.4884 | 89.27% | 289.6663 | 272.2863 | 6534.8724
1943 | 11 | 12 | 561.6327 | 15 | 546.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1943 | 11 | 13 | 429.7143 | 15 | 414.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1943 | 11 | 14 | 347.4286 | 15 | 332.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1943 | 11 | 15 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1943 | 11 | 16 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1943 | 11 | 17 | 239.0204 | 15 | 224.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1943 | 11 | 18 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1943 | 11 | 19 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1943 | 11 | 20 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1943 | 11 | 21 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1943 | 11 | 22 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1943 | 11 | 23 | 249.4694 | 15 | 234.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1943 | 11 | 24 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1943 | 11 | 25 | 252.0816 | 15 | 237.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1943 | 11 | 26 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1943 | 11 | 27 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1943 | 11 | 28 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1943 | 11 | 29 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1943 | 11 | 30 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1943 | 12 | 1 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1943 | 12 | 2 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1943 | 12 | 3 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1943 | 12 | 4 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1943 | 12 | 5 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1943 | 12 | 6 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1943 | 12 | 7 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1943 | 12 | 8 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1943 | 12 | 9 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1943 | 12 | 10 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1943 | 12 | 11 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1943 | 12 | 12 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1943 | 12 | 13 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1943 | 12 | 14 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1943 | 12 | 15 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1943 | 12 | 16 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1943 | 12 | 17 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1943 | 12 | 18 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1943 | 12 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1943 | 12 | 20 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1943 | 12 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1943 | 12 | 22 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1943 | 12 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1943 | 12 | 24 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1943 | 12 | 25 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1943 | 12 | 26 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1943 | 12 | 27 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1943 | 12 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1943 | 12 | 29 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1943 | 12 | 30 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1943 | 12 | 31 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 1 | 1 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 1 | 2 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 4 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1944 | 1 | 5 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1944 | 1 | 6 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1944 | 1 | 7 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 1 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1944 | 1 | 9 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1944 | 1 | 10 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1944 | 1 | 11 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1944 | 1 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 1 | 13 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1944 | 1 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1944 | 1 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 1 | 16 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1944 | 1 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1944 | 1 | 18 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 19 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1944 | 1 | 20 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1944 | 1 | 21 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1944 | 1 | 22 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 24 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 25 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 26 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 1 | 27 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1944 | 1 | 28 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1944 | 1 | 29 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1944 | 1 | 30 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1944 | 1 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1944 | 2 | 1 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1944 | 2 | 2 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 2 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 2 | 4 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1944 | 2 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1944 | 2 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1944 | 2 | 7 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1944 | 2 | 8 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1944 | 2 | 9 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1944 | 2 | 10 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1944 | 2 | 11 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1944 | 2 | 12 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1944 | 2 | 13 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1944 | 2 | 14 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1944 | 2 | 15 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1944 | 2 | 16 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1944 | 2 | 17 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1944 | 2 | 18 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1944 | 2 | 19 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1944 | 2 | 20 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1944 | 2 | 21 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1944 | 2 | 22 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1944 | 2 | 23 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1944 | 2 | 24 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1944 | 2 | 25 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1944 | 2 | 26 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 2 | 27 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 2 | 28 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 2 | 29 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1944 | 3 | 1 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1944 | 3 | 2 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1944 | 3 | 3 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1944 | 3 | 4 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1944 | 3 | 5 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1944 | 3 | 6 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1944 | 3 | 7 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1944 | 3 | 8 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1944 | 3 | 9 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1944 | 3 | 10 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1944 | 3 | 11 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1944 | 3 | 12 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1944 | 3 | 13 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1944 | 3 | 14 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1944 | 3 | 15 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1944 | 3 | 16 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1944 | 3 | 17 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1944 | 3 | 18 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1944 | 3 | 19 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1944 | 3 | 20 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1944 | 3 | 21 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1944 | 3 | 22 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1944 | 3 | 23 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1944 | 3 | 24 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1944 | 3 | 25 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1944 | 3 | 26 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1944 | 3 | 27 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1944 | 3 | 28 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1944 | 3 | 29 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1944 | 3 | 30 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1944 | 3 | 31 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1944 | 4 | 1 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1944 | 4 | 2 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1944 | 4 | 3 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1944 | 4 | 4 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1944 | 4 | 5 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1944 | 4 | 6 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1944 | 4 | 7 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1944 | 4 | 8 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1944 | 4 | 9 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1944 | 4 | 10 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1944 | 4 | 11 | 1097.1429 | 25 | 1072.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
1944 | 4 | 12 | 969.1429 | 25 | 944.1429 | 28.0617 | 139.3858 | 0.77441 | 27.2873 | 89.27% | 287.5467 | 270.2939 | 6487.0544
1944 | 4 | 13 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1944 | 4 | 14 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1944 | 4 | 15 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1944 | 4 | 16 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1944 | 4 | 17 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1944 | 4 | 18 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1944 | 4 | 19 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1944 | 4 | 20 | 1044.898 | 25 | 1019.898 | 27.9102 | 139.3858 | 0.77441 | 27.1358 | 89.27% | 285.9502 | 268.7932 | 6451.0356
1944 | 4 | 21 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1944 | 4 | 22 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1944 | 4 | 23 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1944 | 4 | 24 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1944 | 4 | 25 | 1018.7755 | 25 | 993.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
1944 | 4 | 26 | 944.3265 | 25 | 919.3265 | 28.1113 | 139.3858 | 0.77441 | 27.3369 | 89.27% | 288.0698 | 270.7856 | 6498.8536
1944 | 4 | 27 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1944 | 4 | 28 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1944 | 4 | 29 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1944 | 4 | 30 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1944 | 5 | 1 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1944 | 5 | 2 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1944 | 5 | 3 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1944 | 5 | 4 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1944 | 5 | 5 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1944 | 5 | 6 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1944 | 5 | 7 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1944 | 5 | 8 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1944 | 5 | 9 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1944 | 5 | 10 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1944 | 5 | 11 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1944 | 5 | 12 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1944 | 5 | 13 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1944 | 5 | 14 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1944 | 5 | 15 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1944 | 5 | 16 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1944 | 5 | 17 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1944 | 5 | 18 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1944 | 5 | 19 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1944 | 5 | 20 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1944 | 5 | 21 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1944 | 5 | 22 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1944 | 5 | 23 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1944 | 5 | 24 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1944 | 5 | 25 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1944 | 5 | 26 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1944 | 5 | 27 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1944 | 5 | 28 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1944 | 5 | 29 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1944 | 5 | 30 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1944 | 5 | 31 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1944 | 6 | 1 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1944 | 6 | 2 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1944 | 6 | 3 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1944 | 6 | 4 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1944 | 6 | 5 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1944 | 6 | 6 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1944 | 6 | 7 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1944 | 6 | 8 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1944 | 6 | 9 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1944 | 6 | 10 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1944 | 6 | 11 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1944 | 6 | 12 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1944 | 6 | 13 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1944 | 6 | 14 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1944 | 6 | 15 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1944 | 6 | 16 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1944 | 6 | 17 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1944 | 6 | 18 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1944 | 6 | 19 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1944 | 6 | 20 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1944 | 6 | 21 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1944 | 6 | 22 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1944 | 6 | 23 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1944 | 6 | 24 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1944 | 6 | 25 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1944 | 6 | 26 | 679.1837 | 25 | 654.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
1944 | 6 | 27 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1944 | 6 | 28 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1944 | 6 | 29 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1944 | 6 | 30 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1944 | 7 | 1 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1944 | 7 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1944 | 7 | 3 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1944 | 7 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1944 | 7 | 5 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1944 | 7 | 6 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1944 | 7 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1944 | 7 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1944 | 7 | 9 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1944 | 7 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1944 | 7 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1944 | 7 | 12 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1944 | 7 | 13 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1944 | 7 | 14 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1944 | 7 | 15 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1944 | 7 | 16 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1944 | 7 | 17 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1944 | 7 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1944 | 7 | 19 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1944 | 7 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1944 | 7 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1944 | 7 | 22 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1944 | 7 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1944 | 7 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1944 | 7 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1944 | 7 | 26 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1944 | 7 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1944 | 7 | 28 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1944 | 7 | 29 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1944 | 7 | 30 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1944 | 7 | 31 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1944 | 8 | 1 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1944 | 8 | 2 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1944 | 8 | 3 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1944 | 8 | 4 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1944 | 8 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1944 | 8 | 6 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1944 | 8 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1944 | 8 | 8 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1944 | 8 | 9 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1944 | 8 | 10 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1944 | 8 | 11 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1944 | 8 | 12 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1944 | 8 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1944 | 8 | 14 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1944 | 8 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1944 | 8 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 17 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 18 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 19 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 21 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1944 | 8 | 22 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1944 | 8 | 23 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1944 | 8 | 24 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1944 | 8 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1944 | 8 | 27 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1944 | 8 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1944 | 8 | 29 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1944 | 8 | 30 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1944 | 8 | 31 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1944 | 9 | 1 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1944 | 9 | 2 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1944 | 9 | 3 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1944 | 9 | 4 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1944 | 9 | 5 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1944 | 9 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1944 | 9 | 7 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1944 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1944 | 9 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1944 | 9 | 10 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1944 | 9 | 11 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1944 | 9 | 12 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1944 | 9 | 13 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1944 | 9 | 14 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1944 | 9 | 15 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1944 | 9 | 16 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1944 | 9 | 17 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1944 | 9 | 18 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1944 | 9 | 19 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1944 | 9 | 20 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1944 | 9 | 21 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1944 | 9 | 22 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1944 | 9 | 23 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1944 | 9 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1944 | 9 | 25 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1944 | 9 | 26 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1944 | 9 | 27 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1944 | 9 | 28 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1944 | 9 | 29 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1944 | 9 | 30 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1944 | 10 | 1 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1944 | 10 | 2 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1944 | 10 | 3 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1944 | 10 | 4 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1944 | 10 | 5 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1944 | 10 | 6 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1944 | 10 | 7 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1944 | 10 | 8 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1944 | 10 | 9 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1944 | 10 | 10 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1944 | 10 | 11 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1944 | 10 | 12 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1944 | 10 | 13 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1944 | 10 | 14 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1944 | 10 | 15 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1944 | 10 | 16 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1944 | 10 | 17 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1944 | 10 | 18 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1944 | 10 | 19 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1944 | 10 | 20 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1944 | 10 | 21 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1944 | 10 | 22 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1944 | 10 | 23 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1944 | 10 | 24 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1944 | 10 | 25 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1944 | 10 | 26 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1944 | 10 | 27 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1944 | 10 | 28 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1944 | 10 | 29 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1944 | 10 | 30 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1944 | 10 | 31 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1944 | 11 | 1 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1944 | 11 | 2 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1944 | 11 | 3 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1944 | 11 | 4 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1944 | 11 | 5 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1944 | 11 | 6 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1944 | 11 | 7 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1944 | 11 | 8 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1944 | 11 | 9 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1944 | 11 | 10 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1944 | 11 | 11 | 457.1429 | 15 | 442.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1944 | 11 | 12 | 360.4898 | 15 | 345.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1944 | 11 | 13 | 219.4286 | 15 | 204.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1944 | 11 | 14 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1944 | 11 | 15 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1944 | 11 | 16 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1944 | 11 | 17 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1944 | 11 | 18 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1944 | 11 | 19 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1944 | 11 | 20 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1944 | 11 | 21 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1944 | 11 | 22 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1944 | 11 | 23 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1944 | 11 | 24 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1944 | 11 | 25 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1944 | 11 | 26 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1944 | 11 | 27 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1944 | 11 | 28 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1944 | 11 | 29 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1944 | 11 | 30 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1944 | 12 | 1 | 781.0612 | 5 | 776.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1944 | 12 | 2 | 459.7551 | 5 | 454.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1944 | 12 | 3 | 297.7959 | 5 | 292.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1944 | 12 | 4 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1944 | 12 | 5 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1944 | 12 | 6 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1944 | 12 | 7 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1944 | 12 | 8 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1944 | 12 | 9 | 320 | 5 | 315 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1944 | 12 | 10 | 459.7551 | 5 | 454.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1944 | 12 | 11 | 312.1633 | 5 | 307.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1944 | 12 | 12 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1944 | 12 | 13 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1944 | 12 | 14 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1944 | 12 | 15 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1944 | 12 | 16 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1944 | 12 | 17 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1944 | 12 | 18 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1944 | 12 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1944 | 12 | 20 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1944 | 12 | 21 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1944 | 12 | 22 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1944 | 12 | 23 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1944 | 12 | 24 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1944 | 12 | 25 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1944 | 12 | 26 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1944 | 12 | 27 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1944 | 12 | 28 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1944 | 12 | 29 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1944 | 12 | 30 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1944 | 12 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 1 | 1 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1945 | 1 | 2 | 848.9796 | 5 | 843.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1945 | 1 | 3 | 579.9184 | 5 | 574.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1945 | 1 | 4 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1945 | 1 | 5 | 279.5102 | 5 | 274.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1945 | 1 | 6 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1945 | 1 | 7 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1945 | 1 | 8 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1945 | 1 | 9 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1945 | 1 | 10 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1945 | 1 | 11 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1945 | 1 | 12 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1945 | 1 | 13 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1945 | 1 | 14 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1945 | 1 | 15 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1945 | 1 | 16 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1945 | 1 | 17 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1945 | 1 | 18 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1945 | 1 | 19 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1945 | 1 | 20 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1945 | 1 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1945 | 1 | 22 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1945 | 1 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1945 | 1 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1945 | 1 | 25 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1945 | 1 | 26 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1945 | 1 | 27 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1945 | 1 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1945 | 1 | 29 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 1 | 30 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1945 | 1 | 31 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 1 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1945 | 2 | 2 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1945 | 2 | 3 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 4 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 5 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 6 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1945 | 2 | 7 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 8 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1945 | 2 | 9 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 10 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1945 | 2 | 11 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 2 | 12 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 2 | 13 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1945 | 2 | 14 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1945 | 2 | 16 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1945 | 2 | 17 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 2 | 18 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1945 | 2 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1945 | 2 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1945 | 2 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1945 | 2 | 22 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 2 | 23 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1945 | 2 | 24 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1945 | 2 | 25 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1945 | 2 | 26 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1945 | 2 | 27 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1945 | 2 | 28 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1945 | 3 | 1 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1945 | 3 | 2 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1945 | 3 | 3 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1945 | 3 | 4 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1945 | 3 | 5 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1945 | 3 | 6 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1945 | 3 | 7 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1945 | 3 | 8 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1945 | 3 | 9 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1945 | 3 | 10 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1945 | 3 | 11 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1945 | 3 | 12 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1945 | 3 | 13 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1945 | 3 | 14 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1945 | 3 | 15 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1945 | 3 | 16 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1945 | 3 | 17 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1945 | 3 | 18 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1945 | 3 | 19 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1945 | 3 | 20 | 739.2653 | 25 | 714.2653 | 28.5215 | 139.3858 | 0.77441 | 27.7471 | 89.27% | 292.3915 | 274.848 | 6596.3527
1945 | 3 | 21 | 718.3673 | 25 | 693.3673 | 28.5633 | 139.3858 | 0.77441 | 27.7889 | 89.27% | 292.832 | 275.262 | 6606.2889
1945 | 3 | 22 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1945 | 3 | 23 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1945 | 3 | 24 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1945 | 3 | 25 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1945 | 3 | 26 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1945 | 3 | 27 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1945 | 3 | 28 | 1204.2449 | 25 | 1179.2449 | 27.5915 | 139.3858 | 0.77441 | 26.8171 | 89.27% | 282.5918 | 265.6363 | 6375.272
1945 | 3 | 29 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1945 | 3 | 30 | 1841.6327 | 25 | 1816.6327 | 26.3167 | 139.3858 | 0.77441 | 25.5423 | 89.27% | 269.1586 | 253.0091 | 6072.2176
1945 | 3 | 31 | 1502.0408 | 25 | 1477.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1945 | 4 | 1 | 1260.4082 | 25 | 1235.4082 | 27.4792 | 139.3858 | 0.77441 | 26.7048 | 89.27% | 281.4082 | 264.5237 | 6348.5684
1945 | 4 | 2 | 1071.0204 | 25 | 1046.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
1945 | 4 | 3 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1945 | 4 | 4 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1945 | 4 | 5 | 1071.0204 | 25 | 1046.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
1945 | 4 | 6 | 1123.2653 | 25 | 1098.2653 | 27.7535 | 139.3858 | 0.77441 | 26.9791 | 89.27% | 284.2985 | 267.2406 | 6413.7748
1945 | 4 | 7 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1945 | 4 | 8 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1945 | 4 | 9 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1945 | 4 | 10 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1945 | 4 | 11 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1945 | 4 | 12 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1945 | 4 | 13 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1945 | 4 | 14 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1945 | 4 | 15 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1945 | 4 | 16 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1945 | 4 | 17 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1945 | 4 | 18 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1945 | 4 | 19 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1945 | 4 | 20 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1945 | 4 | 21 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1945 | 4 | 22 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1945 | 4 | 23 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1945 | 4 | 24 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1945 | 4 | 25 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1945 | 4 | 26 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1945 | 4 | 27 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1945 | 4 | 28 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1945 | 4 | 29 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1945 | 4 | 30 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1945 | 5 | 1 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1945 | 5 | 2 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1945 | 5 | 3 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1945 | 5 | 4 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1945 | 5 | 5 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1945 | 5 | 6 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1945 | 5 | 7 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1945 | 5 | 8 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1945 | 5 | 9 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1945 | 5 | 10 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1945 | 5 | 11 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1945 | 5 | 12 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1945 | 5 | 13 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1945 | 5 | 14 | 1671.8367 | 25 | 1646.8367 | 26.6563 | 139.3858 | 0.77441 | 25.8819 | 89.27% | 272.7371 | 256.3729 | 6152.9493
1945 | 5 | 15 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1945 | 5 | 16 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1945 | 5 | 17 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1945 | 5 | 18 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1945 | 5 | 19 | 1204.2449 | 25 | 1179.2449 | 27.5915 | 139.3858 | 0.77441 | 26.8171 | 89.27% | 282.5918 | 265.6363 | 6375.272
1945 | 5 | 20 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1945 | 5 | 21 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1945 | 5 | 22 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1945 | 5 | 23 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1945 | 5 | 24 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1945 | 5 | 25 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1945 | 5 | 26 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1945 | 5 | 27 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1945 | 5 | 28 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1945 | 5 | 29 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1945 | 5 | 30 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1945 | 5 | 31 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1945 | 6 | 1 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1945 | 6 | 2 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1945 | 6 | 3 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1945 | 6 | 4 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1945 | 6 | 5 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1945 | 6 | 6 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1945 | 6 | 7 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1945 | 6 | 8 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1945 | 6 | 9 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1945 | 6 | 10 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1945 | 6 | 11 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1945 | 6 | 12 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1945 | 6 | 13 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1945 | 6 | 14 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1945 | 6 | 15 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1945 | 6 | 16 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1945 | 6 | 17 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1945 | 6 | 18 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1945 | 6 | 19 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1945 | 6 | 20 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1945 | 6 | 21 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1945 | 6 | 22 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1945 | 6 | 23 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1945 | 6 | 24 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1945 | 6 | 25 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1945 | 6 | 26 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1945 | 6 | 27 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1945 | 6 | 28 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1945 | 6 | 29 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1945 | 6 | 30 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1945 | 7 | 1 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1945 | 7 | 2 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1945 | 7 | 3 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1945 | 7 | 4 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1945 | 7 | 5 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1945 | 7 | 6 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1945 | 7 | 7 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1945 | 7 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1945 | 7 | 9 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1945 | 7 | 10 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1945 | 7 | 11 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1945 | 7 | 12 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1945 | 7 | 13 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1945 | 7 | 14 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1945 | 7 | 15 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1945 | 7 | 16 | 417.9592 | 5 | 412.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1945 | 7 | 17 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1945 | 7 | 18 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1945 | 7 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1945 | 7 | 20 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1945 | 7 | 21 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1945 | 7 | 22 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1945 | 7 | 23 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1945 | 7 | 24 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1945 | 7 | 25 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1945 | 7 | 26 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1945 | 7 | 27 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1945 | 7 | 28 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1945 | 7 | 29 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1945 | 7 | 30 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1945 | 7 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1945 | 8 | 1 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1945 | 8 | 2 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1945 | 8 | 3 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1945 | 8 | 4 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1945 | 8 | 5 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1945 | 8 | 6 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1945 | 8 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1945 | 8 | 8 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1945 | 8 | 9 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1945 | 8 | 10 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1945 | 8 | 11 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1945 | 8 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1945 | 8 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1945 | 8 | 14 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1945 | 8 | 15 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1945 | 8 | 16 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1945 | 8 | 17 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1945 | 8 | 18 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1945 | 8 | 19 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1945 | 8 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1945 | 8 | 21 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1945 | 8 | 22 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1945 | 8 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1945 | 8 | 24 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1945 | 8 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1945 | 8 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1945 | 8 | 27 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1945 | 8 | 28 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1945 | 8 | 29 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1945 | 8 | 30 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1945 | 8 | 31 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1945 | 9 | 1 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1945 | 9 | 2 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1945 | 9 | 3 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1945 | 9 | 4 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1945 | 9 | 5 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1945 | 9 | 6 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1945 | 9 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1945 | 9 | 8 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1945 | 9 | 9 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1945 | 9 | 10 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1945 | 9 | 11 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1945 | 9 | 12 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1945 | 9 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1945 | 9 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1945 | 9 | 15 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1945 | 9 | 16 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1945 | 9 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1945 | 9 | 18 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1945 | 9 | 19 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1945 | 9 | 20 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1945 | 9 | 21 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1945 | 9 | 22 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1945 | 9 | 23 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1945 | 9 | 24 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1945 | 9 | 25 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1945 | 9 | 26 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1945 | 9 | 27 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1945 | 9 | 28 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1945 | 9 | 29 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1945 | 9 | 30 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1945 | 10 | 1 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1945 | 10 | 2 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1945 | 10 | 3 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1945 | 10 | 4 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1945 | 10 | 5 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1945 | 10 | 6 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1945 | 10 | 7 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1945 | 10 | 8 | 1358.3673 | 15 | 1343.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1945 | 10 | 9 | 638.6939 | 15 | 623.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1945 | 10 | 10 | 429.7143 | 15 | 414.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1945 | 10 | 11 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1945 | 10 | 12 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1945 | 10 | 13 | 252.0816 | 15 | 237.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1945 | 10 | 14 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1945 | 10 | 15 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1945 | 10 | 16 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1945 | 10 | 17 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1945 | 10 | 18 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1945 | 10 | 19 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1945 | 10 | 20 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1945 | 10 | 21 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1945 | 10 | 22 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1945 | 10 | 23 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1945 | 10 | 24 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1945 | 10 | 25 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1945 | 10 | 26 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1945 | 10 | 27 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1945 | 10 | 28 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1945 | 10 | 29 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1945 | 10 | 30 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1945 | 10 | 31 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1945 | 11 | 1 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1945 | 11 | 2 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1945 | 11 | 3 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1945 | 11 | 4 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1945 | 11 | 5 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1945 | 11 | 6 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1945 | 11 | 7 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1945 | 11 | 8 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1945 | 11 | 9 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1945 | 11 | 10 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1945 | 11 | 11 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1945 | 11 | 12 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1945 | 11 | 13 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1945 | 11 | 14 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1945 | 11 | 15 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1945 | 11 | 16 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1945 | 11 | 17 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1945 | 11 | 18 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1945 | 11 | 19 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1945 | 11 | 20 | 457.1429 | 15 | 442.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1945 | 11 | 21 | 509.3878 | 15 | 494.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1945 | 11 | 22 | 398.3673 | 15 | 383.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1945 | 11 | 23 | 718.3673 | 15 | 703.3673 | 28.5633 | 139.3858 | 0.77441 | 27.7889 | 89.27% | 292.832 | 275.262 | 6606.2889
1945 | 11 | 24 | 459.7551 | 15 | 444.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1945 | 11 | 25 | 322.6122 | 15 | 307.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1945 | 11 | 26 | 252.0816 | 15 | 237.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1945 | 11 | 27 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1945 | 11 | 28 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1945 | 11 | 29 | 160.6531 | 15 | 145.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1945 | 11 | 30 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1945 | 12 | 1 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1945 | 12 | 2 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1945 | 12 | 3 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1945 | 12 | 4 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1945 | 12 | 5 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1945 | 12 | 6 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1945 | 12 | 7 | 391.8367 | 5 | 386.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1945 | 12 | 8 | 1168.9796 | 5 | 1163.9796 | 27.662 | 139.3858 | 0.77441 | 26.8876 | 89.27% | 283.3351 | 266.335 | 6392.0394
1945 | 12 | 9 | 760.1633 | 5 | 755.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1945 | 12 | 10 | 459.7551 | 5 | 454.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1945 | 12 | 11 | 322.6122 | 5 | 317.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1945 | 12 | 12 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1945 | 12 | 13 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1945 | 12 | 14 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1945 | 12 | 15 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1945 | 12 | 16 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1945 | 12 | 17 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1945 | 12 | 18 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1945 | 12 | 19 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1945 | 12 | 20 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1945 | 12 | 21 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1945 | 12 | 22 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1945 | 12 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1945 | 12 | 24 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1945 | 12 | 25 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1945 | 12 | 26 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1945 | 12 | 27 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1945 | 12 | 28 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1945 | 12 | 29 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1945 | 12 | 30 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1945 | 12 | 31 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1946 | 1 | 1 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1946 | 1 | 2 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1946 | 1 | 3 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1946 | 1 | 4 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1946 | 1 | 5 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1946 | 1 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1946 | 1 | 7 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1946 | 1 | 8 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1946 | 1 | 9 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1946 | 1 | 10 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1946 | 1 | 11 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1946 | 1 | 12 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1946 | 1 | 13 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1946 | 1 | 14 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1946 | 1 | 15 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1946 | 1 | 16 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1946 | 1 | 17 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1946 | 1 | 18 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1946 | 1 | 19 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1946 | 1 | 20 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1946 | 1 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1946 | 1 | 22 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1946 | 1 | 23 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1946 | 1 | 24 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1946 | 1 | 25 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1946 | 1 | 26 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1946 | 1 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1946 | 1 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1946 | 1 | 29 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1946 | 1 | 30 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1946 | 1 | 31 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1946 | 2 | 1 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1946 | 2 | 2 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1946 | 2 | 3 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1946 | 2 | 4 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1946 | 2 | 5 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1946 | 2 | 6 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1946 | 2 | 7 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1946 | 2 | 8 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1946 | 2 | 9 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1946 | 2 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1946 | 2 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1946 | 2 | 12 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1946 | 2 | 13 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1946 | 2 | 14 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1946 | 2 | 15 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1946 | 2 | 16 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1946 | 2 | 17 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1946 | 2 | 18 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1946 | 2 | 19 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1946 | 2 | 20 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1946 | 2 | 21 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1946 | 2 | 22 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1946 | 2 | 23 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1946 | 2 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1946 | 2 | 25 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1946 | 2 | 26 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1946 | 2 | 27 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1946 | 2 | 28 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1946 | 3 | 1 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1946 | 3 | 2 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1946 | 3 | 3 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1946 | 3 | 4 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1946 | 3 | 5 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1946 | 3 | 6 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1946 | 3 | 7 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1946 | 3 | 8 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1946 | 3 | 9 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1946 | 3 | 10 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1946 | 3 | 11 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1946 | 3 | 12 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1946 | 3 | 13 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1946 | 3 | 14 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1946 | 3 | 15 | 969.1429 | 25 | 944.1429 | 28.0617 | 139.3858 | 0.77441 | 27.2873 | 89.27% | 287.5467 | 270.2939 | 6487.0544
1946 | 3 | 16 | 1123.2653 | 25 | 1098.2653 | 27.7535 | 139.3858 | 0.77441 | 26.9791 | 89.27% | 284.2985 | 267.2406 | 6413.7748
1946 | 3 | 17 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1946 | 3 | 18 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1946 | 3 | 19 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1946 | 3 | 20 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1946 | 3 | 21 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1946 | 3 | 22 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1946 | 3 | 23 | 944.3265 | 25 | 919.3265 | 28.1113 | 139.3858 | 0.77441 | 27.3369 | 89.27% | 288.0698 | 270.7856 | 6498.8536
1946 | 3 | 24 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1946 | 3 | 25 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1946 | 3 | 26 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1946 | 3 | 27 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1946 | 3 | 28 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1946 | 3 | 29 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1946 | 3 | 30 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1946 | 3 | 31 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1946 | 4 | 1 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1946 | 4 | 2 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1946 | 4 | 3 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1946 | 4 | 4 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1946 | 4 | 5 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1946 | 4 | 6 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1946 | 4 | 7 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1946 | 4 | 8 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1946 | 4 | 9 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1946 | 4 | 10 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1946 | 4 | 11 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1946 | 4 | 12 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1946 | 4 | 13 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1946 | 4 | 14 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1946 | 4 | 15 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1946 | 4 | 16 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1946 | 4 | 17 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1946 | 4 | 18 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1946 | 4 | 19 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1946 | 4 | 20 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1946 | 4 | 21 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1946 | 4 | 22 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1946 | 4 | 23 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1946 | 4 | 24 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1946 | 4 | 25 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1946 | 4 | 26 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1946 | 4 | 27 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1946 | 4 | 28 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1946 | 4 | 29 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1946 | 4 | 30 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1946 | 5 | 1 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1946 | 5 | 2 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1946 | 5 | 3 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1946 | 5 | 4 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1946 | 5 | 5 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1946 | 5 | 6 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1946 | 5 | 7 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1946 | 5 | 8 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1946 | 5 | 9 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1946 | 5 | 10 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1946 | 5 | 11 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1946 | 5 | 12 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1946 | 5 | 13 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1946 | 5 | 14 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1946 | 5 | 15 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1946 | 5 | 16 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1946 | 5 | 17 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1946 | 5 | 18 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1946 | 5 | 19 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1946 | 5 | 20 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1946 | 5 | 21 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1946 | 5 | 22 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1946 | 5 | 23 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1946 | 5 | 24 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1946 | 5 | 25 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1946 | 5 | 26 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1946 | 5 | 27 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1946 | 5 | 28 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1946 | 5 | 29 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1946 | 5 | 30 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1946 | 5 | 31 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1946 | 6 | 1 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1946 | 6 | 2 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1946 | 6 | 3 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1946 | 6 | 4 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1946 | 6 | 5 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1946 | 6 | 6 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1946 | 6 | 7 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1946 | 6 | 8 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1946 | 6 | 9 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1946 | 6 | 10 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1946 | 6 | 11 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1946 | 6 | 12 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1946 | 6 | 13 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1946 | 6 | 14 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1946 | 6 | 15 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1946 | 6 | 16 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1946 | 6 | 17 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1946 | 6 | 18 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1946 | 6 | 19 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1946 | 6 | 20 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1946 | 6 | 21 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1946 | 6 | 22 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1946 | 6 | 23 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1946 | 6 | 24 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1946 | 6 | 25 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1946 | 6 | 26 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1946 | 6 | 27 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1946 | 6 | 28 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1946 | 6 | 29 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1946 | 6 | 30 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1946 | 7 | 1 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1946 | 7 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1946 | 7 | 3 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1946 | 7 | 4 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1946 | 7 | 5 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1946 | 7 | 6 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1946 | 7 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1946 | 7 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1946 | 7 | 9 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1946 | 7 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1946 | 7 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1946 | 7 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1946 | 7 | 13 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1946 | 7 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1946 | 7 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1946 | 7 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1946 | 7 | 17 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1946 | 7 | 18 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1946 | 7 | 19 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1946 | 7 | 20 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1946 | 7 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1946 | 7 | 22 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1946 | 7 | 23 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1946 | 7 | 24 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1946 | 7 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1946 | 7 | 26 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1946 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1946 | 7 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1946 | 7 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1946 | 7 | 30 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1946 | 7 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1946 | 8 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1946 | 8 | 2 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1946 | 8 | 3 | 346.1224 | 5 | 341.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1946 | 8 | 4 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1946 | 8 | 5 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1946 | 8 | 6 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1946 | 8 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1946 | 8 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1946 | 8 | 9 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1946 | 8 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1946 | 8 | 11 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1946 | 8 | 12 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1946 | 8 | 13 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1946 | 8 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1946 | 8 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1946 | 8 | 16 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1946 | 8 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1946 | 8 | 18 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1946 | 8 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1946 | 8 | 20 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1946 | 8 | 21 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1946 | 8 | 22 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1946 | 8 | 23 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1946 | 8 | 24 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1946 | 8 | 25 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1946 | 8 | 26 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1946 | 8 | 27 | 1155.9184 | 5 | 1150.9184 | 27.6882 | 139.3858 | 0.77441 | 26.9138 | 89.27% | 283.6104 | 266.5937 | 6398.2495
1946 | 8 | 28 | 770.6122 | 5 | 765.6122 | 28.4588 | 139.3858 | 0.77441 | 27.6844 | 89.27% | 291.7309 | 274.227 | 6581.4484
1946 | 8 | 29 | 347.4286 | 5 | 342.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1946 | 8 | 30 | 225.9592 | 5 | 220.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1946 | 8 | 31 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1946 | 9 | 1 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1946 | 9 | 2 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1946 | 9 | 3 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1946 | 9 | 4 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1946 | 9 | 5 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1946 | 9 | 6 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1946 | 9 | 7 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1946 | 9 | 8 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1946 | 9 | 9 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1946 | 9 | 10 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1946 | 9 | 11 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1946 | 9 | 12 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1946 | 9 | 13 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1946 | 9 | 14 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1946 | 9 | 15 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1946 | 9 | 16 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1946 | 9 | 17 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1946 | 9 | 18 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1946 | 9 | 19 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1946 | 9 | 20 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1946 | 9 | 21 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1946 | 9 | 22 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1946 | 9 | 23 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1946 | 9 | 24 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1946 | 9 | 25 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1946 | 9 | 26 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1946 | 9 | 27 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1946 | 9 | 28 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1946 | 9 | 29 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1946 | 9 | 30 | 672.6531 | 15 | 657.6531 | 28.6547 | 139.3858 | 0.77441 | 27.8803 | 89.27% | 293.7954 | 276.1677 | 6628.0244
1946 | 10 | 1 | 2155.102 | 15 | 2140.102 | 25.6898 | 139.3858 | 0.77441 | 24.9154 | 89.27% | 262.5521 | 246.7989 | 5923.1744
1946 | 10 | 2 | 872.4898 | 15 | 857.4898 | 28.255 | 139.3858 | 0.77441 | 27.4806 | 89.27% | 289.5837 | 272.2087 | 6533.0094
1946 | 10 | 3 | 475.4286 | 15 | 460.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1946 | 10 | 4 | 320 | 15 | 305 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1946 | 10 | 5 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1946 | 10 | 6 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1946 | 10 | 7 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1946 | 10 | 8 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1946 | 10 | 9 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1946 | 10 | 10 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1946 | 10 | 11 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1946 | 10 | 12 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1946 | 10 | 13 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1946 | 10 | 14 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1946 | 10 | 15 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1946 | 10 | 16 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1946 | 10 | 17 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1946 | 10 | 18 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1946 | 10 | 19 | 429.7143 | 15 | 414.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1946 | 10 | 20 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1946 | 10 | 21 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1946 | 10 | 22 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1946 | 10 | 23 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1946 | 10 | 24 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1946 | 10 | 25 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1946 | 10 | 26 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1946 | 10 | 27 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1946 | 10 | 28 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1946 | 10 | 29 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1946 | 10 | 30 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1946 | 10 | 31 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1946 | 11 | 1 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1946 | 11 | 2 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1946 | 11 | 3 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1946 | 11 | 4 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1946 | 11 | 5 | 233.7959 | 15 | 218.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1946 | 11 | 6 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1946 | 11 | 7 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1946 | 11 | 8 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1946 | 11 | 9 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1946 | 11 | 10 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1946 | 11 | 11 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1946 | 11 | 12 | 320 | 15 | 305 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1946 | 11 | 13 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1946 | 11 | 14 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1946 | 11 | 15 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1946 | 11 | 16 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1946 | 11 | 17 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1946 | 11 | 18 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1946 | 11 | 19 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1946 | 11 | 20 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1946 | 11 | 21 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1946 | 11 | 22 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1946 | 11 | 23 | 286.0408 | 15 | 271.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1946 | 11 | 24 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1946 | 11 | 25 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1946 | 11 | 26 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1946 | 11 | 27 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1946 | 11 | 28 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1946 | 11 | 29 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1946 | 11 | 30 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1946 | 12 | 1 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1946 | 12 | 2 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1946 | 12 | 3 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1946 | 12 | 4 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1946 | 12 | 5 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1946 | 12 | 6 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1946 | 12 | 7 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1946 | 12 | 8 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1946 | 12 | 9 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1946 | 12 | 10 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1946 | 12 | 11 | 305.6327 | 5 | 300.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1946 | 12 | 12 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1946 | 12 | 13 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1946 | 12 | 14 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1946 | 12 | 15 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1946 | 12 | 16 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1946 | 12 | 17 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1946 | 12 | 18 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1946 | 12 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1946 | 12 | 20 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1946 | 12 | 21 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1946 | 12 | 22 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1946 | 12 | 23 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1946 | 12 | 24 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1946 | 12 | 25 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1946 | 12 | 26 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1946 | 12 | 27 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1946 | 12 | 28 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1946 | 12 | 29 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1946 | 12 | 30 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1946 | 12 | 31 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1947 | 1 | 1 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1947 | 1 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1947 | 1 | 3 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1947 | 1 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1947 | 1 | 5 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1947 | 1 | 6 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1947 | 1 | 7 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1947 | 1 | 8 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1947 | 1 | 9 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1947 | 1 | 10 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1947 | 1 | 11 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1947 | 1 | 12 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1947 | 1 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1947 | 1 | 14 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1947 | 1 | 15 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1947 | 1 | 16 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1947 | 1 | 17 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1947 | 1 | 18 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1947 | 1 | 19 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1947 | 1 | 20 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1947 | 1 | 21 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1947 | 1 | 22 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1947 | 1 | 23 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1947 | 1 | 24 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1947 | 1 | 25 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1947 | 1 | 26 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1947 | 1 | 27 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1947 | 1 | 28 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1947 | 1 | 29 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1947 | 1 | 30 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1947 | 1 | 31 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1947 | 2 | 1 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1947 | 2 | 2 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1947 | 2 | 3 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1947 | 2 | 4 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1947 | 2 | 5 | 829.3878 | 5 | 824.3878 | 28.3412 | 139.3858 | 0.77441 | 27.5668 | 89.27% | 290.4921 | 273.0626 | 6553.5028
1947 | 2 | 6 | 1071.0204 | 5 | 1066.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
1947 | 2 | 7 | 619.102 | 5 | 614.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1947 | 2 | 8 | 459.7551 | 5 | 454.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1947 | 2 | 9 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1947 | 2 | 10 | 288.6531 | 5 | 283.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1947 | 2 | 11 | 239.0204 | 5 | 234.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1947 | 2 | 12 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1947 | 2 | 13 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1947 | 2 | 14 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1947 | 2 | 15 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1947 | 2 | 16 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1947 | 2 | 17 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1947 | 2 | 18 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1947 | 2 | 19 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1947 | 2 | 20 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1947 | 2 | 21 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1947 | 2 | 22 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1947 | 2 | 23 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1947 | 2 | 24 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1947 | 2 | 25 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1947 | 2 | 26 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1947 | 2 | 27 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1947 | 2 | 28 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1947 | 3 | 1 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1947 | 3 | 2 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1947 | 3 | 3 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1947 | 3 | 4 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1947 | 3 | 5 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1947 | 3 | 6 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1947 | 3 | 7 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1947 | 3 | 8 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1947 | 3 | 9 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1947 | 3 | 10 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1947 | 3 | 11 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1947 | 3 | 12 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1947 | 3 | 13 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1947 | 3 | 14 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1947 | 3 | 15 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1947 | 3 | 16 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1947 | 3 | 17 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1947 | 3 | 18 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1947 | 3 | 19 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1947 | 3 | 20 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1947 | 3 | 21 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1947 | 3 | 22 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1947 | 3 | 23 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1947 | 3 | 24 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1947 | 3 | 25 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1947 | 3 | 26 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1947 | 3 | 27 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1947 | 3 | 28 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1947 | 3 | 29 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1947 | 3 | 30 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1947 | 3 | 31 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1947 | 4 | 1 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1947 | 4 | 2 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1947 | 4 | 3 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1947 | 4 | 4 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1947 | 4 | 5 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1947 | 4 | 6 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1947 | 4 | 7 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1947 | 4 | 8 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1947 | 4 | 9 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1947 | 4 | 10 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1947 | 4 | 11 | 744.4898 | 25 | 719.4898 | 28.511 | 139.3858 | 0.77441 | 27.7366 | 89.27% | 292.2814 | 274.7445 | 6593.8686
1947 | 4 | 12 | 1541.2245 | 25 | 1516.2245 | 26.9176 | 139.3858 | 0.77441 | 26.1431 | 89.27% | 275.4898 | 258.9604 | 6215.0506
1947 | 4 | 13 | 1580.4082 | 25 | 1555.4082 | 26.8392 | 139.3858 | 0.77441 | 26.0648 | 89.27% | 274.664 | 258.1842 | 6196.4202
1947 | 4 | 14 | 1018.7755 | 25 | 993.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
1947 | 4 | 15 | 718.3673 | 25 | 693.3673 | 28.5633 | 139.3858 | 0.77441 | 27.7889 | 89.27% | 292.832 | 275.262 | 6606.2889
1947 | 4 | 16 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1947 | 4 | 17 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1947 | 4 | 18 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1947 | 4 | 19 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1947 | 4 | 20 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1947 | 4 | 21 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1947 | 4 | 22 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1947 | 4 | 23 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1947 | 4 | 24 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1947 | 4 | 25 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1947 | 4 | 26 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1947 | 4 | 27 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1947 | 4 | 28 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1947 | 4 | 29 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1947 | 4 | 30 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1947 | 5 | 1 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1947 | 5 | 2 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1947 | 5 | 3 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1947 | 5 | 4 | 940.4082 | 25 | 915.4082 | 28.1192 | 139.3858 | 0.77441 | 27.3448 | 89.27% | 288.1523 | 270.8632 | 6500.7167
1947 | 5 | 5 | 1280 | 25 | 1255 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
1947 | 5 | 6 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1947 | 5 | 7 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1947 | 5 | 8 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1947 | 5 | 9 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1947 | 5 | 10 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1947 | 5 | 11 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1947 | 5 | 12 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1947 | 5 | 13 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1947 | 5 | 14 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1947 | 5 | 15 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1947 | 5 | 16 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1947 | 5 | 17 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1947 | 5 | 18 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1947 | 5 | 19 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1947 | 5 | 20 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1947 | 5 | 21 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1947 | 5 | 22 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1947 | 5 | 23 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1947 | 5 | 24 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1947 | 5 | 25 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1947 | 5 | 26 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1947 | 5 | 27 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1947 | 5 | 28 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1947 | 5 | 29 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1947 | 5 | 30 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1947 | 5 | 31 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1947 | 6 | 1 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1947 | 6 | 2 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1947 | 6 | 3 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1947 | 6 | 4 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1947 | 6 | 5 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1947 | 6 | 6 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1947 | 6 | 7 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1947 | 6 | 8 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1947 | 6 | 9 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1947 | 6 | 10 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1947 | 6 | 11 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1947 | 6 | 12 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1947 | 6 | 13 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1947 | 6 | 14 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1947 | 6 | 15 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1947 | 6 | 16 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1947 | 6 | 17 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1947 | 6 | 18 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1947 | 6 | 19 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1947 | 6 | 20 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1947 | 6 | 21 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1947 | 6 | 22 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1947 | 6 | 23 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1947 | 6 | 24 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1947 | 6 | 25 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1947 | 6 | 26 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1947 | 6 | 27 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1947 | 6 | 28 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1947 | 6 | 29 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1947 | 6 | 30 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1947 | 7 | 1 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1947 | 7 | 2 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1947 | 7 | 3 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1947 | 7 | 4 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1947 | 7 | 5 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1947 | 7 | 6 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1947 | 7 | 7 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1947 | 7 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1947 | 7 | 9 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1947 | 7 | 10 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1947 | 7 | 11 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1947 | 7 | 12 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1947 | 7 | 13 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1947 | 7 | 14 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1947 | 7 | 15 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1947 | 7 | 16 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1947 | 7 | 17 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1947 | 7 | 18 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1947 | 7 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1947 | 7 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1947 | 7 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1947 | 7 | 22 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1947 | 7 | 23 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1947 | 7 | 24 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1947 | 7 | 25 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1947 | 7 | 26 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1947 | 7 | 27 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1947 | 7 | 28 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1947 | 7 | 29 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1947 | 7 | 30 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1947 | 7 | 31 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1947 | 8 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1947 | 8 | 2 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1947 | 8 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1947 | 8 | 4 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1947 | 8 | 5 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1947 | 8 | 6 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1947 | 8 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1947 | 8 | 8 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1947 | 8 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1947 | 8 | 10 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1947 | 8 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1947 | 8 | 12 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1947 | 8 | 13 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1947 | 8 | 14 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1947 | 8 | 15 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1947 | 8 | 16 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1947 | 8 | 17 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1947 | 8 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1947 | 8 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1947 | 8 | 20 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1947 | 8 | 21 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1947 | 8 | 22 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 8 | 23 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1947 | 8 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1947 | 8 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1947 | 8 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1947 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1947 | 8 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1947 | 8 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1947 | 8 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1947 | 8 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1947 | 9 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1947 | 9 | 2 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1947 | 9 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1947 | 9 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1947 | 9 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1947 | 9 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1947 | 9 | 7 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1947 | 9 | 8 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1947 | 9 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1947 | 9 | 10 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1947 | 9 | 11 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1947 | 9 | 12 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1947 | 9 | 13 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1947 | 9 | 14 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1947 | 9 | 15 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1947 | 9 | 16 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1947 | 9 | 17 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1947 | 9 | 18 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1947 | 9 | 19 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1947 | 9 | 20 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1947 | 9 | 21 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1947 | 9 | 22 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1947 | 9 | 23 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1947 | 9 | 24 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1947 | 9 | 25 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1947 | 9 | 26 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1947 | 9 | 27 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1947 | 9 | 28 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1947 | 9 | 29 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1947 | 9 | 30 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1947 | 10 | 1 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1947 | 10 | 2 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1947 | 10 | 3 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1947 | 10 | 4 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1947 | 10 | 5 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1947 | 10 | 6 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1947 | 10 | 7 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1947 | 10 | 8 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1947 | 10 | 9 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 10 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1947 | 10 | 11 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1947 | 10 | 12 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1947 | 10 | 13 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1947 | 10 | 14 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1947 | 10 | 15 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 16 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 17 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 18 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 19 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 20 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1947 | 10 | 21 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 22 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1947 | 10 | 23 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1947 | 10 | 24 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1947 | 10 | 25 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1947 | 10 | 26 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1947 | 10 | 27 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1947 | 10 | 28 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1947 | 10 | 29 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1947 | 10 | 30 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1947 | 10 | 31 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1947 | 11 | 1 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1947 | 11 | 2 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1947 | 11 | 3 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1947 | 11 | 4 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1947 | 11 | 5 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1947 | 11 | 6 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1947 | 11 | 7 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1947 | 11 | 8 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1947 | 11 | 9 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1947 | 11 | 10 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1947 | 11 | 11 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1947 | 11 | 12 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1947 | 11 | 13 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1947 | 11 | 14 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1947 | 11 | 15 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1947 | 11 | 16 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1947 | 11 | 17 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1947 | 11 | 18 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1947 | 11 | 19 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1947 | 11 | 20 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1947 | 11 | 21 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1947 | 11 | 22 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1947 | 11 | 23 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1947 | 11 | 24 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1947 | 11 | 25 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1947 | 11 | 26 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1947 | 11 | 27 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1947 | 11 | 28 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1947 | 11 | 29 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1947 | 11 | 30 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1947 | 12 | 1 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1947 | 12 | 2 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1947 | 12 | 3 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 4 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1947 | 12 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 8 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 9 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 10 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1947 | 12 | 11 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1947 | 12 | 12 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1947 | 12 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1947 | 12 | 14 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1947 | 12 | 15 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1947 | 12 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1947 | 12 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1947 | 12 | 18 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1947 | 12 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1947 | 12 | 20 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1947 | 12 | 21 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1947 | 12 | 22 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1947 | 12 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1947 | 12 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 26 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1947 | 12 | 27 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1947 | 12 | 28 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1947 | 12 | 29 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1947 | 12 | 30 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1947 | 12 | 31 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 1 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 2 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1948 | 1 | 3 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1948 | 1 | 4 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 8 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 9 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 10 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 1 | 11 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1948 | 1 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1948 | 1 | 13 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1948 | 1 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 1 | 16 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 17 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 18 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 21 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 23 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 1 | 24 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 25 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 27 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 1 | 30 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 1 | 31 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 1 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 2 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 5 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 7 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 8 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 9 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 10 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1948 | 2 | 11 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1948 | 2 | 12 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1948 | 2 | 13 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1948 | 2 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 2 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1948 | 2 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 17 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1948 | 2 | 18 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1948 | 2 | 19 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1948 | 2 | 20 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1948 | 2 | 21 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1948 | 2 | 22 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1948 | 2 | 23 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 26 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 27 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 2 | 29 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 3 | 1 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1948 | 3 | 2 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1948 | 3 | 3 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1948 | 3 | 4 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1948 | 3 | 5 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1948 | 3 | 6 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1948 | 3 | 7 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1948 | 3 | 8 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1948 | 3 | 9 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1948 | 3 | 10 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1948 | 3 | 11 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1948 | 3 | 12 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1948 | 3 | 13 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1948 | 3 | 14 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1948 | 3 | 15 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1948 | 3 | 16 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1948 | 3 | 17 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1948 | 3 | 18 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1948 | 3 | 19 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1948 | 3 | 20 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1948 | 3 | 21 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1948 | 3 | 22 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1948 | 3 | 23 | 1018.7755 | 25 | 993.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
1948 | 3 | 24 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1948 | 3 | 25 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1948 | 3 | 26 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1948 | 3 | 27 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1948 | 3 | 28 | 1280 | 25 | 1255 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
1948 | 3 | 29 | 868.5714 | 25 | 843.5714 | 28.2629 | 139.3858 | 0.77441 | 27.4884 | 89.27% | 289.6663 | 272.2863 | 6534.8724
1948 | 3 | 30 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1948 | 3 | 31 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1948 | 4 | 1 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1948 | 4 | 2 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1948 | 4 | 3 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1948 | 4 | 4 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1948 | 4 | 5 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1948 | 4 | 6 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1948 | 4 | 7 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1948 | 4 | 8 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1948 | 4 | 9 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1948 | 4 | 10 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1948 | 4 | 11 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1948 | 4 | 12 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1948 | 4 | 13 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1948 | 4 | 14 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1948 | 4 | 15 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1948 | 4 | 16 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1948 | 4 | 17 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1948 | 4 | 18 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1948 | 4 | 19 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1948 | 4 | 20 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1948 | 4 | 21 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1948 | 4 | 22 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1948 | 4 | 23 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1948 | 4 | 24 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1948 | 4 | 25 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1948 | 4 | 26 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1948 | 4 | 27 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1948 | 4 | 28 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1948 | 4 | 29 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1948 | 4 | 30 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1948 | 5 | 1 | 666.1224 | 25 | 641.1224 | 28.6678 | 139.3858 | 0.77441 | 27.8933 | 89.27% | 293.933 | 276.2971 | 6631.1294
1948 | 5 | 2 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1948 | 5 | 3 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1948 | 5 | 4 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1948 | 5 | 5 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1948 | 5 | 6 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1948 | 5 | 7 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1948 | 5 | 8 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1948 | 5 | 9 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1948 | 5 | 10 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1948 | 5 | 11 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1948 | 5 | 12 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1948 | 5 | 13 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1948 | 5 | 14 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1948 | 5 | 15 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1948 | 5 | 16 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1948 | 5 | 17 | 816.3265 | 25 | 791.3265 | 28.3673 | 139.3858 | 0.77441 | 27.5929 | 89.27% | 290.7674 | 273.3214 | 6559.7129
1948 | 5 | 18 | 1750.2041 | 25 | 1725.2041 | 26.4996 | 139.3858 | 0.77441 | 25.7252 | 89.27% | 271.0855 | 254.8204 | 6115.6885
1948 | 5 | 19 | 1260.4082 | 25 | 1235.4082 | 27.4792 | 139.3858 | 0.77441 | 26.7048 | 89.27% | 281.4082 | 264.5237 | 6348.5684
1948 | 5 | 20 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1948 | 5 | 21 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1948 | 5 | 22 | 697.4694 | 25 | 672.4694 | 28.6051 | 139.3858 | 0.77441 | 27.8307 | 89.27% | 293.2724 | 275.676 | 6616.2251
1948 | 5 | 23 | 739.2653 | 25 | 714.2653 | 28.5215 | 139.3858 | 0.77441 | 27.7471 | 89.27% | 292.3915 | 274.848 | 6596.3527
1948 | 5 | 24 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1948 | 5 | 25 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1948 | 5 | 26 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1948 | 5 | 27 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1948 | 5 | 28 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1948 | 5 | 29 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1948 | 5 | 30 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1948 | 5 | 31 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1948 | 6 | 1 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1948 | 6 | 2 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1948 | 6 | 3 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1948 | 6 | 4 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1948 | 6 | 5 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1948 | 6 | 6 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1948 | 6 | 7 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1948 | 6 | 8 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1948 | 6 | 9 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1948 | 6 | 10 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1948 | 6 | 11 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1948 | 6 | 12 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1948 | 6 | 13 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1948 | 6 | 14 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1948 | 6 | 15 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1948 | 6 | 16 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1948 | 6 | 17 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1948 | 6 | 18 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1948 | 6 | 19 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1948 | 6 | 20 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1948 | 6 | 21 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1948 | 6 | 22 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1948 | 6 | 23 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1948 | 6 | 24 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1948 | 6 | 25 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1948 | 6 | 26 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1948 | 6 | 27 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1948 | 6 | 28 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1948 | 6 | 29 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1948 | 6 | 30 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1948 | 7 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1948 | 7 | 2 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1948 | 7 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1948 | 7 | 4 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1948 | 7 | 5 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1948 | 7 | 6 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1948 | 7 | 7 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1948 | 7 | 8 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1948 | 7 | 9 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1948 | 7 | 10 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1948 | 7 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1948 | 7 | 12 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1948 | 7 | 13 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1948 | 7 | 14 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1948 | 7 | 15 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1948 | 7 | 16 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1948 | 7 | 17 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 7 | 18 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 7 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1948 | 7 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 7 | 21 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1948 | 7 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 7 | 23 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 7 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 7 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1948 | 7 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 7 | 27 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 7 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1948 | 7 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1948 | 7 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1948 | 7 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1948 | 8 | 1 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1948 | 8 | 2 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1948 | 8 | 3 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1948 | 8 | 4 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1948 | 8 | 5 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1948 | 8 | 6 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1948 | 8 | 7 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 8 | 8 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1948 | 8 | 9 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1948 | 8 | 10 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1948 | 8 | 11 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1948 | 8 | 12 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1948 | 8 | 13 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1948 | 8 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1948 | 8 | 15 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1948 | 8 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1948 | 8 | 17 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1948 | 8 | 18 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1948 | 8 | 19 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1948 | 8 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1948 | 8 | 21 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1948 | 8 | 22 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1948 | 8 | 23 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1948 | 8 | 24 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1948 | 8 | 25 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1948 | 8 | 26 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1948 | 8 | 27 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1948 | 8 | 28 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1948 | 8 | 29 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1948 | 8 | 30 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1948 | 8 | 31 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1948 | 9 | 1 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1948 | 9 | 2 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1948 | 9 | 3 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1948 | 9 | 4 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1948 | 9 | 5 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1948 | 9 | 6 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1948 | 9 | 7 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1948 | 9 | 8 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1948 | 9 | 9 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1948 | 9 | 10 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1948 | 9 | 11 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1948 | 9 | 12 | 4.702 | 15 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1948 | 9 | 13 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1948 | 9 | 14 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1948 | 9 | 15 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1948 | 9 | 16 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1948 | 9 | 17 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1948 | 9 | 18 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1948 | 9 | 19 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1948 | 9 | 20 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1948 | 9 | 21 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1948 | 9 | 22 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1948 | 9 | 23 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1948 | 9 | 24 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1948 | 9 | 25 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1948 | 9 | 26 | 4.702 | 15 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1948 | 9 | 27 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1948 | 9 | 28 | 3.5265 | 15 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1948 | 9 | 29 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
1948 | 9 | 30 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1948 | 10 | 1 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
1948 | 10 | 2 | 3.5265 | 15 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1948 | 10 | 3 | 3.7878 | 15 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1948 | 10 | 4 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1948 | 10 | 5 | 3.0041 | 15 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1948 | 10 | 6 | 3.2653 | 15 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1948 | 10 | 7 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
1948 | 10 | 8 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
1948 | 10 | 9 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1948 | 10 | 10 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1948 | 10 | 11 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1948 | 10 | 12 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1948 | 10 | 13 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1948 | 10 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1948 | 10 | 15 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1948 | 10 | 16 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1948 | 10 | 17 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1948 | 10 | 18 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1948 | 10 | 19 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1948 | 10 | 20 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1948 | 10 | 21 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1948 | 10 | 22 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1948 | 10 | 23 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1948 | 10 | 24 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1948 | 10 | 25 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1948 | 10 | 26 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1948 | 10 | 27 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1948 | 10 | 28 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1948 | 10 | 29 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1948 | 10 | 30 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1948 | 10 | 31 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1948 | 11 | 1 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1948 | 11 | 2 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1948 | 11 | 3 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1948 | 11 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1948 | 11 | 5 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1948 | 11 | 6 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1948 | 11 | 7 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1948 | 11 | 8 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1948 | 11 | 9 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1948 | 11 | 10 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1948 | 11 | 11 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1948 | 11 | 12 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1948 | 11 | 13 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1948 | 11 | 14 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1948 | 11 | 15 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1948 | 11 | 16 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1948 | 11 | 17 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1948 | 11 | 18 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1948 | 11 | 19 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1948 | 11 | 20 | 333.0612 | 15 | 318.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1948 | 11 | 21 | 395.7551 | 15 | 380.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1948 | 11 | 22 | 236.4082 | 15 | 221.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1948 | 11 | 23 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1948 | 11 | 24 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1948 | 11 | 25 | 305.6327 | 15 | 290.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1948 | 11 | 26 | 249.4694 | 15 | 234.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1948 | 11 | 27 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1948 | 11 | 28 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1948 | 11 | 29 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1948 | 11 | 30 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1948 | 12 | 1 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1948 | 12 | 2 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1948 | 12 | 3 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1948 | 12 | 4 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1948 | 12 | 5 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1948 | 12 | 6 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1948 | 12 | 7 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1948 | 12 | 8 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1948 | 12 | 9 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1948 | 12 | 10 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1948 | 12 | 11 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1948 | 12 | 12 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1948 | 12 | 13 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1948 | 12 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1948 | 12 | 15 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1948 | 12 | 16 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1948 | 12 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1948 | 12 | 18 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1948 | 12 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1948 | 12 | 20 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1948 | 12 | 21 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1948 | 12 | 22 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1948 | 12 | 23 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1948 | 12 | 24 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1948 | 12 | 25 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1948 | 12 | 26 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1948 | 12 | 27 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1948 | 12 | 28 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1948 | 12 | 29 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1948 | 12 | 30 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1948 | 12 | 31 | 1488.9796 | 5 | 1483.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1949 | 1 | 1 | 1933.0612 | 5 | 1928.0612 | 26.1339 | 139.3858 | 0.77441 | 25.3595 | 89.27% | 267.2317 | 251.1978 | 6028.7467
1949 | 1 | 2 | 881.6327 | 5 | 876.6327 | 28.2367 | 139.3858 | 0.77441 | 27.4623 | 89.27% | 289.3911 | 272.0276 | 6528.6623
1949 | 1 | 3 | 475.4286 | 5 | 470.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1949 | 1 | 4 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1949 | 1 | 5 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1949 | 1 | 6 | 744.4898 | 5 | 739.4898 | 28.511 | 139.3858 | 0.77441 | 27.7366 | 89.27% | 292.2814 | 274.7445 | 6593.8686
1949 | 1 | 7 | 842.449 | 5 | 837.449 | 28.3151 | 139.3858 | 0.77441 | 27.5407 | 89.27% | 290.2169 | 272.8039 | 6547.2927
1949 | 1 | 8 | 472.8163 | 5 | 467.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1949 | 1 | 9 | 330.449 | 5 | 325.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1949 | 1 | 10 | 271.6735 | 5 | 266.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1949 | 1 | 11 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1949 | 1 | 12 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1949 | 1 | 13 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1949 | 1 | 14 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1949 | 1 | 15 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1949 | 1 | 16 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1949 | 1 | 17 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1949 | 1 | 18 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1949 | 1 | 19 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1949 | 1 | 20 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1949 | 1 | 21 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1949 | 1 | 22 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1949 | 1 | 23 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1949 | 1 | 24 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1949 | 1 | 25 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1949 | 1 | 26 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1949 | 1 | 27 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1949 | 1 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1949 | 1 | 29 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1949 | 1 | 30 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1949 | 1 | 31 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1949 | 2 | 1 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1949 | 2 | 2 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1949 | 2 | 3 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1949 | 2 | 4 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1949 | 2 | 5 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 6 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 7 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 9 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 10 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1949 | 2 | 11 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1949 | 2 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1949 | 2 | 14 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1949 | 2 | 15 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1949 | 2 | 16 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1949 | 2 | 17 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1949 | 2 | 18 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1949 | 2 | 19 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1949 | 2 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1949 | 2 | 21 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1949 | 2 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1949 | 2 | 23 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1949 | 2 | 24 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1949 | 2 | 25 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1949 | 2 | 26 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1949 | 2 | 27 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1949 | 2 | 28 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1949 | 3 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1949 | 3 | 2 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1949 | 3 | 3 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1949 | 3 | 4 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1949 | 3 | 5 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1949 | 3 | 6 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1949 | 3 | 7 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1949 | 3 | 8 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1949 | 3 | 9 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1949 | 3 | 10 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1949 | 3 | 11 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1949 | 3 | 12 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1949 | 3 | 13 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1949 | 3 | 14 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1949 | 3 | 15 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1949 | 3 | 16 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1949 | 3 | 17 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1949 | 3 | 18 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1949 | 3 | 19 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1949 | 3 | 20 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1949 | 3 | 21 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1949 | 3 | 22 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1949 | 3 | 23 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1949 | 3 | 24 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1949 | 3 | 25 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1949 | 3 | 26 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1949 | 3 | 27 | 670.0408 | 25 | 645.0408 | 28.6599 | 139.3858 | 0.77441 | 27.8855 | 89.27% | 293.8505 | 276.2194 | 6629.2664
1949 | 3 | 28 | 1009.6327 | 25 | 984.6327 | 27.9807 | 139.3858 | 0.77441 | 27.2063 | 89.27% | 286.6934 | 269.4918 | 6467.803
1949 | 3 | 29 | 1243.4286 | 25 | 1218.4286 | 27.5131 | 139.3858 | 0.77441 | 26.7387 | 89.27% | 281.766 | 264.8601 | 6356.6416
1949 | 3 | 30 | 901.2245 | 25 | 876.2245 | 28.1976 | 139.3858 | 0.77441 | 27.4231 | 89.27% | 288.9782 | 271.6395 | 6519.3471
1949 | 3 | 31 | 714.449 | 25 | 689.449 | 28.5711 | 139.3858 | 0.77441 | 27.7967 | 89.27% | 292.9145 | 275.3397 | 6608.1519
1949 | 4 | 1 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1949 | 4 | 2 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1949 | 4 | 3 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
1949 | 4 | 4 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1949 | 4 | 5 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1949 | 4 | 6 | 519.8367 | 25 | 494.8367 | 28.9603 | 139.3858 | 0.77441 | 28.1859 | 89.27% | 297.0161 | 279.1951 | 6700.6829
1949 | 4 | 7 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1949 | 4 | 8 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1949 | 4 | 9 | 536.8163 | 25 | 511.8163 | 28.9264 | 139.3858 | 0.77441 | 28.152 | 89.27% | 296.6582 | 278.8587 | 6692.6097
1949 | 4 | 10 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1949 | 4 | 11 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1949 | 4 | 12 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1949 | 4 | 13 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1949 | 4 | 14 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1949 | 4 | 15 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1949 | 4 | 16 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1949 | 4 | 17 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1949 | 4 | 18 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1949 | 4 | 19 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1949 | 4 | 20 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1949 | 4 | 21 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1949 | 4 | 22 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1949 | 4 | 23 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1949 | 4 | 24 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1949 | 4 | 25 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1949 | 4 | 26 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1949 | 4 | 27 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1949 | 4 | 28 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1949 | 4 | 29 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1949 | 4 | 30 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1949 | 5 | 1 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1949 | 5 | 2 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1949 | 5 | 3 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1949 | 5 | 4 | 829.3878 | 25 | 804.3878 | 28.3412 | 139.3858 | 0.77441 | 27.5668 | 89.27% | 290.4921 | 273.0626 | 6553.5028
1949 | 5 | 5 | 436.2449 | 25 | 411.2449 | 29.1275 | 139.3858 | 0.77441 | 28.3531 | 89.27% | 298.7778 | 280.8512 | 6740.4278
1949 | 5 | 6 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1949 | 5 | 7 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1949 | 5 | 8 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1949 | 5 | 9 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1949 | 5 | 10 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1949 | 5 | 11 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1949 | 5 | 12 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1949 | 5 | 13 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1949 | 5 | 14 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1949 | 5 | 15 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1949 | 5 | 16 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1949 | 5 | 17 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1949 | 5 | 18 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1949 | 5 | 19 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1949 | 5 | 20 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1949 | 5 | 21 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1949 | 5 | 22 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1949 | 5 | 23 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1949 | 5 | 24 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1949 | 5 | 25 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1949 | 5 | 26 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1949 | 5 | 27 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1949 | 5 | 28 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1949 | 5 | 29 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1949 | 5 | 30 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1949 | 5 | 31 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1949 | 6 | 1 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1949 | 6 | 2 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1949 | 6 | 3 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1949 | 6 | 4 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1949 | 6 | 5 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1949 | 6 | 6 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1949 | 6 | 7 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1949 | 6 | 8 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1949 | 6 | 9 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1949 | 6 | 10 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1949 | 6 | 11 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1949 | 6 | 12 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1949 | 6 | 13 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1949 | 6 | 14 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1949 | 6 | 15 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1949 | 6 | 16 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1949 | 6 | 17 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1949 | 6 | 18 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1949 | 6 | 19 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1949 | 6 | 20 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1949 | 6 | 21 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1949 | 6 | 22 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1949 | 6 | 23 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1949 | 6 | 24 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1949 | 6 | 25 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1949 | 6 | 26 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1949 | 6 | 27 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1949 | 6 | 28 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1949 | 6 | 29 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1949 | 6 | 30 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1949 | 7 | 1 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1949 | 7 | 2 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1949 | 7 | 3 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1949 | 7 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1949 | 7 | 5 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1949 | 7 | 6 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1949 | 7 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1949 | 7 | 8 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1949 | 7 | 9 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1949 | 7 | 10 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1949 | 7 | 11 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1949 | 7 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1949 | 7 | 13 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1949 | 7 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1949 | 7 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1949 | 7 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1949 | 7 | 17 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1949 | 7 | 18 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1949 | 7 | 19 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1949 | 7 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1949 | 7 | 21 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1949 | 7 | 22 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1949 | 7 | 23 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1949 | 7 | 24 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1949 | 7 | 25 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1949 | 7 | 26 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1949 | 7 | 27 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1949 | 7 | 28 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1949 | 7 | 29 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1949 | 7 | 30 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1949 | 7 | 31 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1949 | 8 | 1 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1949 | 8 | 2 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1949 | 8 | 3 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1949 | 8 | 4 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1949 | 8 | 5 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1949 | 8 | 6 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1949 | 8 | 7 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1949 | 8 | 8 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1949 | 8 | 9 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1949 | 8 | 10 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1949 | 8 | 11 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1949 | 8 | 12 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1949 | 8 | 13 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1949 | 8 | 14 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1949 | 8 | 15 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1949 | 8 | 16 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1949 | 8 | 17 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1949 | 8 | 18 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1949 | 8 | 19 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1949 | 8 | 20 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1949 | 8 | 21 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1949 | 8 | 22 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1949 | 8 | 23 | 3.2653 | 5 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1949 | 8 | 24 | 2.6122 | 5 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1949 | 8 | 25 | 2.351 | 5 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
1949 | 8 | 26 | 2.351 | 5 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
1949 | 8 | 27 | 2.0898 | 5 | 0 | 29.9958 | 0 | 0 | 29.9958 | 0% | 0 | 0 | 0
1949 | 8 | 28 | 1.698 | 5 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
1949 | 8 | 29 | 2.6122 | 5 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1949 | 8 | 30 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1949 | 8 | 31 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1949 | 9 | 1 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1949 | 9 | 2 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1949 | 9 | 3 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1949 | 9 | 4 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1949 | 9 | 5 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1949 | 9 | 6 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1949 | 9 | 7 | 3.5265 | 15 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1949 | 9 | 8 | 3.2653 | 15 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1949 | 9 | 9 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
1949 | 9 | 10 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1949 | 9 | 11 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1949 | 9 | 12 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1949 | 9 | 13 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1949 | 9 | 14 | 4.049 | 15 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
1949 | 9 | 15 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1949 | 9 | 16 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1949 | 9 | 17 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1949 | 9 | 18 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1949 | 9 | 19 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1949 | 9 | 20 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1949 | 9 | 21 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1949 | 9 | 22 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1949 | 9 | 23 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1949 | 9 | 24 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1949 | 9 | 25 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1949 | 9 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1949 | 9 | 27 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1949 | 9 | 28 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1949 | 9 | 29 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1949 | 9 | 30 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1949 | 10 | 1 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1949 | 10 | 2 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1949 | 10 | 3 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1949 | 10 | 4 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1949 | 10 | 5 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1949 | 10 | 6 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 7 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 8 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1949 | 10 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1949 | 10 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1949 | 10 | 11 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1949 | 10 | 12 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 13 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1949 | 10 | 14 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 15 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1949 | 10 | 16 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1949 | 10 | 17 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1949 | 10 | 18 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1949 | 10 | 19 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1949 | 10 | 20 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1949 | 10 | 21 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1949 | 10 | 22 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 23 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 24 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 25 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1949 | 10 | 26 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1949 | 10 | 27 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1949 | 10 | 28 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1949 | 10 | 29 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1949 | 10 | 30 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1949 | 10 | 31 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1949 | 11 | 1 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1949 | 11 | 2 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1949 | 11 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1949 | 11 | 4 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1949 | 11 | 5 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1949 | 11 | 6 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1949 | 11 | 7 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1949 | 11 | 8 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1949 | 11 | 9 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1949 | 11 | 10 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1949 | 11 | 11 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1949 | 11 | 12 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1949 | 11 | 13 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1949 | 11 | 14 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1949 | 11 | 15 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1949 | 11 | 16 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1949 | 11 | 17 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1949 | 11 | 18 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1949 | 11 | 19 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1949 | 11 | 20 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1949 | 11 | 21 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1949 | 11 | 22 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1949 | 11 | 23 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1949 | 11 | 24 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1949 | 11 | 25 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1949 | 11 | 26 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1949 | 11 | 27 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1949 | 11 | 28 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1949 | 11 | 29 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1949 | 11 | 30 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1949 | 12 | 1 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1949 | 12 | 2 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1949 | 12 | 3 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1949 | 12 | 4 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1949 | 12 | 5 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1949 | 12 | 6 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1949 | 12 | 7 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1949 | 12 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1949 | 12 | 9 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1949 | 12 | 10 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1949 | 12 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1949 | 12 | 12 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1949 | 12 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1949 | 12 | 14 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1949 | 12 | 15 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1949 | 12 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1949 | 12 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1949 | 12 | 18 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1949 | 12 | 19 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1949 | 12 | 20 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1949 | 12 | 21 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1949 | 12 | 22 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1949 | 12 | 23 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1949 | 12 | 24 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1949 | 12 | 25 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1949 | 12 | 26 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1949 | 12 | 27 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1949 | 12 | 28 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1949 | 12 | 29 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1949 | 12 | 30 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1949 | 12 | 31 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1950 | 1 | 1 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1950 | 1 | 2 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1950 | 1 | 3 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1950 | 1 | 4 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1950 | 1 | 5 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1950 | 1 | 6 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1950 | 1 | 7 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1950 | 1 | 8 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1950 | 1 | 9 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1950 | 1 | 10 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1950 | 1 | 11 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1950 | 1 | 12 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1950 | 1 | 13 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1950 | 1 | 14 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1950 | 1 | 15 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1950 | 1 | 16 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1950 | 1 | 17 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1950 | 1 | 18 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1950 | 1 | 19 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1950 | 1 | 20 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1950 | 1 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1950 | 1 | 22 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1950 | 1 | 23 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1950 | 1 | 24 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1950 | 1 | 25 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1950 | 1 | 26 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1950 | 1 | 27 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1950 | 1 | 28 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1950 | 1 | 29 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1950 | 1 | 30 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1950 | 1 | 31 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1950 | 2 | 1 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1950 | 2 | 2 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1950 | 2 | 3 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1950 | 2 | 4 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1950 | 2 | 5 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1950 | 2 | 6 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1950 | 2 | 7 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1950 | 2 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1950 | 2 | 9 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1950 | 2 | 10 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1950 | 2 | 11 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1950 | 2 | 12 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1950 | 2 | 13 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1950 | 2 | 14 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1950 | 2 | 15 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1950 | 2 | 16 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1950 | 2 | 17 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1950 | 2 | 18 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1950 | 2 | 19 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1950 | 2 | 20 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1950 | 2 | 21 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1950 | 2 | 22 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1950 | 2 | 23 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1950 | 2 | 24 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1950 | 2 | 25 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1950 | 2 | 26 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1950 | 2 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1950 | 2 | 28 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1950 | 3 | 1 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1950 | 3 | 2 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1950 | 3 | 3 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1950 | 3 | 4 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1950 | 3 | 5 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1950 | 3 | 6 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1950 | 3 | 7 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1950 | 3 | 8 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1950 | 3 | 9 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1950 | 3 | 10 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1950 | 3 | 11 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1950 | 3 | 12 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1950 | 3 | 13 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1950 | 3 | 14 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1950 | 3 | 15 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1950 | 3 | 16 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1950 | 3 | 17 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1950 | 3 | 18 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1950 | 3 | 19 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1950 | 3 | 20 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1950 | 3 | 21 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1950 | 3 | 22 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1950 | 3 | 23 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1950 | 3 | 24 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1950 | 3 | 25 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1950 | 3 | 26 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1950 | 3 | 27 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1950 | 3 | 28 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1950 | 3 | 29 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1950 | 3 | 30 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1950 | 3 | 31 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
1950 | 4 | 1 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
1950 | 4 | 2 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1950 | 4 | 3 | 398.3673 | 25 | 373.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1950 | 4 | 4 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1950 | 4 | 5 | 689.6327 | 25 | 664.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
1950 | 4 | 6 | 949.551 | 25 | 924.551 | 28.1009 | 139.3858 | 0.77441 | 27.3265 | 89.27% | 287.9596 | 270.6821 | 6496.3696
1950 | 4 | 7 | 685.7143 | 25 | 660.7143 | 28.6286 | 139.3858 | 0.77441 | 27.8542 | 89.27% | 293.5201 | 275.9089 | 6621.8142
1950 | 4 | 8 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1950 | 4 | 9 | 569.4694 | 25 | 544.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
1950 | 4 | 10 | 513.3061 | 25 | 488.3061 | 28.9734 | 139.3858 | 0.77441 | 28.199 | 89.27% | 297.1537 | 279.3245 | 6703.788
1950 | 4 | 11 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1950 | 4 | 12 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1950 | 4 | 13 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1950 | 4 | 14 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1950 | 4 | 15 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1950 | 4 | 16 | 693.551 | 25 | 668.551 | 28.6129 | 139.3858 | 0.77441 | 27.8385 | 89.27% | 293.355 | 275.7537 | 6618.0882
1950 | 4 | 17 | 969.1429 | 25 | 944.1429 | 28.0617 | 139.3858 | 0.77441 | 27.2873 | 89.27% | 287.5467 | 270.2939 | 6487.0544
1950 | 4 | 18 | 1149.3878 | 25 | 1124.3878 | 27.7012 | 139.3858 | 0.77441 | 26.9268 | 89.27% | 283.748 | 266.7231 | 6401.3546
1950 | 4 | 19 | 1295.6735 | 25 | 1270.6735 | 27.4087 | 139.3858 | 0.77441 | 26.6342 | 89.27% | 280.6649 | 263.825 | 6331.8011
1950 | 4 | 20 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
1950 | 4 | 21 | 3147.7551 | 25 | 3122.7551 | 23.7045 | 0 | 0 | 23.7045 | 0% | 0 | 0 | 0
1950 | 4 | 22 | 1632.6531 | 25 | 1607.6531 | 26.7347 | 139.3858 | 0.77441 | 25.9603 | 89.27% | 273.5629 | 257.1492 | 6171.5797
1950 | 4 | 23 | 993.9592 | 25 | 968.9592 | 28.0121 | 139.3858 | 0.77441 | 27.2377 | 89.27% | 287.0237 | 269.8023 | 6475.2551
1950 | 4 | 24 | 790.2041 | 25 | 765.2041 | 28.4196 | 139.3858 | 0.77441 | 27.6452 | 89.27% | 291.318 | 273.8389 | 6572.1332
1950 | 4 | 25 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1950 | 4 | 26 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1950 | 4 | 27 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
1950 | 4 | 28 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1950 | 4 | 29 | 453.2245 | 25 | 428.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
1950 | 4 | 30 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1950 | 5 | 1 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1950 | 5 | 2 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1950 | 5 | 3 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1950 | 5 | 4 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1950 | 5 | 5 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1950 | 5 | 6 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1950 | 5 | 7 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1950 | 5 | 8 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1950 | 5 | 9 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1950 | 5 | 10 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1950 | 5 | 11 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1950 | 5 | 12 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1950 | 5 | 13 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1950 | 5 | 14 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1950 | 5 | 15 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1950 | 5 | 16 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1950 | 5 | 17 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1950 | 5 | 18 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1950 | 5 | 19 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1950 | 5 | 20 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1950 | 5 | 21 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1950 | 5 | 22 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1950 | 5 | 23 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1950 | 5 | 24 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1950 | 5 | 25 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1950 | 5 | 26 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1950 | 5 | 27 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1950 | 5 | 28 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1950 | 5 | 29 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1950 | 5 | 30 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1950 | 5 | 31 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1950 | 6 | 1 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1950 | 6 | 2 | 515.9184 | 25 | 490.9184 | 28.9682 | 139.3858 | 0.77441 | 28.1938 | 89.27% | 297.0987 | 279.2727 | 6702.5459
1950 | 6 | 3 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1950 | 6 | 4 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1950 | 6 | 5 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1950 | 6 | 6 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1950 | 6 | 7 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1950 | 6 | 8 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1950 | 6 | 9 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1950 | 6 | 10 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1950 | 6 | 11 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1950 | 6 | 12 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1950 | 6 | 13 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1950 | 6 | 14 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1950 | 6 | 15 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1950 | 6 | 16 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1950 | 6 | 17 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1950 | 6 | 18 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1950 | 6 | 19 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1950 | 6 | 20 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1950 | 6 | 21 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1950 | 6 | 22 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1950 | 6 | 23 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1950 | 6 | 24 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1950 | 6 | 25 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1950 | 6 | 26 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1950 | 6 | 27 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1950 | 6 | 28 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1950 | 6 | 29 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1950 | 6 | 30 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1950 | 7 | 1 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1950 | 7 | 2 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1950 | 7 | 3 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1950 | 7 | 4 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1950 | 7 | 5 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1950 | 7 | 6 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1950 | 7 | 7 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1950 | 7 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1950 | 7 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1950 | 7 | 10 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1950 | 7 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1950 | 7 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1950 | 7 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1950 | 7 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1950 | 7 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1950 | 7 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1950 | 7 | 17 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1950 | 7 | 18 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1950 | 7 | 19 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1950 | 7 | 20 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1950 | 7 | 21 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1950 | 7 | 22 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1950 | 7 | 23 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1950 | 7 | 24 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1950 | 7 | 25 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1950 | 7 | 26 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1950 | 7 | 27 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1950 | 7 | 28 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1950 | 7 | 29 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1950 | 7 | 30 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1950 | 7 | 31 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1950 | 8 | 1 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1950 | 8 | 2 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1950 | 8 | 3 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1950 | 8 | 4 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1950 | 8 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1950 | 8 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1950 | 8 | 7 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1950 | 8 | 8 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1950 | 8 | 9 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1950 | 8 | 10 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1950 | 8 | 11 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1950 | 8 | 12 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1950 | 8 | 13 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1950 | 8 | 14 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1950 | 8 | 15 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1950 | 8 | 16 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1950 | 8 | 17 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1950 | 8 | 18 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1950 | 8 | 19 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1950 | 8 | 20 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1950 | 8 | 21 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1950 | 8 | 22 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1950 | 8 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1950 | 8 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1950 | 8 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1950 | 8 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1950 | 8 | 27 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1950 | 8 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1950 | 8 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1950 | 8 | 30 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1950 | 8 | 31 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1950 | 9 | 1 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1950 | 9 | 2 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1950 | 9 | 3 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1950 | 9 | 4 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1950 | 9 | 5 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1950 | 9 | 6 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1950 | 9 | 7 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1950 | 9 | 8 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1950 | 9 | 9 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1950 | 9 | 10 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1950 | 9 | 11 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1950 | 9 | 12 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1950 | 9 | 13 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1950 | 9 | 14 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1950 | 9 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1950 | 9 | 16 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1950 | 9 | 17 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1950 | 9 | 18 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1950 | 9 | 19 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1950 | 9 | 20 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1950 | 9 | 21 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1950 | 9 | 22 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1950 | 9 | 23 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1950 | 9 | 24 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1950 | 9 | 25 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1950 | 9 | 26 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1950 | 9 | 27 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1950 | 9 | 28 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1950 | 9 | 29 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1950 | 9 | 30 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1950 | 10 | 1 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1950 | 10 | 2 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1950 | 10 | 3 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1950 | 10 | 4 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1950 | 10 | 5 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1950 | 10 | 6 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1950 | 10 | 7 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1950 | 10 | 8 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1950 | 10 | 9 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1950 | 10 | 10 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1950 | 10 | 11 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1950 | 10 | 12 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1950 | 10 | 13 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1950 | 10 | 14 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1950 | 10 | 15 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1950 | 10 | 16 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1950 | 10 | 17 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1950 | 10 | 18 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1950 | 10 | 19 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1950 | 10 | 20 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1950 | 10 | 21 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1950 | 10 | 22 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1950 | 10 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1950 | 10 | 24 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1950 | 10 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1950 | 10 | 26 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1950 | 10 | 27 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1950 | 10 | 28 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1950 | 10 | 29 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1950 | 10 | 30 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1950 | 10 | 31 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1950 | 11 | 1 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1950 | 11 | 2 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1950 | 11 | 3 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1950 | 11 | 4 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1950 | 11 | 5 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1950 | 11 | 6 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1950 | 11 | 7 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1950 | 11 | 8 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1950 | 11 | 9 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1950 | 11 | 10 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1950 | 11 | 11 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1950 | 11 | 12 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1950 | 11 | 13 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1950 | 11 | 14 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1950 | 11 | 15 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1950 | 11 | 16 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1950 | 11 | 17 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1950 | 11 | 18 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1950 | 11 | 19 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1950 | 11 | 20 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1950 | 11 | 21 | 620.4082 | 15 | 605.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1950 | 11 | 22 | 666.1224 | 15 | 651.1224 | 28.6678 | 139.3858 | 0.77441 | 27.8933 | 89.27% | 293.933 | 276.2971 | 6631.1294
1950 | 11 | 23 | 317.3878 | 15 | 302.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1950 | 11 | 24 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1950 | 11 | 25 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1950 | 11 | 26 | 1854.6939 | 15 | 1839.6939 | 26.2906 | 139.3858 | 0.77441 | 25.5162 | 89.27% | 268.8833 | 252.7503 | 6066.0075
1950 | 11 | 27 | 2311.8367 | 15 | 2296.8367 | 25.3763 | 139.3858 | 0.77441 | 24.6019 | 89.27% | 259.2488 | 243.6939 | 5848.6529
1950 | 11 | 28 | 1123.2653 | 15 | 1108.2653 | 27.7535 | 139.3858 | 0.77441 | 26.9791 | 89.27% | 284.2985 | 267.2406 | 6413.7748
1950 | 11 | 29 | 939.102 | 15 | 924.102 | 28.1218 | 139.3858 | 0.77441 | 27.3474 | 89.27% | 288.1799 | 270.8891 | 6501.3377
1950 | 11 | 30 | 611.2653 | 15 | 596.2653 | 28.7775 | 139.3858 | 0.77441 | 28.0031 | 89.27% | 295.0892 | 277.3838 | 6657.212
1950 | 12 | 1 | 424.4898 | 5 | 419.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1950 | 12 | 2 | 327.8367 | 5 | 322.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1950 | 12 | 3 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1950 | 12 | 4 | 252.0816 | 5 | 247.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1950 | 12 | 5 | 573.3878 | 5 | 568.3878 | 28.8532 | 139.3858 | 0.77441 | 28.0788 | 89.27% | 295.8875 | 278.1342 | 6675.2214
1950 | 12 | 6 | 530.2857 | 5 | 525.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1950 | 12 | 7 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1950 | 12 | 8 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1950 | 12 | 9 | 1580.4082 | 5 | 1575.4082 | 26.8392 | 139.3858 | 0.77441 | 26.0648 | 89.27% | 274.664 | 258.1842 | 6196.4202
1950 | 12 | 10 | 1273.4694 | 5 | 1268.4694 | 27.4531 | 139.3858 | 0.77441 | 26.6787 | 89.27% | 281.1329 | 264.2649 | 6342.3583
1950 | 12 | 11 | 777.1429 | 5 | 772.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1950 | 12 | 12 | 654.3673 | 5 | 649.3673 | 28.6913 | 139.3858 | 0.77441 | 27.9169 | 89.27% | 294.1808 | 276.5299 | 6636.7186
1950 | 12 | 13 | 502.8571 | 5 | 497.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
1950 | 12 | 14 | 381.3878 | 5 | 376.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1950 | 12 | 15 | 310.8571 | 5 | 305.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1950 | 12 | 16 | 271.6735 | 5 | 266.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1950 | 12 | 17 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1950 | 12 | 18 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1950 | 12 | 19 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1950 | 12 | 20 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1950 | 12 | 21 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1950 | 12 | 22 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1950 | 12 | 23 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1950 | 12 | 24 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1950 | 12 | 25 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1950 | 12 | 26 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1950 | 12 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1950 | 12 | 28 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1950 | 12 | 29 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1950 | 12 | 30 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1950 | 12 | 31 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1951 | 1 | 1 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1951 | 1 | 2 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1951 | 1 | 3 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1951 | 1 | 4 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1951 | 1 | 5 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1951 | 1 | 6 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1951 | 1 | 7 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1951 | 1 | 8 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1951 | 1 | 9 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1951 | 1 | 10 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1951 | 1 | 11 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1951 | 1 | 12 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1951 | 1 | 13 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1951 | 1 | 14 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1951 | 1 | 15 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1951 | 1 | 16 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1951 | 1 | 17 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1951 | 1 | 18 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1951 | 1 | 19 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1951 | 1 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1951 | 1 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1951 | 1 | 22 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1951 | 1 | 23 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1951 | 1 | 24 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1951 | 1 | 25 | 344.8163 | 5 | 339.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1951 | 1 | 26 | 291.2653 | 5 | 286.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1951 | 1 | 27 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1951 | 1 | 28 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1951 | 1 | 29 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1951 | 1 | 30 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1951 | 1 | 31 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1951 | 2 | 1 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1951 | 2 | 2 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1951 | 2 | 3 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1951 | 2 | 4 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1951 | 2 | 5 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1951 | 2 | 6 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1951 | 2 | 7 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1951 | 2 | 8 | 1234.2857 | 5 | 1229.2857 | 27.5314 | 139.3858 | 0.77441 | 26.757 | 89.27% | 281.9587 | 265.0412 | 6360.9887
1951 | 2 | 9 | 848.9796 | 5 | 843.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1951 | 2 | 10 | 339.5918 | 5 | 334.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1951 | 2 | 11 | 214.2041 | 5 | 209.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1951 | 2 | 12 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1951 | 2 | 13 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1951 | 2 | 14 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1951 | 2 | 15 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1951 | 2 | 16 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1951 | 2 | 17 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1951 | 2 | 18 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1951 | 2 | 19 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1951 | 2 | 20 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1951 | 2 | 21 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1951 | 2 | 22 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1951 | 2 | 23 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1951 | 2 | 24 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1951 | 2 | 25 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1951 | 2 | 26 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1951 | 2 | 27 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1951 | 2 | 28 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1951 | 3 | 1 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1951 | 3 | 2 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1951 | 3 | 3 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1951 | 3 | 4 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1951 | 3 | 5 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1951 | 3 | 6 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1951 | 3 | 7 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1951 | 3 | 8 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1951 | 3 | 9 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1951 | 3 | 10 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1951 | 3 | 11 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1951 | 3 | 12 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1951 | 3 | 13 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1951 | 3 | 14 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1951 | 3 | 15 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1951 | 3 | 16 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1951 | 3 | 17 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1951 | 3 | 18 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1951 | 3 | 19 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1951 | 3 | 20 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1951 | 3 | 21 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1951 | 3 | 22 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1951 | 3 | 23 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1951 | 3 | 24 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1951 | 3 | 25 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1951 | 3 | 26 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1951 | 3 | 27 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1951 | 3 | 28 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1951 | 3 | 29 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1951 | 3 | 30 | 547.2653 | 25 | 522.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1951 | 3 | 31 | 1084.0816 | 25 | 1059.0816 | 27.8318 | 139.3858 | 0.77441 | 27.0574 | 89.27% | 285.1243 | 268.0169 | 6432.4052
1951 | 4 | 1 | 2024.4898 | 25 | 1999.4898 | 25.951 | 139.3858 | 0.77441 | 25.1766 | 89.27% | 265.3048 | 249.3865 | 5985.2758
1951 | 4 | 2 | 1528.1633 | 25 | 1503.1633 | 26.9437 | 139.3858 | 0.77441 | 26.1693 | 89.27% | 275.7651 | 259.2192 | 6221.2608
1951 | 4 | 3 | 2677.551 | 25 | 2652.551 | 24.6449 | 0 | 0 | 24.6449 | 0% | 0 | 0 | 0
1951 | 4 | 4 | 2991.0204 | 25 | 2966.0204 | 24.018 | 0 | 0 | 24.018 | 0% | 0 | 0 | 0
1951 | 4 | 5 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
1951 | 4 | 6 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1951 | 4 | 7 | 939.102 | 25 | 914.102 | 28.1218 | 139.3858 | 0.77441 | 27.3474 | 89.27% | 288.1799 | 270.8891 | 6501.3377
1951 | 4 | 8 | 901.2245 | 25 | 876.2245 | 28.1976 | 139.3858 | 0.77441 | 27.4231 | 89.27% | 288.9782 | 271.6395 | 6519.3471
1951 | 4 | 9 | 1221.2245 | 25 | 1196.2245 | 27.5576 | 139.3858 | 0.77441 | 26.7831 | 89.27% | 282.234 | 265.3 | 6367.1988
1951 | 4 | 10 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1951 | 4 | 11 | 1138.9388 | 25 | 1113.9388 | 27.7221 | 139.3858 | 0.77441 | 26.9477 | 89.27% | 283.9682 | 266.9301 | 6406.3227
1951 | 4 | 12 | 924.7347 | 25 | 899.7347 | 28.1505 | 139.3858 | 0.77441 | 27.3761 | 89.27% | 288.4827 | 271.1737 | 6508.1688
1951 | 4 | 13 | 896 | 25 | 871 | 28.208 | 139.3858 | 0.77441 | 27.4336 | 89.27% | 289.0883 | 271.743 | 6521.8311
1951 | 4 | 14 | 954.7755 | 25 | 929.7755 | 28.0904 | 139.3858 | 0.77441 | 27.316 | 89.27% | 287.8495 | 270.5786 | 6493.8855
1951 | 4 | 15 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1951 | 4 | 16 | 685.7143 | 25 | 660.7143 | 28.6286 | 139.3858 | 0.77441 | 27.8542 | 89.27% | 293.5201 | 275.9089 | 6621.8142
1951 | 4 | 17 | 547.2653 | 25 | 522.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1951 | 4 | 18 | 441.4694 | 25 | 416.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
1951 | 4 | 19 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1951 | 4 | 20 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1951 | 4 | 21 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1951 | 4 | 22 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1951 | 4 | 23 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1951 | 4 | 24 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1951 | 4 | 25 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1951 | 4 | 26 | 949.551 | 25 | 924.551 | 28.1009 | 139.3858 | 0.77441 | 27.3265 | 89.27% | 287.9596 | 270.6821 | 6496.3696
1951 | 4 | 27 | 777.1429 | 25 | 752.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1951 | 4 | 28 | 502.8571 | 25 | 477.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
1951 | 4 | 29 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1951 | 4 | 30 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1951 | 5 | 1 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1951 | 5 | 2 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1951 | 5 | 3 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1951 | 5 | 4 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1951 | 5 | 5 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1951 | 5 | 6 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1951 | 5 | 7 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1951 | 5 | 8 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1951 | 5 | 9 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1951 | 5 | 10 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1951 | 5 | 11 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1951 | 5 | 12 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1951 | 5 | 13 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1951 | 5 | 14 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1951 | 5 | 15 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1951 | 5 | 16 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1951 | 5 | 17 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1951 | 5 | 18 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1951 | 5 | 19 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1951 | 5 | 20 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1951 | 5 | 21 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1951 | 5 | 22 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1951 | 5 | 23 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1951 | 5 | 24 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1951 | 5 | 25 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1951 | 5 | 26 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1951 | 5 | 27 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1951 | 5 | 28 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1951 | 5 | 29 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1951 | 5 | 30 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1951 | 5 | 31 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1951 | 6 | 1 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1951 | 6 | 2 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1951 | 6 | 3 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1951 | 6 | 4 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1951 | 6 | 5 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1951 | 6 | 6 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1951 | 6 | 7 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1951 | 6 | 8 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1951 | 6 | 9 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1951 | 6 | 10 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1951 | 6 | 11 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1951 | 6 | 12 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1951 | 6 | 13 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1951 | 6 | 14 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1951 | 6 | 15 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1951 | 6 | 16 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1951 | 6 | 17 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1951 | 6 | 18 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1951 | 6 | 19 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1951 | 6 | 20 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1951 | 6 | 21 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1951 | 6 | 22 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1951 | 6 | 23 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1951 | 6 | 24 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1951 | 6 | 25 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1951 | 6 | 26 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1951 | 6 | 27 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1951 | 6 | 28 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1951 | 6 | 29 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1951 | 6 | 30 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1951 | 7 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1951 | 7 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1951 | 7 | 3 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1951 | 7 | 4 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1951 | 7 | 5 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1951 | 7 | 6 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1951 | 7 | 7 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1951 | 7 | 8 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1951 | 7 | 9 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1951 | 7 | 10 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1951 | 7 | 11 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1951 | 7 | 12 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1951 | 7 | 13 | 587.7551 | 5 | 582.7551 | 28.8245 | 139.3858 | 0.77441 | 28.0501 | 89.27% | 295.5847 | 277.8496 | 6668.3902
1951 | 7 | 14 | 263.8367 | 5 | 258.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1951 | 7 | 15 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1951 | 7 | 16 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1951 | 7 | 17 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1951 | 7 | 18 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1951 | 7 | 19 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1951 | 7 | 20 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1951 | 7 | 21 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1951 | 7 | 22 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1951 | 7 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1951 | 7 | 24 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1951 | 7 | 25 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1951 | 7 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1951 | 7 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1951 | 7 | 28 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1951 | 7 | 29 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1951 | 7 | 30 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1951 | 7 | 31 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1951 | 8 | 1 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1951 | 8 | 2 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1951 | 8 | 3 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1951 | 8 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1951 | 8 | 5 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1951 | 8 | 6 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1951 | 8 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1951 | 8 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1951 | 8 | 9 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1951 | 8 | 10 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1951 | 8 | 11 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1951 | 8 | 12 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1951 | 8 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1951 | 8 | 14 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1951 | 8 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1951 | 8 | 16 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1951 | 8 | 17 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1951 | 8 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1951 | 8 | 19 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1951 | 8 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1951 | 8 | 21 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1951 | 8 | 22 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1951 | 8 | 23 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1951 | 8 | 24 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1951 | 8 | 25 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1951 | 8 | 26 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1951 | 8 | 27 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1951 | 8 | 28 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1951 | 8 | 29 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1951 | 8 | 30 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1951 | 8 | 31 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1951 | 9 | 1 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1951 | 9 | 2 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1951 | 9 | 3 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1951 | 9 | 4 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1951 | 9 | 5 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1951 | 9 | 6 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1951 | 9 | 7 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1951 | 9 | 8 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1951 | 9 | 9 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1951 | 9 | 10 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1951 | 9 | 11 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1951 | 9 | 12 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1951 | 9 | 13 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1951 | 9 | 14 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1951 | 9 | 15 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1951 | 9 | 16 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1951 | 9 | 17 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1951 | 9 | 18 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1951 | 9 | 19 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1951 | 9 | 20 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1951 | 9 | 21 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1951 | 9 | 22 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1951 | 9 | 23 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1951 | 9 | 24 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1951 | 9 | 25 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1951 | 9 | 26 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1951 | 9 | 27 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1951 | 9 | 28 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1951 | 9 | 29 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1951 | 9 | 30 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1951 | 10 | 1 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1951 | 10 | 2 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1951 | 10 | 3 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1951 | 10 | 4 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1951 | 10 | 5 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1951 | 10 | 6 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1951 | 10 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1951 | 10 | 8 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1951 | 10 | 9 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1951 | 10 | 10 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1951 | 10 | 11 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1951 | 10 | 12 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1951 | 10 | 13 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1951 | 10 | 14 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1951 | 10 | 15 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1951 | 10 | 16 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1951 | 10 | 17 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1951 | 10 | 18 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1951 | 10 | 19 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1951 | 10 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1951 | 10 | 21 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1951 | 10 | 22 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1951 | 10 | 23 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1951 | 10 | 24 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1951 | 10 | 25 | 450.6122 | 15 | 435.6122 | 29.0988 | 139.3858 | 0.77441 | 28.3244 | 89.27% | 298.475 | 280.5665 | 6733.5966
1951 | 10 | 26 | 376.1633 | 15 | 361.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1951 | 10 | 27 | 216.8163 | 15 | 201.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1951 | 10 | 28 | 160.6531 | 15 | 145.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1951 | 10 | 29 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1951 | 10 | 30 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1951 | 10 | 31 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1951 | 11 | 1 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1951 | 11 | 2 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1951 | 11 | 3 | 1084.0816 | 15 | 1069.0816 | 27.8318 | 139.3858 | 0.77441 | 27.0574 | 89.27% | 285.1243 | 268.0169 | 6432.4052
1951 | 11 | 4 | 1946.1224 | 15 | 1931.1224 | 26.1078 | 139.3858 | 0.77441 | 25.3333 | 89.27% | 266.9564 | 250.939 | 6022.5365
1951 | 11 | 5 | 855.5102 | 15 | 840.5102 | 28.289 | 139.3858 | 0.77441 | 27.5146 | 89.27% | 289.9416 | 272.5451 | 6541.0825
1951 | 11 | 6 | 489.7959 | 15 | 474.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
1951 | 11 | 7 | 822.8571 | 15 | 807.8571 | 28.3543 | 139.3858 | 0.77441 | 27.5799 | 89.27% | 290.6298 | 273.192 | 6556.6079
1951 | 11 | 8 | 1697.9592 | 15 | 1682.9592 | 26.6041 | 139.3858 | 0.77441 | 25.8297 | 89.27% | 272.1866 | 255.8554 | 6140.529
1951 | 11 | 9 | 927.3469 | 15 | 912.3469 | 28.1453 | 139.3858 | 0.77441 | 27.3709 | 89.27% | 288.4276 | 271.122 | 6506.9268
1951 | 11 | 10 | 536.8163 | 15 | 521.8163 | 28.9264 | 139.3858 | 0.77441 | 28.152 | 89.27% | 296.6582 | 278.8587 | 6692.6097
1951 | 11 | 11 | 386.6122 | 15 | 371.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1951 | 11 | 12 | 327.8367 | 15 | 312.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1951 | 11 | 13 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1951 | 11 | 14 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1951 | 11 | 15 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1951 | 11 | 16 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1951 | 11 | 17 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1951 | 11 | 18 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1951 | 11 | 19 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1951 | 11 | 20 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1951 | 11 | 21 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1951 | 11 | 22 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1951 | 11 | 23 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1951 | 11 | 24 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1951 | 11 | 25 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1951 | 11 | 26 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1951 | 11 | 27 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1951 | 11 | 28 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1951 | 11 | 29 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1951 | 11 | 30 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1951 | 12 | 1 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1951 | 12 | 2 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1951 | 12 | 3 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1951 | 12 | 4 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1951 | 12 | 5 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1951 | 12 | 6 | 607.3469 | 5 | 602.3469 | 28.7853 | 139.3858 | 0.77441 | 28.0109 | 89.27% | 295.1718 | 277.4615 | 6659.075
1951 | 12 | 7 | 662.2041 | 5 | 657.2041 | 28.6756 | 139.3858 | 0.77441 | 27.9012 | 89.27% | 294.0156 | 276.3747 | 6632.9925
1951 | 12 | 8 | 415.3469 | 5 | 410.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1951 | 12 | 9 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1951 | 12 | 10 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1951 | 12 | 11 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1951 | 12 | 12 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1951 | 12 | 13 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1951 | 12 | 14 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1951 | 12 | 15 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1951 | 12 | 16 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1951 | 12 | 17 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1951 | 12 | 18 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1951 | 12 | 19 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1951 | 12 | 20 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1951 | 12 | 21 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1951 | 12 | 22 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1951 | 12 | 23 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1951 | 12 | 24 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1951 | 12 | 25 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1951 | 12 | 26 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1951 | 12 | 27 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1951 | 12 | 28 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1951 | 12 | 29 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1951 | 12 | 30 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1951 | 12 | 31 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1952 | 1 | 1 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1952 | 1 | 2 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1952 | 1 | 3 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1952 | 1 | 4 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1952 | 1 | 5 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1952 | 1 | 6 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1952 | 1 | 7 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1952 | 1 | 8 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1952 | 1 | 9 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1952 | 1 | 10 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1952 | 1 | 11 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1952 | 1 | 12 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1952 | 1 | 13 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1952 | 1 | 14 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1952 | 1 | 15 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1952 | 1 | 16 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1952 | 1 | 17 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1952 | 1 | 18 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1952 | 1 | 19 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1952 | 1 | 20 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1952 | 1 | 21 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1952 | 1 | 22 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1952 | 1 | 23 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1952 | 1 | 24 | 233.7959 | 5 | 228.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1952 | 1 | 25 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1952 | 1 | 26 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1952 | 1 | 27 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1952 | 1 | 28 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1952 | 1 | 29 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1952 | 1 | 30 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1952 | 1 | 31 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1952 | 2 | 1 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1952 | 2 | 2 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1952 | 2 | 3 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1952 | 2 | 4 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1952 | 2 | 5 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1952 | 2 | 6 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1952 | 2 | 7 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1952 | 2 | 8 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1952 | 2 | 9 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1952 | 2 | 10 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1952 | 2 | 11 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1952 | 2 | 12 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1952 | 2 | 13 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1952 | 2 | 14 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1952 | 2 | 15 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1952 | 2 | 16 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1952 | 2 | 17 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1952 | 2 | 18 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1952 | 2 | 19 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1952 | 2 | 20 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1952 | 2 | 21 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1952 | 2 | 22 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1952 | 2 | 23 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1952 | 2 | 24 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1952 | 2 | 25 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1952 | 2 | 26 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1952 | 2 | 27 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1952 | 2 | 28 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1952 | 2 | 29 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1952 | 3 | 1 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1952 | 3 | 2 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1952 | 3 | 3 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1952 | 3 | 4 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1952 | 3 | 5 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1952 | 3 | 6 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1952 | 3 | 7 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1952 | 3 | 8 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1952 | 3 | 9 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1952 | 3 | 10 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1952 | 3 | 11 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1952 | 3 | 12 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1952 | 3 | 13 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1952 | 3 | 14 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1952 | 3 | 15 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1952 | 3 | 16 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1952 | 3 | 17 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1952 | 3 | 18 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1952 | 3 | 19 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1952 | 3 | 20 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1952 | 3 | 21 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1952 | 3 | 22 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1952 | 3 | 23 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1952 | 3 | 24 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1952 | 3 | 25 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1952 | 3 | 26 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1952 | 3 | 27 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1952 | 3 | 28 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1952 | 3 | 29 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1952 | 3 | 30 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1952 | 3 | 31 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1952 | 4 | 1 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1952 | 4 | 2 | 565.551 | 25 | 540.551 | 28.8689 | 139.3858 | 0.77441 | 28.0945 | 89.27% | 296.0526 | 278.2895 | 6678.9474
1952 | 4 | 3 | 681.7959 | 25 | 656.7959 | 28.6364 | 139.3858 | 0.77441 | 27.862 | 89.27% | 293.6027 | 275.9866 | 6623.6773
1952 | 4 | 4 | 583.8367 | 25 | 558.8367 | 28.8323 | 139.3858 | 0.77441 | 28.0579 | 89.27% | 295.6673 | 277.9272 | 6670.2533
1952 | 4 | 5 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1952 | 4 | 6 | 1828.5714 | 25 | 1803.5714 | 26.3429 | 139.3858 | 0.77441 | 25.5684 | 89.27% | 269.4339 | 253.2678 | 6078.4277
1952 | 4 | 7 | 1645.7143 | 25 | 1620.7143 | 26.7086 | 139.3858 | 0.77441 | 25.9342 | 89.27% | 273.2877 | 256.8904 | 6165.3696
1952 | 4 | 8 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1952 | 4 | 9 | 1280 | 25 | 1255 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
1952 | 4 | 10 | 1201.6327 | 25 | 1176.6327 | 27.5967 | 139.3858 | 0.77441 | 26.8223 | 89.27% | 282.6469 | 265.6881 | 6376.514
1952 | 4 | 11 | 1462.8571 | 25 | 1437.8571 | 27.0743 | 139.3858 | 0.77441 | 26.2999 | 89.27% | 277.1415 | 260.513 | 6252.3114
1952 | 4 | 12 | 1192.4898 | 25 | 1167.4898 | 27.615 | 139.3858 | 0.77441 | 26.8406 | 89.27% | 282.8396 | 265.8692 | 6380.8611
1952 | 4 | 13 | 969.1429 | 25 | 944.1429 | 28.0617 | 139.3858 | 0.77441 | 27.2873 | 89.27% | 287.5467 | 270.2939 | 6487.0544
1952 | 4 | 14 | 1047.5102 | 25 | 1022.5102 | 27.905 | 139.3858 | 0.77441 | 27.1306 | 89.27% | 285.8951 | 268.7414 | 6449.7936
1952 | 4 | 15 | 1180.7347 | 25 | 1155.7347 | 27.6385 | 139.3858 | 0.77441 | 26.8641 | 89.27% | 283.0873 | 266.1021 | 6386.4503
1952 | 4 | 16 | 1199.0204 | 25 | 1174.0204 | 27.602 | 139.3858 | 0.77441 | 26.8275 | 89.27% | 282.702 | 265.7398 | 6377.7561
1952 | 4 | 17 | 1168.9796 | 25 | 1143.9796 | 27.662 | 139.3858 | 0.77441 | 26.8876 | 89.27% | 283.3351 | 266.335 | 6392.0394
1952 | 4 | 18 | 1110.2041 | 25 | 1085.2041 | 27.7796 | 139.3858 | 0.77441 | 27.0052 | 89.27% | 284.5738 | 267.4994 | 6419.985
1952 | 4 | 19 | 1128.4898 | 25 | 1103.4898 | 27.743 | 139.3858 | 0.77441 | 26.9686 | 89.27% | 284.1884 | 267.1371 | 6411.2908
1952 | 4 | 20 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1952 | 4 | 21 | 1247.3469 | 25 | 1222.3469 | 27.5053 | 139.3858 | 0.77441 | 26.7309 | 89.27% | 281.6834 | 264.7824 | 6354.7786
1952 | 4 | 22 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1952 | 4 | 23 | 717.0612 | 25 | 692.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1952 | 4 | 24 | 629.551 | 25 | 604.551 | 28.7409 | 139.3858 | 0.77441 | 27.9665 | 89.27% | 294.7038 | 277.0216 | 6648.5178
1952 | 4 | 25 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1952 | 4 | 26 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1952 | 4 | 27 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1952 | 4 | 28 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1952 | 4 | 29 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1952 | 4 | 30 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1952 | 5 | 1 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1952 | 5 | 2 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1952 | 5 | 3 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1952 | 5 | 4 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1952 | 5 | 5 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1952 | 5 | 6 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1952 | 5 | 7 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1952 | 5 | 8 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1952 | 5 | 9 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1952 | 5 | 10 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1952 | 5 | 11 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1952 | 5 | 12 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1952 | 5 | 13 | 1227.7551 | 25 | 1202.7551 | 27.5445 | 139.3858 | 0.77441 | 26.7701 | 89.27% | 282.0964 | 265.1706 | 6364.0938
1952 | 5 | 14 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1952 | 5 | 15 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1952 | 5 | 16 | 548.5714 | 25 | 523.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
1952 | 5 | 17 | 548.5714 | 25 | 523.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
1952 | 5 | 18 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1952 | 5 | 19 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1952 | 5 | 20 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1952 | 5 | 21 | 515.9184 | 25 | 490.9184 | 28.9682 | 139.3858 | 0.77441 | 28.1938 | 89.27% | 297.0987 | 279.2727 | 6702.5459
1952 | 5 | 22 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1952 | 5 | 23 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1952 | 5 | 24 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1952 | 5 | 25 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1952 | 5 | 26 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1952 | 5 | 27 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1952 | 5 | 28 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1952 | 5 | 29 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1952 | 5 | 30 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1952 | 5 | 31 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1952 | 6 | 1 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1952 | 6 | 2 | 2207.3469 | 25 | 2182.3469 | 25.5853 | 139.3858 | 0.77441 | 24.8109 | 89.27% | 261.451 | 245.7639 | 5898.3339
1952 | 6 | 3 | 1044.898 | 25 | 1019.898 | 27.9102 | 139.3858 | 0.77441 | 27.1358 | 89.27% | 285.9502 | 268.7932 | 6451.0356
1952 | 6 | 4 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1952 | 6 | 5 | 440.1633 | 25 | 415.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
1952 | 6 | 6 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1952 | 6 | 7 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1952 | 6 | 8 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1952 | 6 | 9 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1952 | 6 | 10 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1952 | 6 | 11 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1952 | 6 | 12 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1952 | 6 | 13 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1952 | 6 | 14 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1952 | 6 | 15 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1952 | 6 | 16 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1952 | 6 | 17 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1952 | 6 | 18 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1952 | 6 | 19 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1952 | 6 | 20 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1952 | 6 | 21 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1952 | 6 | 22 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1952 | 6 | 23 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1952 | 6 | 24 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1952 | 6 | 25 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1952 | 6 | 26 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1952 | 6 | 27 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1952 | 6 | 28 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1952 | 6 | 29 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1952 | 6 | 30 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1952 | 7 | 1 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1952 | 7 | 2 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1952 | 7 | 3 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1952 | 7 | 4 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1952 | 7 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1952 | 7 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1952 | 7 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1952 | 7 | 8 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1952 | 7 | 9 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1952 | 7 | 10 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1952 | 7 | 11 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1952 | 7 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1952 | 7 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1952 | 7 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1952 | 7 | 15 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1952 | 7 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1952 | 7 | 17 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1952 | 7 | 18 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1952 | 7 | 19 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1952 | 7 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1952 | 7 | 21 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1952 | 7 | 22 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1952 | 7 | 23 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 7 | 24 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 7 | 25 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1952 | 7 | 26 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 7 | 27 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 7 | 28 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 7 | 29 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 7 | 30 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1952 | 7 | 31 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1952 | 8 | 1 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1952 | 8 | 2 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1952 | 8 | 3 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1952 | 8 | 4 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1952 | 8 | 5 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1952 | 8 | 6 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1952 | 8 | 7 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1952 | 8 | 8 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1952 | 8 | 9 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1952 | 8 | 10 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1952 | 8 | 11 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1952 | 8 | 12 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1952 | 8 | 13 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1952 | 8 | 14 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1952 | 8 | 15 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1952 | 8 | 16 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1952 | 8 | 17 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 8 | 18 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 8 | 19 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1952 | 8 | 20 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1952 | 8 | 21 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1952 | 8 | 22 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1952 | 8 | 23 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1952 | 8 | 24 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1952 | 8 | 25 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1952 | 8 | 26 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1952 | 8 | 27 | 4.049 | 5 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
1952 | 8 | 28 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1952 | 8 | 29 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1952 | 8 | 30 | 3.0041 | 5 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1952 | 8 | 31 | 2.6122 | 5 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1952 | 9 | 1 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1952 | 9 | 2 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1952 | 9 | 3 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1952 | 9 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1952 | 9 | 5 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1952 | 9 | 6 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1952 | 9 | 7 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1952 | 9 | 8 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1952 | 9 | 9 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1952 | 9 | 10 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1952 | 9 | 11 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1952 | 9 | 12 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1952 | 9 | 13 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1952 | 9 | 14 | 4.702 | 15 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1952 | 9 | 15 | 4.702 | 15 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1952 | 9 | 16 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1952 | 9 | 17 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1952 | 9 | 18 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1952 | 9 | 19 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1952 | 9 | 20 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1952 | 9 | 21 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1952 | 9 | 22 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1952 | 9 | 23 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1952 | 9 | 24 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1952 | 9 | 25 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1952 | 9 | 26 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1952 | 9 | 27 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1952 | 9 | 28 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1952 | 9 | 29 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1952 | 9 | 30 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1952 | 10 | 1 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1952 | 10 | 2 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1952 | 10 | 3 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1952 | 10 | 4 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1952 | 10 | 5 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1952 | 10 | 6 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1952 | 10 | 7 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1952 | 10 | 8 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1952 | 10 | 9 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1952 | 10 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1952 | 10 | 11 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1952 | 10 | 12 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1952 | 10 | 13 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1952 | 10 | 14 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1952 | 10 | 15 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1952 | 10 | 16 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 10 | 17 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 10 | 18 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1952 | 10 | 19 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1952 | 10 | 20 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1952 | 10 | 21 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1952 | 10 | 22 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1952 | 10 | 23 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1952 | 10 | 24 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1952 | 10 | 25 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1952 | 10 | 26 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1952 | 10 | 27 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1952 | 10 | 28 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 10 | 29 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1952 | 10 | 30 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1952 | 10 | 31 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1952 | 11 | 1 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1952 | 11 | 2 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1952 | 11 | 3 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 11 | 4 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1952 | 11 | 5 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1952 | 11 | 6 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1952 | 11 | 7 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 11 | 8 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1952 | 11 | 9 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1952 | 11 | 10 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 11 | 11 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1952 | 11 | 12 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1952 | 11 | 13 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1952 | 11 | 14 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1952 | 11 | 15 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1952 | 11 | 16 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1952 | 11 | 17 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1952 | 11 | 18 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1952 | 11 | 19 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1952 | 11 | 20 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1952 | 11 | 21 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1952 | 11 | 22 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1952 | 11 | 23 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1952 | 11 | 24 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1952 | 11 | 25 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1952 | 11 | 26 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1952 | 11 | 27 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1952 | 11 | 28 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1952 | 11 | 29 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1952 | 11 | 30 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1952 | 12 | 1 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1952 | 12 | 2 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1952 | 12 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1952 | 12 | 4 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1952 | 12 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1952 | 12 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1952 | 12 | 7 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1952 | 12 | 8 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1952 | 12 | 9 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1952 | 12 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1952 | 12 | 11 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1952 | 12 | 12 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1952 | 12 | 13 | 862.0408 | 5 | 857.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
1952 | 12 | 14 | 513.3061 | 5 | 508.3061 | 28.9734 | 139.3858 | 0.77441 | 28.199 | 89.27% | 297.1537 | 279.3245 | 6703.788
1952 | 12 | 15 | 259.9184 | 5 | 254.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1952 | 12 | 16 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1952 | 12 | 17 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1952 | 12 | 18 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1952 | 12 | 19 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1952 | 12 | 20 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1952 | 12 | 21 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1952 | 12 | 22 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1952 | 12 | 23 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1952 | 12 | 24 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1952 | 12 | 25 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1952 | 12 | 26 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1952 | 12 | 27 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1952 | 12 | 28 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1952 | 12 | 29 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1952 | 12 | 30 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1952 | 12 | 31 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1953 | 1 | 1 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1953 | 1 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1953 | 1 | 3 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1953 | 1 | 4 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1953 | 1 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1953 | 1 | 6 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1953 | 1 | 7 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1953 | 1 | 8 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1953 | 1 | 9 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1953 | 1 | 10 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1953 | 1 | 11 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1953 | 1 | 12 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1953 | 1 | 13 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1953 | 1 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1953 | 1 | 15 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1953 | 1 | 16 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1953 | 1 | 17 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1953 | 1 | 18 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1953 | 1 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1953 | 1 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1953 | 1 | 21 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1953 | 1 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1953 | 1 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1953 | 1 | 24 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1953 | 1 | 25 | 646.5306 | 5 | 641.5306 | 28.7069 | 139.3858 | 0.77441 | 27.9325 | 89.27% | 294.346 | 276.6852 | 6640.4446
1953 | 1 | 26 | 535.5102 | 5 | 530.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1953 | 1 | 27 | 295.1837 | 5 | 290.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1953 | 1 | 28 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1953 | 1 | 29 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1953 | 1 | 30 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1953 | 1 | 31 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1953 | 2 | 1 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1953 | 2 | 2 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1953 | 2 | 3 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1953 | 2 | 4 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1953 | 2 | 5 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1953 | 2 | 6 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1953 | 2 | 7 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1953 | 2 | 8 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1953 | 2 | 9 | 286.0408 | 5 | 281.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1953 | 2 | 10 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1953 | 2 | 11 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1953 | 2 | 12 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1953 | 2 | 13 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1953 | 2 | 14 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1953 | 2 | 15 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1953 | 2 | 16 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1953 | 2 | 17 | 303.0204 | 5 | 298.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1953 | 2 | 18 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1953 | 2 | 19 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1953 | 2 | 20 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1953 | 2 | 21 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1953 | 2 | 22 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1953 | 2 | 23 | 286.0408 | 5 | 281.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1953 | 2 | 24 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1953 | 2 | 25 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1953 | 2 | 26 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1953 | 2 | 27 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1953 | 2 | 28 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1953 | 3 | 1 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1953 | 3 | 2 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1953 | 3 | 3 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1953 | 3 | 4 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1953 | 3 | 5 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1953 | 3 | 6 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1953 | 3 | 7 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1953 | 3 | 8 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1953 | 3 | 9 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1953 | 3 | 10 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1953 | 3 | 11 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1953 | 3 | 12 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1953 | 3 | 13 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1953 | 3 | 14 | 683.102 | 25 | 658.102 | 28.6338 | 139.3858 | 0.77441 | 27.8594 | 89.27% | 293.5752 | 275.9607 | 6623.0563
1953 | 3 | 15 | 609.9592 | 25 | 584.9592 | 28.7801 | 139.3858 | 0.77441 | 28.0057 | 89.27% | 295.1167 | 277.4097 | 6657.833
1953 | 3 | 16 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1953 | 3 | 17 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1953 | 3 | 18 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1953 | 3 | 19 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1953 | 3 | 20 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1953 | 3 | 21 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1953 | 3 | 22 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1953 | 3 | 23 | 449.3061 | 25 | 424.3061 | 29.1014 | 139.3858 | 0.77441 | 28.327 | 89.27% | 298.5026 | 280.5924 | 6734.2176
1953 | 3 | 24 | 1084.0816 | 25 | 1059.0816 | 27.8318 | 139.3858 | 0.77441 | 27.0574 | 89.27% | 285.1243 | 268.0169 | 6432.4052
1953 | 3 | 25 | 3866.1224 | 25 | 3841.1224 | 22.2678 | 0 | 0 | 22.2678 | 0% | 0 | 0 | 0
1953 | 3 | 26 | 3918.3673 | 25 | 3893.3673 | 22.1633 | 0 | 0 | 22.1633 | 0% | 0 | 0 | 0
1953 | 3 | 27 | 8124.0816 | 25 | 8099.0816 | 13.7518 | 0 | 0 | 13.7518 | 0% | 0 | 0 | 0
1953 | 3 | 28 | 2951.8367 | 25 | 2926.8367 | 24.0963 | 0 | 0 | 24.0963 | 0% | 0 | 0 | 0
1953 | 3 | 29 | 1515.102 | 25 | 1490.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
1953 | 3 | 30 | 2390.2041 | 25 | 2365.2041 | 25.2196 | 139.3858 | 0.77441 | 24.4452 | 89.27% | 257.5972 | 242.1413 | 5811.3921
1953 | 3 | 31 | 2455.5102 | 25 | 2430.5102 | 25.089 | 139.3858 | 0.77441 | 24.3146 | 89.27% | 256.2208 | 240.8476 | 5780.3414
1953 | 4 | 1 | 1410.6122 | 25 | 1385.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1953 | 4 | 2 | 991.3469 | 25 | 966.3469 | 28.0173 | 139.3858 | 0.77441 | 27.2429 | 89.27% | 287.0788 | 269.854 | 6476.4972
1953 | 4 | 3 | 786.2857 | 25 | 761.2857 | 28.4274 | 139.3858 | 0.77441 | 27.653 | 89.27% | 291.4005 | 273.9165 | 6573.9962
1953 | 4 | 4 | 649.1429 | 25 | 624.1429 | 28.7017 | 139.3858 | 0.77441 | 27.9273 | 89.27% | 294.2909 | 276.6334 | 6639.2026
1953 | 4 | 5 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1953 | 4 | 6 | 508.0816 | 25 | 483.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
1953 | 4 | 7 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1953 | 4 | 8 | 407.5102 | 25 | 382.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1953 | 4 | 9 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1953 | 4 | 10 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1953 | 4 | 11 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1953 | 4 | 12 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1953 | 4 | 13 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1953 | 4 | 14 | 796.7347 | 25 | 771.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1953 | 4 | 15 | 653.0612 | 25 | 628.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
1953 | 4 | 16 | 501.551 | 25 | 476.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
1953 | 4 | 17 | 999.1837 | 25 | 974.1837 | 28.0016 | 139.3858 | 0.77441 | 27.2272 | 89.27% | 286.9136 | 269.6988 | 6472.7711
1953 | 4 | 18 | 939.102 | 25 | 914.102 | 28.1218 | 139.3858 | 0.77441 | 27.3474 | 89.27% | 288.1799 | 270.8891 | 6501.3377
1953 | 4 | 19 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
1953 | 4 | 20 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
1953 | 4 | 21 | 640 | 25 | 615 | 28.72 | 139.3858 | 0.77441 | 27.9456 | 89.27% | 294.4836 | 276.8146 | 6643.5497
1953 | 4 | 22 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1953 | 4 | 23 | 425.7959 | 25 | 400.7959 | 29.1484 | 139.3858 | 0.77441 | 28.374 | 89.27% | 298.998 | 281.0582 | 6745.3959
1953 | 4 | 24 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1953 | 4 | 25 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1953 | 4 | 26 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1953 | 4 | 27 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1953 | 4 | 28 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
1953 | 4 | 29 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1953 | 4 | 30 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1953 | 5 | 1 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1953 | 5 | 2 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
1953 | 5 | 3 | 539.4286 | 25 | 514.4286 | 28.9211 | 139.3858 | 0.77441 | 28.1467 | 89.27% | 296.6032 | 278.807 | 6691.3677
1953 | 5 | 4 | 428.4082 | 25 | 403.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
1953 | 5 | 5 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1953 | 5 | 6 | 275.5918 | 25 | 250.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1953 | 5 | 7 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1953 | 5 | 8 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1953 | 5 | 9 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1953 | 5 | 10 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1953 | 5 | 11 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1953 | 5 | 12 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1953 | 5 | 13 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1953 | 5 | 14 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1953 | 5 | 15 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1953 | 5 | 16 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1953 | 5 | 17 | 394.449 | 25 | 369.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1953 | 5 | 18 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
1953 | 5 | 19 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1953 | 5 | 20 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1953 | 5 | 21 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1953 | 5 | 22 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1953 | 5 | 23 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1953 | 5 | 24 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1953 | 5 | 25 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1953 | 5 | 26 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1953 | 5 | 27 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1953 | 5 | 28 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1953 | 5 | 29 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1953 | 5 | 30 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1953 | 5 | 31 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1953 | 6 | 1 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1953 | 6 | 2 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1953 | 6 | 3 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1953 | 6 | 4 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1953 | 6 | 5 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1953 | 6 | 6 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1953 | 6 | 7 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1953 | 6 | 8 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1953 | 6 | 9 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1953 | 6 | 10 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1953 | 6 | 11 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1953 | 6 | 12 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1953 | 6 | 13 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1953 | 6 | 14 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1953 | 6 | 15 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1953 | 6 | 16 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1953 | 6 | 17 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1953 | 6 | 18 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1953 | 6 | 19 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1953 | 6 | 20 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1953 | 6 | 21 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1953 | 6 | 22 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1953 | 6 | 23 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1953 | 6 | 24 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1953 | 6 | 25 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1953 | 6 | 26 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1953 | 6 | 27 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1953 | 6 | 28 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1953 | 6 | 29 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1953 | 6 | 30 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1953 | 7 | 1 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1953 | 7 | 2 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 7 | 3 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 7 | 4 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1953 | 7 | 5 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1953 | 7 | 6 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1953 | 7 | 7 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1953 | 7 | 8 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1953 | 7 | 9 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1953 | 7 | 10 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1953 | 7 | 11 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1953 | 7 | 12 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1953 | 7 | 13 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1953 | 7 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1953 | 7 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1953 | 7 | 16 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 7 | 17 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1953 | 7 | 18 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
1953 | 7 | 19 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1953 | 7 | 20 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1953 | 7 | 21 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1953 | 7 | 22 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1953 | 7 | 23 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1953 | 7 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1953 | 7 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1953 | 7 | 26 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1953 | 7 | 27 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1953 | 7 | 28 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1953 | 7 | 29 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1953 | 7 | 30 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1953 | 7 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1953 | 8 | 1 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1953 | 8 | 2 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 8 | 3 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 8 | 4 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1953 | 8 | 5 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1953 | 8 | 6 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1953 | 8 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1953 | 8 | 8 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1953 | 8 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1953 | 8 | 10 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1953 | 8 | 11 | 373.551 | 5 | 368.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1953 | 8 | 12 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1953 | 8 | 13 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1953 | 8 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1953 | 8 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1953 | 8 | 16 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1953 | 8 | 17 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1953 | 8 | 18 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1953 | 8 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1953 | 8 | 20 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1953 | 8 | 21 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1953 | 8 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1953 | 8 | 23 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1953 | 8 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1953 | 8 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1953 | 8 | 26 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1953 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 8 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1953 | 8 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1953 | 8 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1953 | 8 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1953 | 9 | 1 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1953 | 9 | 2 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1953 | 9 | 3 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1953 | 9 | 4 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1953 | 9 | 5 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1953 | 9 | 6 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1953 | 9 | 7 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1953 | 9 | 8 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1953 | 9 | 9 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1953 | 9 | 10 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1953 | 9 | 11 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1953 | 9 | 12 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1953 | 9 | 13 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1953 | 9 | 14 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1953 | 9 | 15 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1953 | 9 | 16 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1953 | 9 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1953 | 9 | 18 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1953 | 9 | 19 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1953 | 9 | 20 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1953 | 9 | 21 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1953 | 9 | 22 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1953 | 9 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1953 | 9 | 24 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1953 | 9 | 25 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1953 | 9 | 26 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1953 | 9 | 27 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 9 | 28 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1953 | 9 | 29 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1953 | 9 | 30 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1953 | 10 | 1 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1953 | 10 | 2 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1953 | 10 | 3 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1953 | 10 | 4 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1953 | 10 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1953 | 10 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1953 | 10 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1953 | 10 | 8 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1953 | 10 | 9 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1953 | 10 | 10 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1953 | 10 | 11 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1953 | 10 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1953 | 10 | 13 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1953 | 10 | 14 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1953 | 10 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1953 | 10 | 16 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1953 | 10 | 17 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1953 | 10 | 18 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1953 | 10 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 20 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 21 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 22 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 23 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 24 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 25 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1953 | 10 | 26 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1953 | 10 | 27 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1953 | 10 | 28 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1953 | 10 | 29 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1953 | 10 | 30 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1953 | 10 | 31 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1953 | 11 | 1 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1953 | 11 | 2 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1953 | 11 | 3 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1953 | 11 | 4 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1953 | 11 | 5 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1953 | 11 | 6 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1953 | 11 | 7 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1953 | 11 | 8 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1953 | 11 | 9 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1953 | 11 | 10 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1953 | 11 | 11 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1953 | 11 | 12 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1953 | 11 | 13 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1953 | 11 | 14 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1953 | 11 | 15 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1953 | 11 | 16 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1953 | 11 | 17 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1953 | 11 | 18 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1953 | 11 | 19 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1953 | 11 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1953 | 11 | 21 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1953 | 11 | 22 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1953 | 11 | 23 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1953 | 11 | 24 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1953 | 11 | 25 | 253.3878 | 15 | 238.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1953 | 11 | 26 | 848.9796 | 15 | 833.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1953 | 11 | 27 | 544.6531 | 15 | 529.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
1953 | 11 | 28 | 352.6531 | 15 | 337.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1953 | 11 | 29 | 266.449 | 15 | 251.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1953 | 11 | 30 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1953 | 12 | 1 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1953 | 12 | 2 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1953 | 12 | 3 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1953 | 12 | 4 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1953 | 12 | 5 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1953 | 12 | 6 | 286.0408 | 5 | 281.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1953 | 12 | 7 | 946.9388 | 5 | 941.9388 | 28.1061 | 139.3858 | 0.77441 | 27.3317 | 89.27% | 288.0147 | 270.7338 | 6497.6116
1953 | 12 | 8 | 720.9796 | 5 | 715.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1953 | 12 | 9 | 472.8163 | 5 | 467.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1953 | 12 | 10 | 466.2857 | 5 | 461.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
1953 | 12 | 11 | 419.2653 | 5 | 414.2653 | 29.1615 | 139.3858 | 0.77441 | 28.3871 | 89.27% | 299.1357 | 281.1875 | 6748.5009
1953 | 12 | 12 | 327.8367 | 5 | 322.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1953 | 12 | 13 | 280.8163 | 5 | 275.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1953 | 12 | 14 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1953 | 12 | 15 | 278.2041 | 5 | 273.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1953 | 12 | 16 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1953 | 12 | 17 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1953 | 12 | 18 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1953 | 12 | 19 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1953 | 12 | 20 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1953 | 12 | 21 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1953 | 12 | 22 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1953 | 12 | 23 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1953 | 12 | 24 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1953 | 12 | 25 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1953 | 12 | 26 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1953 | 12 | 27 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1953 | 12 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1953 | 12 | 29 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1953 | 12 | 30 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1953 | 12 | 31 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1954 | 1 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1954 | 1 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1954 | 1 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1954 | 1 | 4 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1954 | 1 | 5 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1954 | 1 | 6 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1954 | 1 | 7 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1954 | 1 | 8 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1954 | 1 | 9 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1954 | 1 | 10 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1954 | 1 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1954 | 1 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1954 | 1 | 13 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1954 | 1 | 14 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1954 | 1 | 15 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1954 | 1 | 16 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1954 | 1 | 17 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1954 | 1 | 18 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1954 | 1 | 19 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1954 | 1 | 20 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 1 | 21 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1954 | 1 | 22 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1954 | 1 | 23 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1954 | 1 | 24 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 1 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 1 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1954 | 1 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1954 | 1 | 28 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1954 | 1 | 29 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1954 | 1 | 30 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1954 | 1 | 31 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1954 | 2 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1954 | 2 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1954 | 2 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1954 | 2 | 4 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1954 | 2 | 5 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1954 | 2 | 6 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1954 | 2 | 7 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1954 | 2 | 8 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1954 | 2 | 9 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1954 | 2 | 10 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1954 | 2 | 11 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1954 | 2 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1954 | 2 | 13 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 2 | 14 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1954 | 2 | 15 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 2 | 16 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1954 | 2 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1954 | 2 | 18 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1954 | 2 | 19 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1954 | 2 | 20 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1954 | 2 | 21 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1954 | 2 | 22 | 381.3878 | 5 | 376.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1954 | 2 | 23 | 731.4286 | 5 | 726.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1954 | 2 | 24 | 585.1429 | 5 | 580.1429 | 28.8297 | 139.3858 | 0.77441 | 28.0553 | 89.27% | 295.6397 | 277.9013 | 6669.6323
1954 | 2 | 25 | 431.0204 | 5 | 426.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1954 | 2 | 26 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1954 | 2 | 27 | 343.5102 | 5 | 338.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1954 | 2 | 28 | 374.8571 | 5 | 369.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1954 | 3 | 1 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1954 | 3 | 2 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1954 | 3 | 3 | 525.0612 | 25 | 500.0612 | 28.9499 | 139.3858 | 0.77441 | 28.1755 | 89.27% | 296.906 | 279.0916 | 6698.1989
1954 | 3 | 4 | 1013.551 | 25 | 988.551 | 27.9729 | 139.3858 | 0.77441 | 27.1985 | 89.27% | 286.6108 | 269.4142 | 6465.9399
1954 | 3 | 5 | 773.2245 | 25 | 748.2245 | 28.4536 | 139.3858 | 0.77441 | 27.6791 | 89.27% | 291.6758 | 274.1753 | 6580.2064
1954 | 3 | 6 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1954 | 3 | 7 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1954 | 3 | 8 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1954 | 3 | 9 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1954 | 3 | 10 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1954 | 3 | 11 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1954 | 3 | 12 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1954 | 3 | 13 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1954 | 3 | 14 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1954 | 3 | 15 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1954 | 3 | 16 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1954 | 3 | 17 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1954 | 3 | 18 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1954 | 3 | 19 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1954 | 3 | 20 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1954 | 3 | 21 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1954 | 3 | 22 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1954 | 3 | 23 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1954 | 3 | 24 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1954 | 3 | 25 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1954 | 3 | 26 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1954 | 3 | 27 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1954 | 3 | 28 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1954 | 3 | 29 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1954 | 3 | 30 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1954 | 3 | 31 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1954 | 4 | 1 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1954 | 4 | 2 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1954 | 4 | 3 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1954 | 4 | 4 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1954 | 4 | 5 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1954 | 4 | 6 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1954 | 4 | 7 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1954 | 4 | 8 | 800.6531 | 25 | 775.6531 | 28.3987 | 139.3858 | 0.77441 | 27.6243 | 89.27% | 291.0977 | 273.6319 | 6567.1651
1954 | 4 | 9 | 809.7959 | 25 | 784.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
1954 | 4 | 10 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1954 | 4 | 11 | 709.2245 | 25 | 684.2245 | 28.5816 | 139.3858 | 0.77441 | 27.8071 | 89.27% | 293.0246 | 275.4432 | 6610.636
1954 | 4 | 12 | 764.0816 | 25 | 739.0816 | 28.4718 | 139.3858 | 0.77441 | 27.6974 | 89.27% | 291.8685 | 274.3564 | 6584.5534
1954 | 4 | 13 | 786.2857 | 25 | 761.2857 | 28.4274 | 139.3858 | 0.77441 | 27.653 | 89.27% | 291.4005 | 273.9165 | 6573.9962
1954 | 4 | 14 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1954 | 4 | 15 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1954 | 4 | 16 | 709.2245 | 25 | 684.2245 | 28.5816 | 139.3858 | 0.77441 | 27.8071 | 89.27% | 293.0246 | 275.4432 | 6610.636
1954 | 4 | 17 | 1266.9388 | 25 | 1241.9388 | 27.4661 | 139.3858 | 0.77441 | 26.6917 | 89.27% | 281.2705 | 264.3943 | 6345.4634
1954 | 4 | 18 | 3030.2041 | 25 | 3005.2041 | 23.9396 | 0 | 0 | 23.9396 | 0% | 0 | 0 | 0
1954 | 4 | 19 | 2024.4898 | 25 | 1999.4898 | 25.951 | 139.3858 | 0.77441 | 25.1766 | 89.27% | 265.3048 | 249.3865 | 5985.2758
1954 | 4 | 20 | 1175.5102 | 25 | 1150.5102 | 27.649 | 139.3858 | 0.77441 | 26.8746 | 89.27% | 283.1974 | 266.2056 | 6388.9343
1954 | 4 | 21 | 1266.9388 | 25 | 1241.9388 | 27.4661 | 139.3858 | 0.77441 | 26.6917 | 89.27% | 281.2705 | 264.3943 | 6345.4634
1954 | 4 | 22 | 1286.5306 | 25 | 1261.5306 | 27.4269 | 139.3858 | 0.77441 | 26.6525 | 89.27% | 280.8576 | 264.0062 | 6336.1482
1954 | 4 | 23 | 1168.9796 | 25 | 1143.9796 | 27.662 | 139.3858 | 0.77441 | 26.8876 | 89.27% | 283.3351 | 266.335 | 6392.0394
1954 | 4 | 24 | 851.5918 | 25 | 826.5918 | 28.2968 | 139.3858 | 0.77441 | 27.5224 | 89.27% | 290.0242 | 272.6227 | 6542.9456
1954 | 4 | 25 | 647.8367 | 25 | 622.8367 | 28.7043 | 139.3858 | 0.77441 | 27.9299 | 89.27% | 294.3184 | 276.6593 | 6639.8236
1954 | 4 | 26 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1954 | 4 | 27 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1954 | 4 | 28 | 458.449 | 25 | 433.449 | 29.0831 | 139.3858 | 0.77441 | 28.3087 | 89.27% | 298.3099 | 280.4113 | 6729.8705
1954 | 4 | 29 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
1954 | 4 | 30 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1954 | 5 | 1 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1954 | 5 | 2 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1954 | 5 | 3 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1954 | 5 | 4 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1954 | 5 | 5 | 745.7959 | 25 | 720.7959 | 28.5084 | 139.3858 | 0.77441 | 27.734 | 89.27% | 292.2539 | 274.7187 | 6593.2476
1954 | 5 | 6 | 796.7347 | 25 | 771.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1954 | 5 | 7 | 830.6939 | 25 | 805.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
1954 | 5 | 8 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1954 | 5 | 9 | 1750.2041 | 25 | 1725.2041 | 26.4996 | 139.3858 | 0.77441 | 25.7252 | 89.27% | 271.0855 | 254.8204 | 6115.6885
1954 | 5 | 10 | 2194.2857 | 25 | 2169.2857 | 25.6114 | 139.3858 | 0.77441 | 24.837 | 89.27% | 261.7262 | 246.0227 | 5904.544
1954 | 5 | 11 | 1060.5714 | 25 | 1035.5714 | 27.8789 | 139.3858 | 0.77441 | 27.1044 | 89.27% | 285.6198 | 268.4826 | 6443.5835
1954 | 5 | 12 | 709.2245 | 25 | 684.2245 | 28.5816 | 139.3858 | 0.77441 | 27.8071 | 89.27% | 293.0246 | 275.4432 | 6610.636
1954 | 5 | 13 | 536.8163 | 25 | 511.8163 | 28.9264 | 139.3858 | 0.77441 | 28.152 | 89.27% | 296.6582 | 278.8587 | 6692.6097
1954 | 5 | 14 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1954 | 5 | 15 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1954 | 5 | 16 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1954 | 5 | 17 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1954 | 5 | 18 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1954 | 5 | 19 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1954 | 5 | 20 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1954 | 5 | 21 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1954 | 5 | 22 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1954 | 5 | 23 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1954 | 5 | 24 | 340.898 | 25 | 315.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
1954 | 5 | 25 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1954 | 5 | 26 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1954 | 5 | 27 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1954 | 5 | 28 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1954 | 5 | 29 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1954 | 5 | 30 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1954 | 5 | 31 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1954 | 6 | 1 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1954 | 6 | 2 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1954 | 6 | 3 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1954 | 6 | 4 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1954 | 6 | 5 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1954 | 6 | 6 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1954 | 6 | 7 | 394.449 | 25 | 369.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1954 | 6 | 8 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1954 | 6 | 9 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1954 | 6 | 10 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1954 | 6 | 11 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1954 | 6 | 12 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1954 | 6 | 13 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1954 | 6 | 14 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1954 | 6 | 15 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1954 | 6 | 16 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1954 | 6 | 17 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1954 | 6 | 18 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1954 | 6 | 19 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1954 | 6 | 20 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1954 | 6 | 21 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1954 | 6 | 22 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1954 | 6 | 23 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1954 | 6 | 24 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1954 | 6 | 25 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1954 | 6 | 26 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1954 | 6 | 27 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1954 | 6 | 28 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1954 | 6 | 29 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1954 | 6 | 30 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1954 | 7 | 1 | 348.7347 | 5 | 343.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1954 | 7 | 2 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1954 | 7 | 3 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1954 | 7 | 4 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1954 | 7 | 5 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1954 | 7 | 6 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1954 | 7 | 7 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1954 | 7 | 8 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1954 | 7 | 9 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1954 | 7 | 10 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1954 | 7 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1954 | 7 | 12 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1954 | 7 | 13 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 7 | 14 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1954 | 7 | 15 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1954 | 7 | 16 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1954 | 7 | 17 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1954 | 7 | 18 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1954 | 7 | 19 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1954 | 7 | 20 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1954 | 7 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1954 | 7 | 22 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1954 | 7 | 23 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1954 | 7 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1954 | 7 | 25 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1954 | 7 | 26 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1954 | 7 | 27 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1954 | 7 | 28 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1954 | 7 | 29 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1954 | 7 | 30 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1954 | 7 | 31 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1954 | 8 | 1 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1954 | 8 | 2 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1954 | 8 | 3 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1954 | 8 | 4 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1954 | 8 | 5 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1954 | 8 | 6 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1954 | 8 | 7 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1954 | 8 | 8 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1954 | 8 | 9 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1954 | 8 | 10 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1954 | 8 | 11 | 295.1837 | 5 | 290.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1954 | 8 | 12 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1954 | 8 | 13 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1954 | 8 | 14 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1954 | 8 | 15 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1954 | 8 | 16 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1954 | 8 | 17 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1954 | 8 | 18 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1954 | 8 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1954 | 8 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1954 | 8 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1954 | 8 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1954 | 8 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1954 | 8 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1954 | 8 | 25 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1954 | 8 | 26 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1954 | 8 | 27 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1954 | 8 | 28 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1954 | 8 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1954 | 8 | 30 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1954 | 8 | 31 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1954 | 9 | 1 | 757.551 | 15 | 742.551 | 28.4849 | 139.3858 | 0.77441 | 27.7105 | 89.27% | 292.0061 | 274.4858 | 6587.6585
1954 | 9 | 2 | 343.5102 | 15 | 328.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1954 | 9 | 3 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1954 | 9 | 4 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1954 | 9 | 5 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1954 | 9 | 6 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1954 | 9 | 7 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1954 | 9 | 8 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1954 | 9 | 9 | 359.1837 | 15 | 344.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1954 | 9 | 10 | 544.6531 | 15 | 529.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
1954 | 9 | 11 | 1371.4286 | 15 | 1356.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1954 | 9 | 12 | 2808.1633 | 15 | 2793.1633 | 24.3837 | 0 | 0 | 24.3837 | 0% | 0 | 0 | 0
1954 | 9 | 13 | 986.1224 | 15 | 971.1224 | 28.0278 | 139.3858 | 0.77441 | 27.2533 | 89.27% | 287.1889 | 269.9576 | 6478.9812
1954 | 9 | 14 | 768 | 15 | 753 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
1954 | 9 | 15 | 592.9796 | 15 | 577.9796 | 28.814 | 139.3858 | 0.77441 | 28.0396 | 89.27% | 295.4746 | 277.7461 | 6665.9062
1954 | 9 | 16 | 424.4898 | 15 | 409.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1954 | 9 | 17 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1954 | 9 | 18 | 367.0204 | 15 | 352.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1954 | 9 | 19 | 346.1224 | 15 | 331.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1954 | 9 | 20 | 664.8163 | 15 | 649.8163 | 28.6704 | 139.3858 | 0.77441 | 27.896 | 89.27% | 293.9606 | 276.3229 | 6631.7504
1954 | 9 | 21 | 462.3673 | 15 | 447.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
1954 | 9 | 22 | 367.0204 | 15 | 352.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1954 | 9 | 23 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1954 | 9 | 24 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1954 | 9 | 25 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1954 | 9 | 26 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1954 | 9 | 27 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1954 | 9 | 28 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1954 | 9 | 29 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1954 | 9 | 30 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1954 | 10 | 1 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1954 | 10 | 2 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1954 | 10 | 3 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1954 | 10 | 4 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1954 | 10 | 5 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1954 | 10 | 6 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1954 | 10 | 7 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1954 | 10 | 8 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1954 | 10 | 9 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1954 | 10 | 10 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1954 | 10 | 11 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1954 | 10 | 12 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1954 | 10 | 13 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1954 | 10 | 14 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1954 | 10 | 15 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1954 | 10 | 16 | 685.7143 | 15 | 670.7143 | 28.6286 | 139.3858 | 0.77441 | 27.8542 | 89.27% | 293.5201 | 275.9089 | 6621.8142
1954 | 10 | 17 | 705.3061 | 15 | 690.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1954 | 10 | 18 | 414.0408 | 15 | 399.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1954 | 10 | 19 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1954 | 10 | 20 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1954 | 10 | 21 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1954 | 10 | 22 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1954 | 10 | 23 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1954 | 10 | 24 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1954 | 10 | 25 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1954 | 10 | 26 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1954 | 10 | 27 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1954 | 10 | 28 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1954 | 10 | 29 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1954 | 10 | 30 | 282.1224 | 15 | 267.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1954 | 10 | 31 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1954 | 11 | 1 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1954 | 11 | 2 | 317.3878 | 15 | 302.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1954 | 11 | 3 | 535.5102 | 15 | 520.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1954 | 11 | 4 | 1137.6327 | 15 | 1122.6327 | 27.7247 | 139.3858 | 0.77441 | 26.9503 | 89.27% | 283.9957 | 266.956 | 6406.9437
1954 | 11 | 5 | 643.9184 | 15 | 628.9184 | 28.7122 | 139.3858 | 0.77441 | 27.9378 | 89.27% | 294.401 | 276.7369 | 6641.6867
1954 | 11 | 6 | 424.4898 | 15 | 409.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1954 | 11 | 7 | 323.9184 | 15 | 308.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1954 | 11 | 8 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1954 | 11 | 9 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1954 | 11 | 10 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1954 | 11 | 11 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1954 | 11 | 12 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1954 | 11 | 13 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1954 | 11 | 14 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1954 | 11 | 15 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1954 | 11 | 16 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1954 | 11 | 17 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1954 | 11 | 18 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1954 | 11 | 19 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1954 | 11 | 20 | 287.3469 | 15 | 272.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1954 | 11 | 21 | 692.2449 | 15 | 677.2449 | 28.6155 | 139.3858 | 0.77441 | 27.8411 | 89.27% | 293.3825 | 275.7795 | 6618.7092
1954 | 11 | 22 | 692.2449 | 15 | 677.2449 | 28.6155 | 139.3858 | 0.77441 | 27.8411 | 89.27% | 293.3825 | 275.7795 | 6618.7092
1954 | 11 | 23 | 451.9184 | 15 | 436.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1954 | 11 | 24 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1954 | 11 | 25 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1954 | 11 | 26 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1954 | 11 | 27 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1954 | 11 | 28 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1954 | 11 | 29 | 339.5918 | 15 | 324.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1954 | 11 | 30 | 372.2449 | 15 | 357.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1954 | 12 | 1 | 348.7347 | 5 | 343.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1954 | 12 | 2 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1954 | 12 | 3 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1954 | 12 | 4 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1954 | 12 | 5 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1954 | 12 | 6 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1954 | 12 | 7 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1954 | 12 | 8 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1954 | 12 | 9 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1954 | 12 | 10 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1954 | 12 | 11 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1954 | 12 | 12 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1954 | 12 | 13 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1954 | 12 | 14 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1954 | 12 | 15 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1954 | 12 | 16 | 420.5714 | 5 | 415.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1954 | 12 | 17 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1954 | 12 | 18 | 542.0408 | 5 | 537.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
1954 | 12 | 19 | 2115.9184 | 5 | 2110.9184 | 25.7682 | 139.3858 | 0.77441 | 24.9938 | 89.27% | 263.3779 | 247.5752 | 5941.8048
1954 | 12 | 20 | 862.0408 | 5 | 857.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
1954 | 12 | 21 | 495.0204 | 5 | 490.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1954 | 12 | 22 | 378.7755 | 5 | 373.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1954 | 12 | 23 | 367.0204 | 5 | 362.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1954 | 12 | 24 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1954 | 12 | 25 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1954 | 12 | 26 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1954 | 12 | 27 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1954 | 12 | 28 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1954 | 12 | 29 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1954 | 12 | 30 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1954 | 12 | 31 | 218.1224 | 5 | 213.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1955 | 1 | 1 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1955 | 1 | 2 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1955 | 1 | 3 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1955 | 1 | 4 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1955 | 1 | 5 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1955 | 1 | 6 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1955 | 1 | 7 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1955 | 1 | 8 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1955 | 1 | 9 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1955 | 1 | 10 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1955 | 1 | 11 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1955 | 1 | 12 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1955 | 1 | 13 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1955 | 1 | 14 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1955 | 1 | 15 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1955 | 1 | 16 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1955 | 1 | 17 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1955 | 1 | 18 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1955 | 1 | 19 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1955 | 1 | 20 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1955 | 1 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1955 | 1 | 22 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1955 | 1 | 23 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1955 | 1 | 24 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1955 | 1 | 25 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1955 | 1 | 26 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1955 | 1 | 27 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1955 | 1 | 28 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1955 | 1 | 29 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1955 | 1 | 30 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1955 | 1 | 31 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1955 | 2 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1955 | 2 | 2 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1955 | 2 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1955 | 2 | 4 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1955 | 2 | 5 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1955 | 2 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1955 | 2 | 7 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1955 | 2 | 8 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1955 | 2 | 9 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1955 | 2 | 10 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1955 | 2 | 11 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1955 | 2 | 12 | 309.551 | 5 | 304.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1955 | 2 | 13 | 357.8776 | 5 | 352.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1955 | 2 | 14 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1955 | 2 | 15 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1955 | 2 | 16 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1955 | 2 | 17 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1955 | 2 | 18 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1955 | 2 | 19 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1955 | 2 | 20 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1955 | 2 | 21 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1955 | 2 | 22 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1955 | 2 | 23 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1955 | 2 | 24 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1955 | 2 | 25 | 263.8367 | 5 | 258.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1955 | 2 | 26 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1955 | 2 | 27 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1955 | 2 | 28 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1955 | 3 | 1 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1955 | 3 | 2 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1955 | 3 | 3 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1955 | 3 | 4 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1955 | 3 | 5 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1955 | 3 | 6 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1955 | 3 | 7 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1955 | 3 | 8 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1955 | 3 | 9 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1955 | 3 | 10 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1955 | 3 | 11 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1955 | 3 | 12 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1955 | 3 | 13 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1955 | 3 | 14 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1955 | 3 | 15 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1955 | 3 | 16 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1955 | 3 | 17 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1955 | 3 | 18 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1955 | 3 | 19 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1955 | 3 | 20 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1955 | 3 | 21 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1955 | 3 | 22 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1955 | 3 | 23 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1955 | 3 | 24 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1955 | 3 | 25 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1955 | 3 | 26 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1955 | 3 | 27 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1955 | 3 | 28 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1955 | 3 | 29 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1955 | 3 | 30 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1955 | 3 | 31 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1955 | 4 | 1 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1955 | 4 | 2 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1955 | 4 | 3 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1955 | 4 | 4 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
1955 | 4 | 5 | 574.6939 | 25 | 549.6939 | 28.8506 | 139.3858 | 0.77441 | 28.0762 | 89.27% | 295.8599 | 278.1083 | 6674.6004
1955 | 4 | 6 | 770.6122 | 25 | 745.6122 | 28.4588 | 139.3858 | 0.77441 | 27.6844 | 89.27% | 291.7309 | 274.227 | 6581.4484
1955 | 4 | 7 | 903.8367 | 25 | 878.8367 | 28.1923 | 139.3858 | 0.77441 | 27.4179 | 89.27% | 288.9231 | 271.5877 | 6518.105
1955 | 4 | 8 | 996.5714 | 25 | 971.5714 | 28.0069 | 139.3858 | 0.77441 | 27.2324 | 89.27% | 286.9687 | 269.7505 | 6474.0131
1955 | 4 | 9 | 705.3061 | 25 | 680.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1955 | 4 | 10 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
1955 | 4 | 11 | 875.102 | 25 | 850.102 | 28.2498 | 139.3858 | 0.77441 | 27.4754 | 89.27% | 289.5287 | 272.157 | 6531.7673
1955 | 4 | 12 | 1103.6735 | 25 | 1078.6735 | 27.7927 | 139.3858 | 0.77441 | 27.0182 | 89.27% | 284.7114 | 267.6288 | 6423.09
1955 | 4 | 13 | 825.4694 | 25 | 800.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
1955 | 4 | 14 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1955 | 4 | 15 | 914.2857 | 25 | 889.2857 | 28.1714 | 139.3858 | 0.77441 | 27.397 | 89.27% | 288.7029 | 271.3807 | 6513.1369
1955 | 4 | 16 | 1214.6939 | 25 | 1189.6939 | 27.5706 | 139.3858 | 0.77441 | 26.7962 | 89.27% | 282.3716 | 265.4293 | 6370.3039
1955 | 4 | 17 | 903.8367 | 25 | 878.8367 | 28.1923 | 139.3858 | 0.77441 | 27.4179 | 89.27% | 288.9231 | 271.5877 | 6518.105
1955 | 4 | 18 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1955 | 4 | 19 | 609.9592 | 25 | 584.9592 | 28.7801 | 139.3858 | 0.77441 | 28.0057 | 89.27% | 295.1167 | 277.4097 | 6657.833
1955 | 4 | 20 | 723.5918 | 25 | 698.5918 | 28.5528 | 139.3858 | 0.77441 | 27.7784 | 89.27% | 292.7218 | 275.1585 | 6603.8049
1955 | 4 | 21 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1955 | 4 | 22 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1955 | 4 | 23 | 410.1224 | 25 | 385.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1955 | 4 | 24 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1955 | 4 | 25 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1955 | 4 | 26 | 643.9184 | 25 | 618.9184 | 28.7122 | 139.3858 | 0.77441 | 27.9378 | 89.27% | 294.401 | 276.7369 | 6641.6867
1955 | 4 | 27 | 782.3673 | 25 | 757.3673 | 28.4353 | 139.3858 | 0.77441 | 27.6609 | 89.27% | 291.4831 | 273.9941 | 6575.8593
1955 | 4 | 28 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1955 | 4 | 29 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1955 | 4 | 30 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1955 | 5 | 1 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1955 | 5 | 2 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1955 | 5 | 3 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1955 | 5 | 4 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1955 | 5 | 5 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1955 | 5 | 6 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1955 | 5 | 7 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1955 | 5 | 8 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1955 | 5 | 9 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1955 | 5 | 10 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1955 | 5 | 11 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1955 | 5 | 12 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1955 | 5 | 13 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1955 | 5 | 14 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1955 | 5 | 15 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1955 | 5 | 16 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1955 | 5 | 17 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1955 | 5 | 18 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1955 | 5 | 19 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1955 | 5 | 20 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1955 | 5 | 21 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1955 | 5 | 22 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1955 | 5 | 23 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1955 | 5 | 24 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1955 | 5 | 25 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1955 | 5 | 26 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
1955 | 5 | 27 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1955 | 5 | 28 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1955 | 5 | 29 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1955 | 5 | 30 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1955 | 5 | 31 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1955 | 6 | 1 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1955 | 6 | 2 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1955 | 6 | 3 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1955 | 6 | 4 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1955 | 6 | 5 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1955 | 6 | 6 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1955 | 6 | 7 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1955 | 6 | 8 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1955 | 6 | 9 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1955 | 6 | 10 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1955 | 6 | 11 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1955 | 6 | 12 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1955 | 6 | 13 | 754.9388 | 25 | 729.9388 | 28.4901 | 139.3858 | 0.77441 | 27.7157 | 89.27% | 292.0612 | 274.5375 | 6588.9005
1955 | 6 | 14 | 589.0612 | 25 | 564.0612 | 28.8219 | 139.3858 | 0.77441 | 28.0475 | 89.27% | 295.5571 | 277.8237 | 6667.7692
1955 | 6 | 15 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1955 | 6 | 16 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1955 | 6 | 17 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1955 | 6 | 18 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1955 | 6 | 19 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1955 | 6 | 20 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1955 | 6 | 21 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1955 | 6 | 22 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1955 | 6 | 23 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1955 | 6 | 24 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1955 | 6 | 25 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1955 | 6 | 26 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1955 | 6 | 27 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1955 | 6 | 28 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1955 | 6 | 29 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1955 | 6 | 30 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1955 | 7 | 1 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1955 | 7 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1955 | 7 | 3 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1955 | 7 | 4 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1955 | 7 | 5 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1955 | 7 | 6 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1955 | 7 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1955 | 7 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1955 | 7 | 9 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1955 | 7 | 10 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1955 | 7 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1955 | 7 | 12 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1955 | 7 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1955 | 7 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 7 | 15 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1955 | 7 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 7 | 17 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1955 | 7 | 18 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1955 | 7 | 19 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 7 | 20 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1955 | 7 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 7 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 7 | 23 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1955 | 7 | 24 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1955 | 7 | 25 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1955 | 7 | 26 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1955 | 7 | 27 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1955 | 7 | 28 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1955 | 7 | 29 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1955 | 7 | 30 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1955 | 7 | 31 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1955 | 8 | 1 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1955 | 8 | 2 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1955 | 8 | 3 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1955 | 8 | 4 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1955 | 8 | 5 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1955 | 8 | 6 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1955 | 8 | 7 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1955 | 8 | 8 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1955 | 8 | 9 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1955 | 8 | 10 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1955 | 8 | 11 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 8 | 12 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1955 | 8 | 13 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1955 | 8 | 14 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1955 | 8 | 15 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1955 | 8 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1955 | 8 | 17 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1955 | 8 | 18 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1955 | 8 | 19 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1955 | 8 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1955 | 8 | 21 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 8 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 8 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 8 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1955 | 8 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1955 | 8 | 26 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1955 | 8 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 8 | 28 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1955 | 8 | 29 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1955 | 8 | 30 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1955 | 8 | 31 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1955 | 9 | 1 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1955 | 9 | 2 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1955 | 9 | 3 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1955 | 9 | 4 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1955 | 9 | 5 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1955 | 9 | 6 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1955 | 9 | 7 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1955 | 9 | 8 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1955 | 9 | 9 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 10 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 11 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 12 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1955 | 9 | 13 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 14 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 15 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1955 | 9 | 16 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 17 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1955 | 9 | 18 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 19 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1955 | 9 | 20 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1955 | 9 | 21 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1955 | 9 | 22 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1955 | 9 | 23 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
1955 | 9 | 24 | 3.2653 | 15 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1955 | 9 | 25 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1955 | 9 | 26 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1955 | 9 | 27 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1955 | 9 | 28 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1955 | 9 | 29 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 9 | 30 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1955 | 10 | 1 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1955 | 10 | 2 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1955 | 10 | 3 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1955 | 10 | 4 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1955 | 10 | 5 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1955 | 10 | 6 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1955 | 10 | 7 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1955 | 10 | 8 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1955 | 10 | 9 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1955 | 10 | 10 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1955 | 10 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1955 | 10 | 12 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1955 | 10 | 13 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1955 | 10 | 14 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1955 | 10 | 15 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1955 | 10 | 16 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1955 | 10 | 17 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1955 | 10 | 18 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1955 | 10 | 19 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1955 | 10 | 20 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1955 | 10 | 21 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1955 | 10 | 22 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1955 | 10 | 23 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1955 | 10 | 24 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1955 | 10 | 25 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1955 | 10 | 26 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1955 | 10 | 27 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1955 | 10 | 28 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1955 | 10 | 29 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1955 | 10 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1955 | 10 | 31 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1955 | 11 | 1 | 509.3878 | 15 | 494.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1955 | 11 | 2 | 424.4898 | 15 | 409.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1955 | 11 | 3 | 242.9388 | 15 | 227.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1955 | 11 | 4 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1955 | 11 | 5 | 431.0204 | 15 | 416.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1955 | 11 | 6 | 355.2653 | 15 | 340.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1955 | 11 | 7 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1955 | 11 | 8 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1955 | 11 | 9 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1955 | 11 | 10 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1955 | 11 | 11 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1955 | 11 | 12 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1955 | 11 | 13 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1955 | 11 | 14 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1955 | 11 | 15 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1955 | 11 | 16 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1955 | 11 | 17 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1955 | 11 | 18 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1955 | 11 | 19 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1955 | 11 | 20 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1955 | 11 | 21 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1955 | 11 | 22 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1955 | 11 | 23 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1955 | 11 | 24 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1955 | 11 | 25 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1955 | 11 | 26 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1955 | 11 | 27 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1955 | 11 | 28 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1955 | 11 | 29 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1955 | 11 | 30 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1955 | 12 | 1 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1955 | 12 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1955 | 12 | 3 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1955 | 12 | 4 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1955 | 12 | 5 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1955 | 12 | 6 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1955 | 12 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1955 | 12 | 8 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1955 | 12 | 9 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1955 | 12 | 10 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1955 | 12 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1955 | 12 | 12 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1955 | 12 | 13 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1955 | 12 | 14 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1955 | 12 | 15 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1955 | 12 | 16 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1955 | 12 | 17 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1955 | 12 | 18 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1955 | 12 | 19 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1955 | 12 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1955 | 12 | 21 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1955 | 12 | 22 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 12 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 12 | 24 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1955 | 12 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 12 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 12 | 27 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1955 | 12 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1955 | 12 | 29 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1955 | 12 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1955 | 12 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 2 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1956 | 1 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 6 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 1 | 8 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1956 | 1 | 9 | 476.7347 | 5 | 471.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
1956 | 1 | 10 | 1097.1429 | 5 | 1092.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
1956 | 1 | 11 | 1071.0204 | 5 | 1066.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
1956 | 1 | 12 | 768 | 5 | 763 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
1956 | 1 | 13 | 1149.3878 | 5 | 1144.3878 | 27.7012 | 139.3858 | 0.77441 | 26.9268 | 89.27% | 283.748 | 266.7231 | 6401.3546
1956 | 1 | 14 | 914.2857 | 5 | 909.2857 | 28.1714 | 139.3858 | 0.77441 | 27.397 | 89.27% | 288.7029 | 271.3807 | 6513.1369
1956 | 1 | 15 | 528.9796 | 5 | 523.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1956 | 1 | 16 | 374.8571 | 5 | 369.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1956 | 1 | 17 | 295.1837 | 5 | 290.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1956 | 1 | 18 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1956 | 1 | 19 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1956 | 1 | 20 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1956 | 1 | 21 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1956 | 1 | 22 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1956 | 1 | 23 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1956 | 1 | 24 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1956 | 1 | 25 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1956 | 1 | 26 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1956 | 1 | 27 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1956 | 1 | 28 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1956 | 1 | 29 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1956 | 1 | 30 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1956 | 1 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1956 | 2 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1956 | 2 | 2 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1956 | 2 | 3 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1956 | 2 | 4 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1956 | 2 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1956 | 2 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1956 | 2 | 7 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1956 | 2 | 8 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1956 | 2 | 9 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1956 | 2 | 10 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1956 | 2 | 11 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1956 | 2 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1956 | 2 | 13 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1956 | 2 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1956 | 2 | 15 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1956 | 2 | 16 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1956 | 2 | 17 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1956 | 2 | 18 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1956 | 2 | 19 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1956 | 2 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1956 | 2 | 21 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1956 | 2 | 22 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1956 | 2 | 23 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1956 | 2 | 24 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1956 | 2 | 25 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1956 | 2 | 26 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1956 | 2 | 27 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1956 | 2 | 28 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1956 | 2 | 29 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1956 | 3 | 1 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1956 | 3 | 2 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1956 | 3 | 3 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1956 | 3 | 4 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 5 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 6 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1956 | 3 | 7 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1956 | 3 | 8 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1956 | 3 | 9 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1956 | 3 | 10 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1956 | 3 | 11 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 12 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1956 | 3 | 13 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 14 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 15 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 16 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1956 | 3 | 17 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1956 | 3 | 18 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1956 | 3 | 19 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1956 | 3 | 20 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1956 | 3 | 21 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1956 | 3 | 22 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1956 | 3 | 23 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1956 | 3 | 24 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1956 | 3 | 25 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1956 | 3 | 26 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1956 | 3 | 27 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 3 | 28 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1956 | 3 | 29 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1956 | 3 | 30 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1956 | 3 | 31 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 4 | 1 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 4 | 2 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 4 | 3 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1956 | 4 | 4 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1956 | 4 | 5 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1956 | 4 | 6 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1956 | 4 | 7 | 585.1429 | 25 | 560.1429 | 28.8297 | 139.3858 | 0.77441 | 28.0553 | 89.27% | 295.6397 | 277.9013 | 6669.6323
1956 | 4 | 8 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1956 | 4 | 9 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
1956 | 4 | 10 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1956 | 4 | 11 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1956 | 4 | 12 | 544.6531 | 25 | 519.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
1956 | 4 | 13 | 653.0612 | 25 | 628.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
1956 | 4 | 14 | 705.3061 | 25 | 680.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1956 | 4 | 15 | 670.0408 | 25 | 645.0408 | 28.6599 | 139.3858 | 0.77441 | 27.8855 | 89.27% | 293.8505 | 276.2194 | 6629.2664
1956 | 4 | 16 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
1956 | 4 | 17 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1956 | 4 | 18 | 1201.6327 | 25 | 1176.6327 | 27.5967 | 139.3858 | 0.77441 | 26.8223 | 89.27% | 282.6469 | 265.6881 | 6376.514
1956 | 4 | 19 | 862.0408 | 25 | 837.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
1956 | 4 | 20 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1956 | 4 | 21 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1956 | 4 | 22 | 585.1429 | 25 | 560.1429 | 28.8297 | 139.3858 | 0.77441 | 28.0553 | 89.27% | 295.6397 | 277.9013 | 6669.6323
1956 | 4 | 23 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1956 | 4 | 24 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
1956 | 4 | 25 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1956 | 4 | 26 | 416.6531 | 25 | 391.6531 | 29.1667 | 139.3858 | 0.77441 | 28.3923 | 89.27% | 299.1907 | 281.2393 | 6749.7429
1956 | 4 | 27 | 420.5714 | 25 | 395.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1956 | 4 | 28 | 687.0204 | 25 | 662.0204 | 28.626 | 139.3858 | 0.77441 | 27.8515 | 89.27% | 293.4926 | 275.8831 | 6621.1932
1956 | 4 | 29 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1956 | 4 | 30 | 1131.102 | 25 | 1106.102 | 27.7378 | 139.3858 | 0.77441 | 26.9634 | 89.27% | 284.1334 | 267.0854 | 6410.0488
1956 | 5 | 1 | 809.7959 | 25 | 784.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
1956 | 5 | 2 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1956 | 5 | 3 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1956 | 5 | 4 | 568.1633 | 25 | 543.1633 | 28.8637 | 139.3858 | 0.77441 | 28.0893 | 89.27% | 295.9976 | 278.2377 | 6677.7054
1956 | 5 | 5 | 609.9592 | 25 | 584.9592 | 28.7801 | 139.3858 | 0.77441 | 28.0057 | 89.27% | 295.1167 | 277.4097 | 6657.833
1956 | 5 | 6 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1956 | 5 | 7 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1956 | 5 | 8 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1956 | 5 | 9 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1956 | 5 | 10 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1956 | 5 | 11 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1956 | 5 | 12 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1956 | 5 | 13 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1956 | 5 | 14 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1956 | 5 | 15 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1956 | 5 | 16 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1956 | 5 | 17 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1956 | 5 | 18 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1956 | 5 | 19 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1956 | 5 | 20 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1956 | 5 | 21 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1956 | 5 | 22 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1956 | 5 | 23 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1956 | 5 | 24 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1956 | 5 | 25 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1956 | 5 | 26 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1956 | 5 | 27 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1956 | 5 | 28 | 862.0408 | 25 | 837.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
1956 | 5 | 29 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1956 | 5 | 30 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1956 | 5 | 31 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1956 | 6 | 1 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1956 | 6 | 2 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1956 | 6 | 3 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1956 | 6 | 4 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1956 | 6 | 5 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1956 | 6 | 6 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1956 | 6 | 7 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1956 | 6 | 8 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1956 | 6 | 9 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1956 | 6 | 10 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1956 | 6 | 11 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1956 | 6 | 12 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1956 | 6 | 13 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1956 | 6 | 14 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1956 | 6 | 15 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1956 | 6 | 16 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1956 | 6 | 17 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1956 | 6 | 18 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1956 | 6 | 19 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1956 | 6 | 20 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1956 | 6 | 21 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1956 | 6 | 22 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1956 | 6 | 23 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1956 | 6 | 24 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1956 | 6 | 25 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1956 | 6 | 26 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1956 | 6 | 27 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1956 | 6 | 28 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1956 | 6 | 29 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1956 | 6 | 30 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1956 | 7 | 1 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1956 | 7 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1956 | 7 | 3 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1956 | 7 | 4 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1956 | 7 | 5 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1956 | 7 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1956 | 7 | 7 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1956 | 7 | 8 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1956 | 7 | 9 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1956 | 7 | 10 | 640 | 5 | 635 | 28.72 | 139.3858 | 0.77441 | 27.9456 | 89.27% | 294.4836 | 276.8146 | 6643.5497
1956 | 7 | 11 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1956 | 7 | 12 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1956 | 7 | 13 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1956 | 7 | 14 | 431.0204 | 5 | 426.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1956 | 7 | 15 | 363.102 | 5 | 358.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1956 | 7 | 16 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1956 | 7 | 17 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1956 | 7 | 18 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1956 | 7 | 19 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1956 | 7 | 20 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1956 | 7 | 21 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1956 | 7 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1956 | 7 | 23 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1956 | 7 | 24 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1956 | 7 | 25 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1956 | 7 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1956 | 7 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1956 | 7 | 28 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1956 | 7 | 29 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1956 | 7 | 30 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1956 | 7 | 31 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1956 | 8 | 1 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1956 | 8 | 2 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1956 | 8 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1956 | 8 | 4 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1956 | 8 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1956 | 8 | 6 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1956 | 8 | 7 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1956 | 8 | 8 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1956 | 8 | 9 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1956 | 8 | 10 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1956 | 8 | 11 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1956 | 8 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1956 | 8 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1956 | 8 | 14 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1956 | 8 | 15 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1956 | 8 | 16 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1956 | 8 | 17 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1956 | 8 | 18 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1956 | 8 | 19 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1956 | 8 | 20 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1956 | 8 | 21 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1956 | 8 | 22 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1956 | 8 | 23 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1956 | 8 | 24 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1956 | 8 | 25 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1956 | 8 | 26 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1956 | 8 | 27 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1956 | 8 | 28 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1956 | 8 | 29 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1956 | 8 | 30 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1956 | 8 | 31 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1956 | 9 | 1 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1956 | 9 | 2 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1956 | 9 | 3 | 457.1429 | 15 | 442.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1956 | 9 | 4 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1956 | 9 | 5 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1956 | 9 | 6 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1956 | 9 | 7 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1956 | 9 | 8 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1956 | 9 | 9 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1956 | 9 | 10 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1956 | 9 | 11 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1956 | 9 | 12 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1956 | 9 | 13 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1956 | 9 | 14 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1956 | 9 | 15 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1956 | 9 | 16 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1956 | 9 | 17 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1956 | 9 | 18 | 355.2653 | 15 | 340.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1956 | 9 | 19 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1956 | 9 | 20 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1956 | 9 | 21 | 346.1224 | 15 | 331.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1956 | 9 | 22 | 220.7347 | 15 | 205.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1956 | 9 | 23 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1956 | 9 | 24 | 313.4694 | 15 | 298.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1956 | 9 | 25 | 346.1224 | 15 | 331.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1956 | 9 | 26 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1956 | 9 | 27 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1956 | 9 | 28 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1956 | 9 | 29 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1956 | 9 | 30 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1956 | 10 | 1 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1956 | 10 | 2 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1956 | 10 | 3 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1956 | 10 | 4 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1956 | 10 | 5 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1956 | 10 | 6 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1956 | 10 | 7 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1956 | 10 | 8 | 394.449 | 15 | 379.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1956 | 10 | 9 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1956 | 10 | 10 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1956 | 10 | 11 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1956 | 10 | 12 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1956 | 10 | 13 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1956 | 10 | 14 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1956 | 10 | 15 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1956 | 10 | 16 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1956 | 10 | 17 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1956 | 10 | 18 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1956 | 10 | 19 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1956 | 10 | 20 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1956 | 10 | 21 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1956 | 10 | 22 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1956 | 10 | 23 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1956 | 10 | 24 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1956 | 10 | 25 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1956 | 10 | 26 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1956 | 10 | 27 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1956 | 10 | 28 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1956 | 10 | 29 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1956 | 10 | 30 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1956 | 10 | 31 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1956 | 11 | 1 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1956 | 11 | 2 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1956 | 11 | 3 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1956 | 11 | 4 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1956 | 11 | 5 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1956 | 11 | 6 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1956 | 11 | 7 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1956 | 11 | 8 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1956 | 11 | 9 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1956 | 11 | 10 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1956 | 11 | 11 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1956 | 11 | 12 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1956 | 11 | 13 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1956 | 11 | 14 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1956 | 11 | 15 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1956 | 11 | 16 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1956 | 11 | 17 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1956 | 11 | 18 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1956 | 11 | 19 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1956 | 11 | 20 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1956 | 11 | 21 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1956 | 11 | 22 | 437.551 | 15 | 422.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1956 | 11 | 23 | 367.0204 | 15 | 352.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1956 | 11 | 24 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1956 | 11 | 25 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1956 | 11 | 26 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1956 | 11 | 27 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1956 | 11 | 28 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1956 | 11 | 29 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1956 | 11 | 30 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1956 | 12 | 1 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1956 | 12 | 2 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1956 | 12 | 3 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1956 | 12 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1956 | 12 | 5 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1956 | 12 | 6 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1956 | 12 | 7 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1956 | 12 | 8 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1956 | 12 | 9 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1956 | 12 | 10 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1956 | 12 | 11 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1956 | 12 | 12 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1956 | 12 | 13 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1956 | 12 | 14 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1956 | 12 | 15 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1956 | 12 | 16 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1956 | 12 | 17 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1956 | 12 | 18 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1956 | 12 | 19 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1956 | 12 | 20 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1956 | 12 | 21 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1956 | 12 | 22 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1956 | 12 | 23 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1956 | 12 | 24 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1956 | 12 | 25 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1956 | 12 | 26 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1956 | 12 | 27 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1956 | 12 | 28 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1956 | 12 | 29 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1956 | 12 | 30 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1956 | 12 | 31 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1957 | 1 | 1 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1957 | 1 | 2 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1957 | 1 | 3 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1957 | 1 | 4 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1957 | 1 | 5 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1957 | 1 | 6 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 1 | 7 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1957 | 1 | 8 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1957 | 1 | 9 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1957 | 1 | 10 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1957 | 1 | 11 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 1 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 1 | 13 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 1 | 14 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1957 | 1 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1957 | 1 | 16 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1957 | 1 | 17 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1957 | 1 | 18 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1957 | 1 | 19 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1957 | 1 | 20 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1957 | 1 | 21 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1957 | 1 | 22 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1957 | 1 | 23 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1957 | 1 | 24 | 400.9796 | 5 | 395.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1957 | 1 | 25 | 320 | 5 | 315 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1957 | 1 | 26 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1957 | 1 | 27 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1957 | 1 | 28 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1957 | 1 | 29 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1957 | 1 | 30 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1957 | 1 | 31 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1957 | 2 | 1 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1957 | 2 | 2 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1957 | 2 | 3 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1957 | 2 | 4 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1957 | 2 | 5 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1957 | 2 | 6 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1957 | 2 | 7 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1957 | 2 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1957 | 2 | 9 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1957 | 2 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1957 | 2 | 11 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1957 | 2 | 12 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1957 | 2 | 13 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 2 | 14 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 2 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 2 | 16 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1957 | 2 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1957 | 2 | 18 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1957 | 2 | 19 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1957 | 2 | 20 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1957 | 2 | 21 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1957 | 2 | 22 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1957 | 2 | 23 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1957 | 2 | 24 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1957 | 2 | 25 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1957 | 2 | 26 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1957 | 2 | 27 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1957 | 2 | 28 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1957 | 3 | 1 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1957 | 3 | 2 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1957 | 3 | 3 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1957 | 3 | 4 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1957 | 3 | 5 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1957 | 3 | 6 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1957 | 3 | 7 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1957 | 3 | 8 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1957 | 3 | 9 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1957 | 3 | 10 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1957 | 3 | 11 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1957 | 3 | 12 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1957 | 3 | 13 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1957 | 3 | 14 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1957 | 3 | 15 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1957 | 3 | 16 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1957 | 3 | 17 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1957 | 3 | 18 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1957 | 3 | 19 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1957 | 3 | 20 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1957 | 3 | 21 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1957 | 3 | 22 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1957 | 3 | 23 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1957 | 3 | 24 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1957 | 3 | 25 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1957 | 3 | 26 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1957 | 3 | 27 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1957 | 3 | 28 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1957 | 3 | 29 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1957 | 3 | 30 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1957 | 3 | 31 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1957 | 4 | 1 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1957 | 4 | 2 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1957 | 4 | 3 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1957 | 4 | 4 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1957 | 4 | 5 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1957 | 4 | 6 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1957 | 4 | 7 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1957 | 4 | 8 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1957 | 4 | 9 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1957 | 4 | 10 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1957 | 4 | 11 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1957 | 4 | 12 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1957 | 4 | 13 | 441.4694 | 25 | 416.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
1957 | 4 | 14 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1957 | 4 | 15 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1957 | 4 | 16 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1957 | 4 | 17 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1957 | 4 | 18 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1957 | 4 | 19 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1957 | 4 | 20 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1957 | 4 | 21 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1957 | 4 | 22 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1957 | 4 | 23 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1957 | 4 | 24 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1957 | 4 | 25 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1957 | 4 | 26 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1957 | 4 | 27 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1957 | 4 | 28 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1957 | 4 | 29 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1957 | 4 | 30 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1957 | 5 | 1 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1957 | 5 | 2 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1957 | 5 | 3 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1957 | 5 | 4 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1957 | 5 | 5 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1957 | 5 | 6 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1957 | 5 | 7 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1957 | 5 | 8 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1957 | 5 | 9 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1957 | 5 | 10 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1957 | 5 | 11 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1957 | 5 | 12 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1957 | 5 | 13 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1957 | 5 | 14 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1957 | 5 | 15 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1957 | 5 | 16 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1957 | 5 | 17 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1957 | 5 | 18 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1957 | 5 | 19 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1957 | 5 | 20 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1957 | 5 | 21 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1957 | 5 | 22 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1957 | 5 | 23 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1957 | 5 | 24 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1957 | 5 | 25 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1957 | 5 | 26 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1957 | 5 | 27 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1957 | 5 | 28 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1957 | 5 | 29 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1957 | 5 | 30 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1957 | 5 | 31 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1957 | 6 | 1 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1957 | 6 | 2 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1957 | 6 | 3 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1957 | 6 | 4 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1957 | 6 | 5 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1957 | 6 | 6 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1957 | 6 | 7 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1957 | 6 | 8 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1957 | 6 | 9 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1957 | 6 | 10 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1957 | 6 | 11 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1957 | 6 | 12 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1957 | 6 | 13 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1957 | 6 | 14 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1957 | 6 | 15 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1957 | 6 | 16 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1957 | 6 | 17 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1957 | 6 | 18 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1957 | 6 | 19 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1957 | 6 | 20 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1957 | 6 | 21 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1957 | 6 | 22 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1957 | 6 | 23 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1957 | 6 | 24 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1957 | 6 | 25 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1957 | 6 | 26 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1957 | 6 | 27 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1957 | 6 | 28 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1957 | 6 | 29 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1957 | 6 | 30 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1957 | 7 | 1 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1957 | 7 | 2 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1957 | 7 | 3 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1957 | 7 | 4 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1957 | 7 | 5 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1957 | 7 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1957 | 7 | 7 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1957 | 7 | 8 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1957 | 7 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1957 | 7 | 10 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1957 | 7 | 11 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1957 | 7 | 12 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1957 | 7 | 13 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1957 | 7 | 14 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1957 | 7 | 15 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1957 | 7 | 16 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1957 | 7 | 17 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1957 | 7 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1957 | 7 | 19 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1957 | 7 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1957 | 7 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1957 | 7 | 22 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1957 | 7 | 23 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1957 | 7 | 24 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1957 | 7 | 25 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1957 | 7 | 26 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1957 | 7 | 27 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1957 | 7 | 28 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1957 | 7 | 29 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1957 | 7 | 30 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1957 | 7 | 31 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1957 | 8 | 1 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1957 | 8 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1957 | 8 | 3 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1957 | 8 | 4 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1957 | 8 | 5 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1957 | 8 | 6 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1957 | 8 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1957 | 8 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1957 | 8 | 9 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1957 | 8 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1957 | 8 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1957 | 8 | 12 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1957 | 8 | 13 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1957 | 8 | 14 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1957 | 8 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1957 | 8 | 16 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1957 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1957 | 8 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1957 | 8 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1957 | 8 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1957 | 8 | 21 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1957 | 8 | 22 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1957 | 8 | 23 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1957 | 8 | 24 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1957 | 8 | 25 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1957 | 8 | 26 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1957 | 8 | 27 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1957 | 8 | 28 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1957 | 8 | 29 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1957 | 8 | 30 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1957 | 8 | 31 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 9 | 1 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1957 | 9 | 2 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1957 | 9 | 3 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1957 | 9 | 4 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1957 | 9 | 5 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1957 | 9 | 6 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 9 | 7 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1957 | 9 | 8 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1957 | 9 | 9 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1957 | 9 | 10 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 9 | 11 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1957 | 9 | 12 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 9 | 13 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1957 | 9 | 14 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1957 | 9 | 15 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1957 | 9 | 16 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 9 | 17 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1957 | 9 | 18 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1957 | 9 | 19 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1957 | 9 | 20 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1957 | 9 | 21 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1957 | 9 | 22 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1957 | 9 | 23 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 9 | 24 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1957 | 9 | 25 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1957 | 9 | 26 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1957 | 9 | 27 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1957 | 9 | 28 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1957 | 9 | 29 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1957 | 9 | 30 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1957 | 10 | 1 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1957 | 10 | 2 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1957 | 10 | 3 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1957 | 10 | 4 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1957 | 10 | 5 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1957 | 10 | 6 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1957 | 10 | 7 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1957 | 10 | 8 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1957 | 10 | 9 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1957 | 10 | 10 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1957 | 10 | 11 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1957 | 10 | 12 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1957 | 10 | 13 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1957 | 10 | 14 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1957 | 10 | 15 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1957 | 10 | 16 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1957 | 10 | 17 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1957 | 10 | 18 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1957 | 10 | 19 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1957 | 10 | 20 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1957 | 10 | 21 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1957 | 10 | 22 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1957 | 10 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1957 | 10 | 24 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1957 | 10 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1957 | 10 | 26 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1957 | 10 | 27 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1957 | 10 | 28 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1957 | 10 | 29 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1957 | 10 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1957 | 10 | 31 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1957 | 11 | 1 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1957 | 11 | 2 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1957 | 11 | 3 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1957 | 11 | 4 | 370.9388 | 15 | 355.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1957 | 11 | 5 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1957 | 11 | 6 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1957 | 11 | 7 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1957 | 11 | 8 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1957 | 11 | 9 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1957 | 11 | 10 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1957 | 11 | 11 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1957 | 11 | 12 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1957 | 11 | 13 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1957 | 11 | 14 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1957 | 11 | 15 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1957 | 11 | 16 | 305.6327 | 15 | 290.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1957 | 11 | 17 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1957 | 11 | 18 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1957 | 11 | 19 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1957 | 11 | 20 | 582.5306 | 15 | 567.5306 | 28.8349 | 139.3858 | 0.77441 | 28.0605 | 89.27% | 295.6948 | 277.9531 | 6670.8743
1957 | 11 | 21 | 368.3265 | 15 | 353.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1957 | 11 | 22 | 231.1837 | 15 | 216.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1957 | 11 | 23 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1957 | 11 | 24 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1957 | 11 | 25 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1957 | 11 | 26 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1957 | 11 | 27 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1957 | 11 | 28 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1957 | 11 | 29 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1957 | 11 | 30 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1957 | 12 | 1 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1957 | 12 | 2 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1957 | 12 | 3 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1957 | 12 | 4 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1957 | 12 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1957 | 12 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1957 | 12 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1957 | 12 | 8 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1957 | 12 | 9 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1957 | 12 | 10 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1957 | 12 | 11 | 1108.898 | 5 | 1103.898 | 27.7822 | 139.3858 | 0.77441 | 27.0078 | 89.27% | 284.6013 | 267.5252 | 6420.606
1957 | 12 | 12 | 620.4082 | 5 | 615.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1957 | 12 | 13 | 411.4286 | 5 | 406.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1957 | 12 | 14 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1957 | 12 | 15 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1957 | 12 | 16 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1957 | 12 | 17 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1957 | 12 | 18 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1957 | 12 | 19 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1957 | 12 | 20 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1957 | 12 | 21 | 1920 | 5 | 1915 | 26.16 | 139.3858 | 0.77441 | 25.3856 | 89.27% | 267.507 | 251.4565 | 6034.9568
1957 | 12 | 22 | 1384.4898 | 5 | 1379.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
1957 | 12 | 23 | 624.3265 | 5 | 619.3265 | 28.7513 | 139.3858 | 0.77441 | 27.9769 | 89.27% | 294.8139 | 277.1251 | 6651.0019
1957 | 12 | 24 | 446.6939 | 5 | 441.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1957 | 12 | 25 | 310.8571 | 5 | 305.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1957 | 12 | 26 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1957 | 12 | 27 | 1175.5102 | 5 | 1170.5102 | 27.649 | 139.3858 | 0.77441 | 26.8746 | 89.27% | 283.1974 | 266.2056 | 6388.9343
1957 | 12 | 28 | 700.0816 | 5 | 695.0816 | 28.5998 | 139.3858 | 0.77441 | 27.8254 | 89.27% | 293.2173 | 275.6243 | 6614.9831
1957 | 12 | 29 | 453.2245 | 5 | 448.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
1957 | 12 | 30 | 327.8367 | 5 | 322.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1957 | 12 | 31 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1958 | 1 | 1 | 286.0408 | 5 | 281.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1958 | 1 | 2 | 339.5918 | 5 | 334.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1958 | 1 | 3 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1958 | 1 | 4 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1958 | 1 | 5 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1958 | 1 | 6 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1958 | 1 | 7 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1958 | 1 | 8 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1958 | 1 | 9 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1958 | 1 | 10 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1958 | 1 | 11 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1958 | 1 | 12 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1958 | 1 | 13 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1958 | 1 | 14 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1958 | 1 | 15 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1958 | 1 | 16 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1958 | 1 | 17 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1958 | 1 | 18 | 336.9796 | 5 | 331.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1958 | 1 | 19 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1958 | 1 | 20 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1958 | 1 | 21 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1958 | 1 | 22 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1958 | 1 | 23 | 370.9388 | 5 | 365.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1958 | 1 | 24 | 316.0816 | 5 | 311.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1958 | 1 | 25 | 262.5306 | 5 | 257.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1958 | 1 | 26 | 386.6122 | 5 | 381.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1958 | 1 | 27 | 513.3061 | 5 | 508.3061 | 28.9734 | 139.3858 | 0.77441 | 28.199 | 89.27% | 297.1537 | 279.3245 | 6703.788
1958 | 1 | 28 | 403.5918 | 5 | 398.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1958 | 1 | 29 | 327.8367 | 5 | 322.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1958 | 1 | 30 | 280.8163 | 5 | 275.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1958 | 1 | 31 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1958 | 2 | 1 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1958 | 2 | 2 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1958 | 2 | 3 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1958 | 2 | 4 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1958 | 2 | 5 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1958 | 2 | 6 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1958 | 2 | 7 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1958 | 2 | 8 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1958 | 2 | 9 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1958 | 2 | 10 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1958 | 2 | 11 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1958 | 2 | 12 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1958 | 2 | 13 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1958 | 2 | 14 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1958 | 2 | 15 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1958 | 2 | 16 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1958 | 2 | 17 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1958 | 2 | 18 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1958 | 2 | 19 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1958 | 2 | 20 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1958 | 2 | 21 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1958 | 2 | 22 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1958 | 2 | 23 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1958 | 2 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1958 | 2 | 25 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1958 | 2 | 26 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1958 | 2 | 27 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1958 | 2 | 28 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1958 | 3 | 1 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1958 | 3 | 2 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1958 | 3 | 3 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1958 | 3 | 4 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1958 | 3 | 5 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1958 | 3 | 6 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1958 | 3 | 7 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1958 | 3 | 8 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1958 | 3 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1958 | 3 | 10 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1958 | 3 | 11 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1958 | 3 | 12 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1958 | 3 | 13 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1958 | 3 | 14 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1958 | 3 | 15 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1958 | 3 | 16 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1958 | 3 | 17 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1958 | 3 | 18 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1958 | 3 | 19 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1958 | 3 | 20 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1958 | 3 | 21 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1958 | 3 | 22 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1958 | 3 | 23 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1958 | 3 | 24 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1958 | 3 | 25 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1958 | 3 | 26 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1958 | 3 | 27 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1958 | 3 | 28 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1958 | 3 | 29 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1958 | 3 | 30 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1958 | 3 | 31 | 420.5714 | 25 | 395.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1958 | 4 | 1 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1958 | 4 | 2 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1958 | 4 | 3 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1958 | 4 | 4 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
1958 | 4 | 5 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1958 | 4 | 6 | 730.1224 | 25 | 705.1224 | 28.5398 | 139.3858 | 0.77441 | 27.7653 | 89.27% | 292.5842 | 275.0292 | 6600.6998
1958 | 4 | 7 | 710.5306 | 25 | 685.5306 | 28.5789 | 139.3858 | 0.77441 | 27.8045 | 89.27% | 292.9971 | 275.4173 | 6610.015
1958 | 4 | 8 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1958 | 4 | 9 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1958 | 4 | 10 | 416.6531 | 25 | 391.6531 | 29.1667 | 139.3858 | 0.77441 | 28.3923 | 89.27% | 299.1907 | 281.2393 | 6749.7429
1958 | 4 | 11 | 488.4898 | 25 | 463.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
1958 | 4 | 12 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1958 | 4 | 13 | 551.1837 | 25 | 526.1837 | 28.8976 | 139.3858 | 0.77441 | 28.1232 | 89.27% | 296.3554 | 278.5741 | 6685.7786
1958 | 4 | 14 | 745.7959 | 25 | 720.7959 | 28.5084 | 139.3858 | 0.77441 | 27.734 | 89.27% | 292.2539 | 274.7187 | 6593.2476
1958 | 4 | 15 | 834.6122 | 25 | 809.6122 | 28.3308 | 139.3858 | 0.77441 | 27.5564 | 89.27% | 290.382 | 272.9591 | 6551.0187
1958 | 4 | 16 | 1170.2857 | 25 | 1145.2857 | 27.6594 | 139.3858 | 0.77441 | 26.885 | 89.27% | 283.3076 | 266.3091 | 6391.4184
1958 | 4 | 17 | 1528.1633 | 25 | 1503.1633 | 26.9437 | 139.3858 | 0.77441 | 26.1693 | 89.27% | 275.7651 | 259.2192 | 6221.2608
1958 | 4 | 18 | 1658.7755 | 25 | 1633.7755 | 26.6824 | 139.3858 | 0.77441 | 25.908 | 89.27% | 273.0124 | 256.6316 | 6159.1594
1958 | 4 | 19 | 1671.8367 | 25 | 1646.8367 | 26.6563 | 139.3858 | 0.77441 | 25.8819 | 89.27% | 272.7371 | 256.3729 | 6152.9493
1958 | 4 | 20 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1958 | 4 | 21 | 1170.2857 | 25 | 1145.2857 | 27.6594 | 139.3858 | 0.77441 | 26.885 | 89.27% | 283.3076 | 266.3091 | 6391.4184
1958 | 4 | 22 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
1958 | 4 | 23 | 2115.9184 | 25 | 2090.9184 | 25.7682 | 139.3858 | 0.77441 | 24.9938 | 89.27% | 263.3779 | 247.5752 | 5941.8048
1958 | 4 | 24 | 1580.4082 | 25 | 1555.4082 | 26.8392 | 139.3858 | 0.77441 | 26.0648 | 89.27% | 274.664 | 258.1842 | 6196.4202
1958 | 4 | 25 | 1082.7755 | 25 | 1057.7755 | 27.8344 | 139.3858 | 0.77441 | 27.06 | 89.27% | 285.1519 | 268.0428 | 6433.0262
1958 | 4 | 26 | 719.6735 | 25 | 694.6735 | 28.5607 | 139.3858 | 0.77441 | 27.7862 | 89.27% | 292.8044 | 275.2362 | 6605.6679
1958 | 4 | 27 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1958 | 4 | 28 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1958 | 4 | 29 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1958 | 4 | 30 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1958 | 5 | 1 | 940.4082 | 25 | 915.4082 | 28.1192 | 139.3858 | 0.77441 | 27.3448 | 89.27% | 288.1523 | 270.8632 | 6500.7167
1958 | 5 | 2 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1958 | 5 | 3 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1958 | 5 | 4 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1958 | 5 | 5 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1958 | 5 | 6 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1958 | 5 | 7 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1958 | 5 | 8 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1958 | 5 | 9 | 569.4694 | 25 | 544.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
1958 | 5 | 10 | 410.1224 | 25 | 385.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1958 | 5 | 11 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1958 | 5 | 12 | 594.2857 | 25 | 569.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
1958 | 5 | 13 | 564.2449 | 25 | 539.2449 | 28.8715 | 139.3858 | 0.77441 | 28.0971 | 89.27% | 296.0802 | 278.3154 | 6679.5685
1958 | 5 | 14 | 384 | 25 | 359 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
1958 | 5 | 15 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1958 | 5 | 16 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1958 | 5 | 17 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1958 | 5 | 18 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1958 | 5 | 19 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1958 | 5 | 20 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1958 | 5 | 21 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1958 | 5 | 22 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1958 | 5 | 23 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1958 | 5 | 24 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1958 | 5 | 25 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1958 | 5 | 26 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1958 | 5 | 27 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1958 | 5 | 28 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1958 | 5 | 29 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1958 | 5 | 30 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1958 | 5 | 31 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1958 | 6 | 1 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1958 | 6 | 2 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1958 | 6 | 3 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1958 | 6 | 4 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1958 | 6 | 5 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1958 | 6 | 6 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1958 | 6 | 7 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1958 | 6 | 8 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1958 | 6 | 9 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1958 | 6 | 10 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1958 | 6 | 11 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1958 | 6 | 12 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1958 | 6 | 13 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1958 | 6 | 14 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1958 | 6 | 15 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1958 | 6 | 16 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1958 | 6 | 17 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1958 | 6 | 18 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1958 | 6 | 19 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1958 | 6 | 20 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1958 | 6 | 21 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1958 | 6 | 22 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1958 | 6 | 23 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1958 | 6 | 24 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1958 | 6 | 25 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1958 | 6 | 26 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1958 | 6 | 27 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1958 | 6 | 28 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1958 | 6 | 29 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1958 | 6 | 30 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1958 | 7 | 1 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1958 | 7 | 2 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1958 | 7 | 3 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1958 | 7 | 4 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1958 | 7 | 5 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 7 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 7 | 7 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 7 | 8 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 7 | 9 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1958 | 7 | 10 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1958 | 7 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1958 | 7 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1958 | 7 | 13 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1958 | 7 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1958 | 7 | 15 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1958 | 7 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1958 | 7 | 17 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1958 | 7 | 18 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1958 | 7 | 19 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1958 | 7 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1958 | 7 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1958 | 7 | 22 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1958 | 7 | 23 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1958 | 7 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1958 | 7 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1958 | 7 | 26 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1958 | 7 | 27 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1958 | 7 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1958 | 7 | 29 | 333.0612 | 5 | 328.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1958 | 7 | 30 | 364.4082 | 5 | 359.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1958 | 7 | 31 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1958 | 8 | 1 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1958 | 8 | 2 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1958 | 8 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1958 | 8 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1958 | 8 | 5 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1958 | 8 | 6 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1958 | 8 | 7 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1958 | 8 | 8 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1958 | 8 | 9 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1958 | 8 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1958 | 8 | 11 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1958 | 8 | 12 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1958 | 8 | 13 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1958 | 8 | 14 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1958 | 8 | 15 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1958 | 8 | 16 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1958 | 8 | 17 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1958 | 8 | 18 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1958 | 8 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1958 | 8 | 20 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1958 | 8 | 21 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1958 | 8 | 22 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1958 | 8 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 8 | 24 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 8 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 8 | 26 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1958 | 8 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1958 | 8 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1958 | 8 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1958 | 8 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1958 | 8 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1958 | 9 | 1 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1958 | 9 | 2 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1958 | 9 | 3 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1958 | 9 | 4 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1958 | 9 | 5 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1958 | 9 | 6 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1958 | 9 | 7 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1958 | 9 | 8 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1958 | 9 | 9 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1958 | 9 | 10 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1958 | 9 | 11 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1958 | 9 | 12 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1958 | 9 | 13 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1958 | 9 | 14 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1958 | 9 | 15 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1958 | 9 | 16 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1958 | 9 | 17 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1958 | 9 | 18 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1958 | 9 | 19 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1958 | 9 | 20 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1958 | 9 | 21 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1958 | 9 | 22 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1958 | 9 | 23 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1958 | 9 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1958 | 9 | 25 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1958 | 9 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1958 | 9 | 27 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1958 | 9 | 28 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1958 | 9 | 29 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1958 | 9 | 30 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1958 | 10 | 1 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1958 | 10 | 2 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1958 | 10 | 3 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1958 | 10 | 4 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1958 | 10 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1958 | 10 | 6 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1958 | 10 | 7 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1958 | 10 | 8 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1958 | 10 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1958 | 10 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1958 | 10 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1958 | 10 | 12 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1958 | 10 | 13 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1958 | 10 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1958 | 10 | 15 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1958 | 10 | 16 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1958 | 10 | 17 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1958 | 10 | 18 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1958 | 10 | 19 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1958 | 10 | 20 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1958 | 10 | 21 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1958 | 10 | 22 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1958 | 10 | 23 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1958 | 10 | 24 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1958 | 10 | 25 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1958 | 10 | 26 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1958 | 10 | 27 | 404.898 | 15 | 389.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1958 | 10 | 28 | 407.5102 | 15 | 392.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1958 | 10 | 29 | 449.3061 | 15 | 434.3061 | 29.1014 | 139.3858 | 0.77441 | 28.327 | 89.27% | 298.5026 | 280.5924 | 6734.2176
1958 | 10 | 30 | 364.4082 | 15 | 349.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1958 | 10 | 31 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1958 | 11 | 1 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1958 | 11 | 2 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1958 | 11 | 3 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1958 | 11 | 4 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1958 | 11 | 5 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1958 | 11 | 6 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1958 | 11 | 7 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1958 | 11 | 8 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1958 | 11 | 9 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1958 | 11 | 10 | 242.9388 | 15 | 227.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1958 | 11 | 11 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1958 | 11 | 12 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1958 | 11 | 13 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1958 | 11 | 14 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1958 | 11 | 15 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1958 | 11 | 16 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1958 | 11 | 17 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1958 | 11 | 18 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1958 | 11 | 19 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1958 | 11 | 20 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1958 | 11 | 21 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1958 | 11 | 22 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1958 | 11 | 23 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1958 | 11 | 24 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1958 | 11 | 25 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1958 | 11 | 26 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1958 | 11 | 27 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1958 | 11 | 28 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1958 | 11 | 29 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1958 | 11 | 30 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1958 | 12 | 1 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1958 | 12 | 2 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1958 | 12 | 3 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1958 | 12 | 4 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1958 | 12 | 5 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1958 | 12 | 6 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1958 | 12 | 7 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1958 | 12 | 8 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1958 | 12 | 9 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1958 | 12 | 10 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1958 | 12 | 11 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1958 | 12 | 12 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1958 | 12 | 13 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1958 | 12 | 14 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1958 | 12 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1958 | 12 | 16 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1958 | 12 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1958 | 12 | 18 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1958 | 12 | 19 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1958 | 12 | 20 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1958 | 12 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1958 | 12 | 22 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1958 | 12 | 23 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1958 | 12 | 24 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1958 | 12 | 25 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1958 | 12 | 26 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1958 | 12 | 27 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1958 | 12 | 28 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1958 | 12 | 29 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1958 | 12 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1958 | 12 | 31 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1959 | 1 | 1 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1959 | 1 | 2 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1959 | 1 | 3 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1959 | 1 | 4 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1959 | 1 | 5 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1959 | 1 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1959 | 1 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1959 | 1 | 8 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1959 | 1 | 9 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1959 | 1 | 10 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1959 | 1 | 11 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1959 | 1 | 12 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1959 | 1 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1959 | 1 | 14 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 1 | 15 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 1 | 16 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1959 | 1 | 17 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1959 | 1 | 18 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1959 | 1 | 19 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1959 | 1 | 20 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1959 | 1 | 21 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1959 | 1 | 22 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1959 | 1 | 23 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1959 | 1 | 24 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1959 | 1 | 25 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1959 | 1 | 26 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1959 | 1 | 27 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1959 | 1 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1959 | 1 | 29 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1959 | 1 | 30 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1959 | 1 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1959 | 2 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1959 | 2 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1959 | 2 | 3 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1959 | 2 | 4 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1959 | 2 | 5 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1959 | 2 | 6 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1959 | 2 | 7 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1959 | 2 | 8 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1959 | 2 | 9 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1959 | 2 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1959 | 2 | 11 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1959 | 2 | 12 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1959 | 2 | 13 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1959 | 2 | 14 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1959 | 2 | 15 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1959 | 2 | 16 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1959 | 2 | 17 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1959 | 2 | 18 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1959 | 2 | 19 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1959 | 2 | 20 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1959 | 2 | 21 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 2 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1959 | 2 | 23 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1959 | 2 | 24 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 2 | 25 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 2 | 26 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 2 | 27 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 2 | 28 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 3 | 1 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1959 | 3 | 2 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1959 | 3 | 3 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1959 | 3 | 4 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1959 | 3 | 5 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1959 | 3 | 6 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1959 | 3 | 7 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1959 | 3 | 8 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1959 | 3 | 9 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1959 | 3 | 10 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1959 | 3 | 11 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1959 | 3 | 12 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1959 | 3 | 13 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1959 | 3 | 14 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1959 | 3 | 15 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1959 | 3 | 16 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1959 | 3 | 17 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1959 | 3 | 18 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1959 | 3 | 19 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1959 | 3 | 20 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1959 | 3 | 21 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1959 | 3 | 22 | 361.7959 | 25 | 336.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1959 | 3 | 23 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1959 | 3 | 24 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1959 | 3 | 25 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1959 | 3 | 26 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1959 | 3 | 27 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1959 | 3 | 28 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1959 | 3 | 29 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1959 | 3 | 30 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1959 | 3 | 31 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1959 | 4 | 1 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1959 | 4 | 2 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1959 | 4 | 3 | 1985.3061 | 25 | 1960.3061 | 26.0294 | 139.3858 | 0.77441 | 25.255 | 89.27% | 266.1306 | 250.1628 | 6003.9061
1959 | 4 | 4 | 2050.6122 | 25 | 2025.6122 | 25.8988 | 139.3858 | 0.77441 | 25.1244 | 89.27% | 264.7542 | 248.869 | 5972.8555
1959 | 4 | 5 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1959 | 4 | 6 | 1345.3061 | 25 | 1320.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
1959 | 4 | 7 | 1136.3265 | 25 | 1111.3265 | 27.7273 | 139.3858 | 0.77441 | 26.9529 | 89.27% | 284.0233 | 266.9819 | 6407.5647
1959 | 4 | 8 | 958.6939 | 25 | 933.6939 | 28.0826 | 139.3858 | 0.77441 | 27.3082 | 89.27% | 287.767 | 270.5009 | 6492.0225
1959 | 4 | 9 | 1093.2245 | 25 | 1068.2245 | 27.8136 | 139.3858 | 0.77441 | 27.0391 | 89.27% | 284.9317 | 267.8358 | 6428.0581
1959 | 4 | 10 | 903.8367 | 25 | 878.8367 | 28.1923 | 139.3858 | 0.77441 | 27.4179 | 89.27% | 288.9231 | 271.5877 | 6518.105
1959 | 4 | 11 | 941.7143 | 25 | 916.7143 | 28.1166 | 139.3858 | 0.77441 | 27.3422 | 89.27% | 288.1248 | 270.8373 | 6500.0957
1959 | 4 | 12 | 773.2245 | 25 | 748.2245 | 28.4536 | 139.3858 | 0.77441 | 27.6791 | 89.27% | 291.6758 | 274.1753 | 6580.2064
1959 | 4 | 13 | 617.7959 | 25 | 592.7959 | 28.7644 | 139.3858 | 0.77441 | 27.99 | 89.27% | 294.9515 | 277.2545 | 6654.1069
1959 | 4 | 14 | 535.5102 | 25 | 510.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1959 | 4 | 15 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1959 | 4 | 16 | 489.7959 | 25 | 464.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
1959 | 4 | 17 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
1959 | 4 | 18 | 508.0816 | 25 | 483.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
1959 | 4 | 19 | 467.5918 | 25 | 442.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1959 | 4 | 20 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1959 | 4 | 21 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1959 | 4 | 22 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1959 | 4 | 23 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1959 | 4 | 24 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1959 | 4 | 25 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1959 | 4 | 26 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1959 | 4 | 27 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1959 | 4 | 28 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1959 | 4 | 29 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1959 | 4 | 30 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1959 | 5 | 1 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1959 | 5 | 2 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1959 | 5 | 3 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1959 | 5 | 4 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1959 | 5 | 5 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1959 | 5 | 6 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1959 | 5 | 7 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1959 | 5 | 8 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1959 | 5 | 9 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1959 | 5 | 10 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1959 | 5 | 11 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1959 | 5 | 12 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1959 | 5 | 13 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1959 | 5 | 14 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1959 | 5 | 15 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1959 | 5 | 16 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1959 | 5 | 17 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1959 | 5 | 18 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1959 | 5 | 19 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1959 | 5 | 20 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1959 | 5 | 21 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1959 | 5 | 22 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1959 | 5 | 23 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1959 | 5 | 24 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1959 | 5 | 25 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1959 | 5 | 26 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1959 | 5 | 27 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1959 | 5 | 28 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1959 | 5 | 29 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1959 | 5 | 30 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1959 | 5 | 31 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1959 | 6 | 1 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1959 | 6 | 2 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1959 | 6 | 3 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1959 | 6 | 4 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1959 | 6 | 5 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1959 | 6 | 6 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1959 | 6 | 7 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1959 | 6 | 8 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1959 | 6 | 9 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1959 | 6 | 10 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1959 | 6 | 11 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1959 | 6 | 12 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1959 | 6 | 13 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1959 | 6 | 14 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1959 | 6 | 15 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1959 | 6 | 16 | 557.7143 | 25 | 532.7143 | 28.8846 | 139.3858 | 0.77441 | 28.1102 | 89.27% | 296.2178 | 278.4447 | 6682.6735
1959 | 6 | 17 | 454.5306 | 25 | 429.5306 | 29.0909 | 139.3858 | 0.77441 | 28.3165 | 89.27% | 298.3924 | 280.4889 | 6731.7336
1959 | 6 | 18 | 512 | 25 | 487 | 28.976 | 139.3858 | 0.77441 | 28.2016 | 89.27% | 297.1812 | 279.3504 | 6704.409
1959 | 6 | 19 | 773.2245 | 25 | 748.2245 | 28.4536 | 139.3858 | 0.77441 | 27.6791 | 89.27% | 291.6758 | 274.1753 | 6580.2064
1959 | 6 | 20 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1959 | 6 | 21 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1959 | 6 | 22 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1959 | 6 | 23 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1959 | 6 | 24 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1959 | 6 | 25 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1959 | 6 | 26 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1959 | 6 | 27 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1959 | 6 | 28 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1959 | 6 | 29 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1959 | 6 | 30 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1959 | 7 | 1 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1959 | 7 | 2 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1959 | 7 | 3 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1959 | 7 | 4 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1959 | 7 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1959 | 7 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1959 | 7 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1959 | 7 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1959 | 7 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1959 | 7 | 10 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1959 | 7 | 11 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1959 | 7 | 12 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1959 | 7 | 13 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1959 | 7 | 14 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1959 | 7 | 15 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1959 | 7 | 16 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1959 | 7 | 17 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1959 | 7 | 18 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1959 | 7 | 19 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1959 | 7 | 20 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1959 | 7 | 21 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1959 | 7 | 22 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1959 | 7 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1959 | 7 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1959 | 7 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1959 | 7 | 26 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1959 | 7 | 27 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1959 | 7 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1959 | 7 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1959 | 7 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1959 | 7 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1959 | 8 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1959 | 8 | 2 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1959 | 8 | 3 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1959 | 8 | 4 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1959 | 8 | 5 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1959 | 8 | 6 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1959 | 8 | 7 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1959 | 8 | 8 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1959 | 8 | 9 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1959 | 8 | 10 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1959 | 8 | 11 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1959 | 8 | 12 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1959 | 8 | 13 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1959 | 8 | 14 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1959 | 8 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1959 | 8 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1959 | 8 | 17 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1959 | 8 | 18 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1959 | 8 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1959 | 8 | 20 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1959 | 8 | 21 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1959 | 8 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1959 | 8 | 23 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1959 | 8 | 24 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1959 | 8 | 25 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1959 | 8 | 26 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1959 | 8 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1959 | 8 | 28 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1959 | 8 | 29 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1959 | 8 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1959 | 8 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1959 | 9 | 1 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1959 | 9 | 2 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1959 | 9 | 3 | 352.6531 | 15 | 337.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1959 | 9 | 4 | 246.8571 | 15 | 231.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
1959 | 9 | 5 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1959 | 9 | 6 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1959 | 9 | 7 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1959 | 9 | 8 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1959 | 9 | 9 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1959 | 9 | 10 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1959 | 9 | 11 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1959 | 9 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1959 | 9 | 13 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1959 | 9 | 14 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1959 | 9 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1959 | 9 | 16 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1959 | 9 | 17 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1959 | 9 | 18 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1959 | 9 | 19 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1959 | 9 | 20 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1959 | 9 | 21 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1959 | 9 | 22 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1959 | 9 | 23 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1959 | 9 | 24 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1959 | 9 | 25 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1959 | 9 | 26 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1959 | 9 | 27 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1959 | 9 | 28 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1959 | 9 | 29 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1959 | 9 | 30 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1959 | 10 | 1 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1959 | 10 | 2 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1959 | 10 | 3 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1959 | 10 | 4 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1959 | 10 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1959 | 10 | 6 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1959 | 10 | 7 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1959 | 10 | 8 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1959 | 10 | 9 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1959 | 10 | 10 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1959 | 10 | 11 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1959 | 10 | 12 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1959 | 10 | 13 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1959 | 10 | 14 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1959 | 10 | 15 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1959 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1959 | 10 | 17 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1959 | 10 | 18 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1959 | 10 | 19 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1959 | 10 | 20 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1959 | 10 | 21 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1959 | 10 | 22 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1959 | 10 | 23 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1959 | 10 | 24 | 535.5102 | 15 | 520.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1959 | 10 | 25 | 2194.2857 | 15 | 2179.2857 | 25.6114 | 139.3858 | 0.77441 | 24.837 | 89.27% | 261.7262 | 246.0227 | 5904.544
1959 | 10 | 26 | 961.3061 | 15 | 946.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1959 | 10 | 27 | 491.102 | 15 | 476.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1959 | 10 | 28 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1959 | 10 | 29 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1959 | 10 | 30 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1959 | 10 | 31 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1959 | 11 | 1 | 344.8163 | 15 | 329.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1959 | 11 | 2 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1959 | 11 | 3 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1959 | 11 | 4 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1959 | 11 | 5 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1959 | 11 | 6 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1959 | 11 | 7 | 607.3469 | 15 | 592.3469 | 28.7853 | 139.3858 | 0.77441 | 28.0109 | 89.27% | 295.1718 | 277.4615 | 6659.075
1959 | 11 | 8 | 615.1837 | 15 | 600.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1959 | 11 | 9 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1959 | 11 | 10 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1959 | 11 | 11 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1959 | 11 | 12 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1959 | 11 | 13 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1959 | 11 | 14 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1959 | 11 | 15 | 427.102 | 15 | 412.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1959 | 11 | 16 | 360.4898 | 15 | 345.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1959 | 11 | 17 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1959 | 11 | 18 | 391.8367 | 15 | 376.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1959 | 11 | 19 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1959 | 11 | 20 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1959 | 11 | 21 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1959 | 11 | 22 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1959 | 11 | 23 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1959 | 11 | 24 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1959 | 11 | 25 | 1488.9796 | 15 | 1473.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1959 | 11 | 26 | 1410.6122 | 15 | 1395.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1959 | 11 | 27 | 675.2653 | 15 | 660.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1959 | 11 | 28 | 855.5102 | 15 | 840.5102 | 28.289 | 139.3858 | 0.77441 | 27.5146 | 89.27% | 289.9416 | 272.5451 | 6541.0825
1959 | 11 | 29 | 1619.5918 | 15 | 1604.5918 | 26.7608 | 139.3858 | 0.77441 | 25.9864 | 89.27% | 273.8382 | 257.4079 | 6177.7898
1959 | 11 | 30 | 808.4898 | 15 | 793.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
1959 | 12 | 1 | 509.3878 | 5 | 504.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1959 | 12 | 2 | 387.9184 | 5 | 382.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1959 | 12 | 3 | 338.2857 | 5 | 333.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1959 | 12 | 4 | 312.1633 | 5 | 307.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1959 | 12 | 5 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1959 | 12 | 6 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1959 | 12 | 7 | 411.4286 | 5 | 406.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1959 | 12 | 8 | 625.6327 | 5 | 620.6327 | 28.7487 | 139.3858 | 0.77441 | 27.9743 | 89.27% | 294.7864 | 277.0992 | 6650.3808
1959 | 12 | 9 | 410.1224 | 5 | 405.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1959 | 12 | 10 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1959 | 12 | 11 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1959 | 12 | 12 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1959 | 12 | 13 | 468.898 | 5 | 463.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1959 | 12 | 14 | 566.8571 | 5 | 561.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1959 | 12 | 15 | 512 | 5 | 507 | 28.976 | 139.3858 | 0.77441 | 28.2016 | 89.27% | 297.1812 | 279.3504 | 6704.409
1959 | 12 | 16 | 309.551 | 5 | 304.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1959 | 12 | 17 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1959 | 12 | 18 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1959 | 12 | 19 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1959 | 12 | 20 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1959 | 12 | 21 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1959 | 12 | 22 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1959 | 12 | 23 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1959 | 12 | 24 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1959 | 12 | 25 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1959 | 12 | 26 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1959 | 12 | 27 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1959 | 12 | 28 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1959 | 12 | 29 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1959 | 12 | 30 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1959 | 12 | 31 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1960 | 1 | 1 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1960 | 1 | 2 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1960 | 1 | 3 | 280.8163 | 5 | 275.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1960 | 1 | 4 | 561.6327 | 5 | 556.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1960 | 1 | 5 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1960 | 1 | 6 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1960 | 1 | 7 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1960 | 1 | 8 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1960 | 1 | 9 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1960 | 1 | 10 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1960 | 1 | 11 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1960 | 1 | 12 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1960 | 1 | 13 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1960 | 1 | 14 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1960 | 1 | 15 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1960 | 1 | 16 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1960 | 1 | 17 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1960 | 1 | 18 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1960 | 1 | 19 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1960 | 1 | 20 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1960 | 1 | 21 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1960 | 1 | 22 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1960 | 1 | 23 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1960 | 1 | 24 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1960 | 1 | 25 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1960 | 1 | 26 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1960 | 1 | 27 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1960 | 1 | 28 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1960 | 1 | 29 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1960 | 1 | 30 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1960 | 1 | 31 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1960 | 2 | 1 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1960 | 2 | 2 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1960 | 2 | 3 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1960 | 2 | 4 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1960 | 2 | 5 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1960 | 2 | 6 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1960 | 2 | 7 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1960 | 2 | 8 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1960 | 2 | 9 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1960 | 2 | 10 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1960 | 2 | 11 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1960 | 2 | 12 | 803.2653 | 5 | 798.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1960 | 2 | 13 | 566.8571 | 5 | 561.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1960 | 2 | 14 | 395.7551 | 5 | 390.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1960 | 2 | 15 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1960 | 2 | 16 | 266.449 | 5 | 261.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1960 | 2 | 17 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1960 | 2 | 18 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1960 | 2 | 19 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1960 | 2 | 20 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1960 | 2 | 21 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1960 | 2 | 22 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1960 | 2 | 23 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1960 | 2 | 24 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1960 | 2 | 25 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1960 | 2 | 26 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1960 | 2 | 27 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1960 | 2 | 28 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1960 | 2 | 29 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1960 | 3 | 1 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1960 | 3 | 2 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1960 | 3 | 3 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1960 | 3 | 4 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1960 | 3 | 5 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1960 | 3 | 6 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1960 | 3 | 7 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1960 | 3 | 8 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1960 | 3 | 9 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1960 | 3 | 10 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1960 | 3 | 11 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1960 | 3 | 12 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1960 | 3 | 13 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1960 | 3 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1960 | 3 | 15 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1960 | 3 | 16 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1960 | 3 | 17 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1960 | 3 | 18 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1960 | 3 | 19 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1960 | 3 | 20 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1960 | 3 | 21 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1960 | 3 | 22 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1960 | 3 | 23 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1960 | 3 | 24 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1960 | 3 | 25 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1960 | 3 | 26 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1960 | 3 | 27 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1960 | 3 | 28 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1960 | 3 | 29 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1960 | 3 | 30 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1960 | 3 | 31 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1960 | 4 | 1 | 850.2857 | 25 | 825.2857 | 28.2994 | 139.3858 | 0.77441 | 27.525 | 89.27% | 290.0517 | 272.6486 | 6543.5666
1960 | 4 | 2 | 916.898 | 25 | 891.898 | 28.1662 | 139.3858 | 0.77441 | 27.3918 | 89.27% | 288.6478 | 271.329 | 6511.8949
1960 | 4 | 3 | 808.4898 | 25 | 783.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
1960 | 4 | 4 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1960 | 4 | 5 | 2076.7347 | 25 | 2051.7347 | 25.8465 | 139.3858 | 0.77441 | 25.0721 | 89.27% | 264.2037 | 248.3515 | 5960.4352
1960 | 4 | 6 | 2142.0408 | 25 | 2117.0408 | 25.7159 | 139.3858 | 0.77441 | 24.9415 | 89.27% | 262.8273 | 247.0577 | 5929.3846
1960 | 4 | 7 | 1098.449 | 25 | 1073.449 | 27.8031 | 139.3858 | 0.77441 | 27.0287 | 89.27% | 284.8215 | 267.7323 | 6425.5741
1960 | 4 | 8 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1960 | 4 | 9 | 650.449 | 25 | 625.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
1960 | 4 | 10 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1960 | 4 | 11 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1960 | 4 | 12 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1960 | 4 | 13 | 956.0816 | 25 | 931.0816 | 28.0878 | 139.3858 | 0.77441 | 27.3134 | 89.27% | 287.822 | 270.5527 | 6493.2645
1960 | 4 | 14 | 990.0408 | 25 | 965.0408 | 28.0199 | 139.3858 | 0.77441 | 27.2455 | 89.27% | 287.1063 | 269.8799 | 6477.1182
1960 | 4 | 15 | 984.8163 | 25 | 959.8163 | 28.0304 | 139.3858 | 0.77441 | 27.256 | 89.27% | 287.2164 | 269.9834 | 6479.6022
1960 | 4 | 16 | 1345.3061 | 25 | 1320.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
1960 | 4 | 17 | 1240.8163 | 25 | 1215.8163 | 27.5184 | 139.3858 | 0.77441 | 26.744 | 89.27% | 281.8211 | 264.9118 | 6357.8836
1960 | 4 | 18 | 1168.9796 | 25 | 1143.9796 | 27.662 | 139.3858 | 0.77441 | 26.8876 | 89.27% | 283.3351 | 266.335 | 6392.0394
1960 | 4 | 19 | 1031.8367 | 25 | 1006.8367 | 27.9363 | 139.3858 | 0.77441 | 27.1619 | 89.27% | 286.2254 | 269.0519 | 6457.2458
1960 | 4 | 20 | 726.2041 | 25 | 701.2041 | 28.5476 | 139.3858 | 0.77441 | 27.7732 | 89.27% | 292.6668 | 275.1068 | 6602.5628
1960 | 4 | 21 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1960 | 4 | 22 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1960 | 4 | 23 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1960 | 4 | 24 | 474.1224 | 25 | 449.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
1960 | 4 | 25 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1960 | 4 | 26 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1960 | 4 | 27 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1960 | 4 | 28 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1960 | 4 | 29 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1960 | 4 | 30 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1960 | 5 | 1 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1960 | 5 | 2 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1960 | 5 | 3 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1960 | 5 | 4 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1960 | 5 | 5 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1960 | 5 | 6 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1960 | 5 | 7 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1960 | 5 | 8 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1960 | 5 | 9 | 777.1429 | 25 | 752.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1960 | 5 | 10 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1960 | 5 | 11 | 773.2245 | 25 | 748.2245 | 28.4536 | 139.3858 | 0.77441 | 27.6791 | 89.27% | 291.6758 | 274.1753 | 6580.2064
1960 | 5 | 12 | 690.9388 | 25 | 665.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
1960 | 5 | 13 | 986.1224 | 25 | 961.1224 | 28.0278 | 139.3858 | 0.77441 | 27.2533 | 89.27% | 287.1889 | 269.9576 | 6478.9812
1960 | 5 | 14 | 1724.0816 | 25 | 1699.0816 | 26.5518 | 139.3858 | 0.77441 | 25.7774 | 89.27% | 271.636 | 255.3379 | 6128.1088
1960 | 5 | 15 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1960 | 5 | 16 | 855.5102 | 25 | 830.5102 | 28.289 | 139.3858 | 0.77441 | 27.5146 | 89.27% | 289.9416 | 272.5451 | 6541.0825
1960 | 5 | 17 | 576 | 25 | 551 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1960 | 5 | 18 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1960 | 5 | 19 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1960 | 5 | 20 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1960 | 5 | 21 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1960 | 5 | 22 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1960 | 5 | 23 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1960 | 5 | 24 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1960 | 5 | 25 | 939.102 | 25 | 914.102 | 28.1218 | 139.3858 | 0.77441 | 27.3474 | 89.27% | 288.1799 | 270.8891 | 6501.3377
1960 | 5 | 26 | 625.6327 | 25 | 600.6327 | 28.7487 | 139.3858 | 0.77441 | 27.9743 | 89.27% | 294.7864 | 277.0992 | 6650.3808
1960 | 5 | 27 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1960 | 5 | 28 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1960 | 5 | 29 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1960 | 5 | 30 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1960 | 5 | 31 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1960 | 6 | 1 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1960 | 6 | 2 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1960 | 6 | 3 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1960 | 6 | 4 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1960 | 6 | 5 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1960 | 6 | 6 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1960 | 6 | 7 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1960 | 6 | 8 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1960 | 6 | 9 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1960 | 6 | 10 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1960 | 6 | 11 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1960 | 6 | 12 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1960 | 6 | 13 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1960 | 6 | 14 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1960 | 6 | 15 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1960 | 6 | 16 | 581.2245 | 25 | 556.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1960 | 6 | 17 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1960 | 6 | 18 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1960 | 6 | 19 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1960 | 6 | 20 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1960 | 6 | 21 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1960 | 6 | 22 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1960 | 6 | 23 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1960 | 6 | 24 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1960 | 6 | 25 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1960 | 6 | 26 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1960 | 6 | 27 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1960 | 6 | 28 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1960 | 6 | 29 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1960 | 6 | 30 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1960 | 7 | 1 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1960 | 7 | 2 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1960 | 7 | 3 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1960 | 7 | 4 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1960 | 7 | 5 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1960 | 7 | 6 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1960 | 7 | 7 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1960 | 7 | 8 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1960 | 7 | 9 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1960 | 7 | 10 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1960 | 7 | 11 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1960 | 7 | 12 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1960 | 7 | 13 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1960 | 7 | 14 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1960 | 7 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1960 | 7 | 16 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1960 | 7 | 17 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1960 | 7 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1960 | 7 | 19 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1960 | 7 | 20 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1960 | 7 | 21 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1960 | 7 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1960 | 7 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1960 | 7 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1960 | 7 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1960 | 7 | 26 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1960 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1960 | 7 | 28 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 7 | 29 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 7 | 30 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 7 | 31 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1960 | 8 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1960 | 8 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1960 | 8 | 3 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1960 | 8 | 4 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1960 | 8 | 5 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1960 | 8 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1960 | 8 | 7 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1960 | 8 | 8 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1960 | 8 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 8 | 10 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 8 | 11 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 8 | 12 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1960 | 8 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1960 | 8 | 14 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1960 | 8 | 15 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1960 | 8 | 16 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 8 | 17 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1960 | 8 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1960 | 8 | 19 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1960 | 8 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1960 | 8 | 21 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1960 | 8 | 22 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1960 | 8 | 23 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1960 | 8 | 24 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1960 | 8 | 25 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1960 | 8 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1960 | 8 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1960 | 8 | 28 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1960 | 8 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1960 | 8 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1960 | 8 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1960 | 9 | 1 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1960 | 9 | 2 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1960 | 9 | 3 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1960 | 9 | 4 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1960 | 9 | 5 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1960 | 9 | 6 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1960 | 9 | 7 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1960 | 9 | 8 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1960 | 9 | 9 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1960 | 9 | 10 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1960 | 9 | 11 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1960 | 9 | 12 | 555.102 | 15 | 540.102 | 28.8898 | 139.3858 | 0.77441 | 28.1154 | 89.27% | 296.2729 | 278.4965 | 6683.9156
1960 | 9 | 13 | 803.2653 | 15 | 788.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1960 | 9 | 14 | 338.2857 | 15 | 323.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1960 | 9 | 15 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1960 | 9 | 16 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1960 | 9 | 17 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1960 | 9 | 18 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1960 | 9 | 19 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1960 | 9 | 20 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1960 | 9 | 21 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1960 | 9 | 22 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1960 | 9 | 23 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1960 | 9 | 24 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1960 | 9 | 25 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1960 | 9 | 26 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1960 | 9 | 27 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1960 | 9 | 28 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1960 | 9 | 29 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1960 | 9 | 30 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1960 | 10 | 1 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1960 | 10 | 2 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1960 | 10 | 3 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1960 | 10 | 4 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1960 | 10 | 5 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1960 | 10 | 6 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1960 | 10 | 7 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1960 | 10 | 8 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1960 | 10 | 9 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1960 | 10 | 10 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1960 | 10 | 11 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1960 | 10 | 12 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1960 | 10 | 13 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1960 | 10 | 14 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1960 | 10 | 15 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1960 | 10 | 16 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1960 | 10 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1960 | 10 | 18 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1960 | 10 | 19 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1960 | 10 | 20 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1960 | 10 | 21 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1960 | 10 | 22 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1960 | 10 | 23 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1960 | 10 | 24 | 444.0816 | 15 | 429.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1960 | 10 | 25 | 979.5918 | 15 | 964.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1960 | 10 | 26 | 463.6735 | 15 | 448.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1960 | 10 | 27 | 263.8367 | 15 | 248.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1960 | 10 | 28 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1960 | 10 | 29 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1960 | 10 | 30 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1960 | 10 | 31 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1960 | 11 | 1 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1960 | 11 | 2 | 809.7959 | 15 | 794.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
1960 | 11 | 3 | 528.9796 | 15 | 513.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1960 | 11 | 4 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1960 | 11 | 5 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1960 | 11 | 6 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1960 | 11 | 7 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1960 | 11 | 8 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1960 | 11 | 9 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1960 | 11 | 10 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1960 | 11 | 11 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1960 | 11 | 12 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1960 | 11 | 13 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1960 | 11 | 14 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1960 | 11 | 15 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1960 | 11 | 16 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1960 | 11 | 17 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1960 | 11 | 18 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1960 | 11 | 19 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1960 | 11 | 20 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1960 | 11 | 21 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1960 | 11 | 22 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1960 | 11 | 23 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1960 | 11 | 24 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1960 | 11 | 25 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1960 | 11 | 26 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1960 | 11 | 27 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1960 | 11 | 28 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1960 | 11 | 29 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1960 | 11 | 30 | 483.2653 | 15 | 468.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1960 | 12 | 1 | 329.1429 | 5 | 324.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1960 | 12 | 2 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1960 | 12 | 3 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1960 | 12 | 4 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1960 | 12 | 5 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1960 | 12 | 6 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1960 | 12 | 7 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1960 | 12 | 8 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1960 | 12 | 9 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1960 | 12 | 10 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1960 | 12 | 11 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1960 | 12 | 12 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1960 | 12 | 13 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1960 | 12 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1960 | 12 | 15 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1960 | 12 | 16 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1960 | 12 | 17 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1960 | 12 | 18 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1960 | 12 | 19 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1960 | 12 | 20 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1960 | 12 | 21 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1960 | 12 | 22 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1960 | 12 | 23 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1960 | 12 | 24 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1960 | 12 | 25 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1960 | 12 | 26 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1960 | 12 | 27 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1960 | 12 | 28 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1960 | 12 | 29 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1960 | 12 | 30 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1960 | 12 | 31 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1961 | 1 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1961 | 1 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1961 | 1 | 3 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1961 | 1 | 4 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1961 | 1 | 5 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1961 | 1 | 6 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1961 | 1 | 7 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1961 | 1 | 8 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1961 | 1 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1961 | 1 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1961 | 1 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1961 | 1 | 12 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1961 | 1 | 13 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1961 | 1 | 14 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1961 | 1 | 15 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1961 | 1 | 16 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1961 | 1 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1961 | 1 | 18 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1961 | 1 | 19 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1961 | 1 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1961 | 1 | 21 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1961 | 1 | 22 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1961 | 1 | 23 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1961 | 1 | 24 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1961 | 1 | 25 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1961 | 1 | 26 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1961 | 1 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1961 | 1 | 28 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1961 | 1 | 29 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 1 | 30 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1961 | 1 | 31 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 2 | 1 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 2 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 2 | 3 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 2 | 4 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1961 | 2 | 5 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1961 | 2 | 6 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1961 | 2 | 7 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1961 | 2 | 8 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1961 | 2 | 9 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 10 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 11 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 12 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 13 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1961 | 2 | 14 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 15 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 16 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1961 | 2 | 17 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1961 | 2 | 18 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 2 | 19 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1961 | 2 | 20 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1961 | 2 | 21 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1961 | 2 | 22 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1961 | 2 | 23 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1961 | 2 | 24 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1961 | 2 | 25 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1961 | 2 | 26 | 378.7755 | 5 | 373.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1961 | 2 | 27 | 615.1837 | 5 | 610.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1961 | 2 | 28 | 455.8367 | 5 | 450.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1961 | 3 | 1 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1961 | 3 | 2 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1961 | 3 | 3 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1961 | 3 | 4 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1961 | 3 | 5 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1961 | 3 | 6 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1961 | 3 | 7 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1961 | 3 | 8 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1961 | 3 | 9 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1961 | 3 | 10 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1961 | 3 | 11 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1961 | 3 | 12 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1961 | 3 | 13 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1961 | 3 | 14 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1961 | 3 | 15 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1961 | 3 | 16 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1961 | 3 | 17 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1961 | 3 | 18 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1961 | 3 | 19 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1961 | 3 | 20 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1961 | 3 | 21 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1961 | 3 | 22 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1961 | 3 | 23 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1961 | 3 | 24 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1961 | 3 | 25 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1961 | 3 | 26 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1961 | 3 | 27 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1961 | 3 | 28 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1961 | 3 | 29 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1961 | 3 | 30 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1961 | 3 | 31 | 461.0612 | 25 | 436.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
1961 | 4 | 1 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1961 | 4 | 2 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1961 | 4 | 3 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1961 | 4 | 4 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1961 | 4 | 5 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1961 | 4 | 6 | 581.2245 | 25 | 556.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1961 | 4 | 7 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1961 | 4 | 8 | 655.6735 | 25 | 630.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1961 | 4 | 9 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1961 | 4 | 10 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1961 | 4 | 11 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1961 | 4 | 12 | 706.6122 | 25 | 681.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
1961 | 4 | 13 | 752.3265 | 25 | 727.3265 | 28.4953 | 139.3858 | 0.77441 | 27.7209 | 89.27% | 292.1162 | 274.5893 | 6590.1426
1961 | 4 | 14 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1961 | 4 | 15 | 590.3673 | 25 | 565.3673 | 28.8193 | 139.3858 | 0.77441 | 28.0449 | 89.27% | 295.5296 | 277.7978 | 6667.1482
1961 | 4 | 16 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1961 | 4 | 17 | 905.1429 | 25 | 880.1429 | 28.1897 | 139.3858 | 0.77441 | 27.4153 | 89.27% | 288.8956 | 271.5618 | 6517.484
1961 | 4 | 18 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1961 | 4 | 19 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1961 | 4 | 20 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1961 | 4 | 21 | 762.7755 | 25 | 737.7755 | 28.4744 | 139.3858 | 0.77441 | 27.7 | 89.27% | 291.896 | 274.3823 | 6585.1745
1961 | 4 | 22 | 867.2653 | 25 | 842.2653 | 28.2655 | 139.3858 | 0.77441 | 27.4911 | 89.27% | 289.6939 | 272.3122 | 6535.4934
1961 | 4 | 23 | 1111.5102 | 25 | 1086.5102 | 27.777 | 139.3858 | 0.77441 | 27.0026 | 89.27% | 284.5463 | 267.4735 | 6419.3639
1961 | 4 | 24 | 1188.5714 | 25 | 1163.5714 | 27.6229 | 139.3858 | 0.77441 | 26.8484 | 89.27% | 282.9222 | 265.9468 | 6382.7242
1961 | 4 | 25 | 927.3469 | 25 | 902.3469 | 28.1453 | 139.3858 | 0.77441 | 27.3709 | 89.27% | 288.4276 | 271.122 | 6506.9268
1961 | 4 | 26 | 1073.6327 | 25 | 1048.6327 | 27.8527 | 139.3858 | 0.77441 | 27.0783 | 89.27% | 285.3446 | 268.2239 | 6437.3733
1961 | 4 | 27 | 1008.3265 | 25 | 983.3265 | 27.9833 | 139.3858 | 0.77441 | 27.2089 | 89.27% | 286.7209 | 269.5177 | 6468.424
1961 | 4 | 28 | 747.102 | 25 | 722.102 | 28.5058 | 139.3858 | 0.77441 | 27.7314 | 89.27% | 292.2264 | 274.6928 | 6592.6266
1961 | 4 | 29 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1961 | 4 | 30 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1961 | 5 | 1 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1961 | 5 | 2 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1961 | 5 | 3 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1961 | 5 | 4 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1961 | 5 | 5 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1961 | 5 | 6 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1961 | 5 | 7 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1961 | 5 | 8 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1961 | 5 | 9 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1961 | 5 | 10 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1961 | 5 | 11 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1961 | 5 | 12 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1961 | 5 | 13 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1961 | 5 | 14 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1961 | 5 | 15 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1961 | 5 | 16 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1961 | 5 | 17 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1961 | 5 | 18 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1961 | 5 | 19 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1961 | 5 | 20 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1961 | 5 | 21 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1961 | 5 | 22 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1961 | 5 | 23 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1961 | 5 | 24 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1961 | 5 | 25 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1961 | 5 | 26 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1961 | 5 | 27 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1961 | 5 | 28 | 576 | 25 | 551 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1961 | 5 | 29 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1961 | 5 | 30 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1961 | 5 | 31 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1961 | 6 | 1 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1961 | 6 | 2 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1961 | 6 | 3 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1961 | 6 | 4 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1961 | 6 | 5 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1961 | 6 | 6 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1961 | 6 | 7 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1961 | 6 | 8 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1961 | 6 | 9 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1961 | 6 | 10 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1961 | 6 | 11 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1961 | 6 | 12 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1961 | 6 | 13 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1961 | 6 | 14 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1961 | 6 | 15 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1961 | 6 | 16 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1961 | 6 | 17 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1961 | 6 | 18 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1961 | 6 | 19 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1961 | 6 | 20 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1961 | 6 | 21 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1961 | 6 | 22 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1961 | 6 | 23 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1961 | 6 | 24 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1961 | 6 | 25 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1961 | 6 | 26 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1961 | 6 | 27 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1961 | 6 | 28 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1961 | 6 | 29 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1961 | 6 | 30 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1961 | 7 | 1 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1961 | 7 | 2 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 7 | 3 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1961 | 7 | 4 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1961 | 7 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1961 | 7 | 6 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1961 | 7 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 7 | 8 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 7 | 9 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1961 | 7 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1961 | 7 | 11 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1961 | 7 | 12 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1961 | 7 | 13 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 7 | 14 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1961 | 7 | 15 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1961 | 7 | 16 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1961 | 7 | 17 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1961 | 7 | 18 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1961 | 7 | 19 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1961 | 7 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1961 | 7 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 7 | 22 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1961 | 7 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1961 | 7 | 24 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1961 | 7 | 25 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1961 | 7 | 26 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1961 | 7 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1961 | 7 | 28 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1961 | 7 | 29 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1961 | 7 | 30 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1961 | 7 | 31 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1961 | 8 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1961 | 8 | 2 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1961 | 8 | 3 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1961 | 8 | 4 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1961 | 8 | 5 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1961 | 8 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1961 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1961 | 8 | 8 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1961 | 8 | 9 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1961 | 8 | 10 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1961 | 8 | 11 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1961 | 8 | 12 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1961 | 8 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1961 | 8 | 14 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1961 | 8 | 15 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1961 | 8 | 16 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1961 | 8 | 17 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1961 | 8 | 18 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 8 | 19 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1961 | 8 | 20 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1961 | 8 | 21 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1961 | 8 | 22 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1961 | 8 | 23 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1961 | 8 | 24 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1961 | 8 | 25 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1961 | 8 | 26 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1961 | 8 | 27 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1961 | 8 | 28 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1961 | 8 | 29 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1961 | 8 | 30 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1961 | 8 | 31 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1961 | 9 | 1 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1961 | 9 | 2 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1961 | 9 | 3 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1961 | 9 | 4 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1961 | 9 | 5 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1961 | 9 | 6 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1961 | 9 | 7 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1961 | 9 | 8 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1961 | 9 | 9 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1961 | 9 | 10 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1961 | 9 | 11 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1961 | 9 | 12 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1961 | 9 | 13 | 3.7878 | 15 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1961 | 9 | 14 | 3.7878 | 15 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1961 | 9 | 15 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1961 | 9 | 16 | 6.6612 | 15 | 0 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1961 | 9 | 17 | 6.6612 | 15 | 0 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1961 | 9 | 18 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1961 | 9 | 19 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1961 | 9 | 20 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1961 | 9 | 21 | 4.049 | 15 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
1961 | 9 | 22 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1961 | 9 | 23 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1961 | 9 | 24 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1961 | 9 | 25 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1961 | 9 | 26 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1961 | 9 | 27 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1961 | 9 | 28 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1961 | 9 | 29 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1961 | 9 | 30 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1961 | 10 | 1 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1961 | 10 | 2 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1961 | 10 | 3 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1961 | 10 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1961 | 10 | 5 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1961 | 10 | 6 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1961 | 10 | 7 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1961 | 10 | 8 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1961 | 10 | 9 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1961 | 10 | 10 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1961 | 10 | 11 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1961 | 10 | 12 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1961 | 10 | 13 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1961 | 10 | 14 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1961 | 10 | 15 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1961 | 10 | 16 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1961 | 10 | 17 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1961 | 10 | 18 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1961 | 10 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1961 | 10 | 20 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1961 | 10 | 21 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1961 | 10 | 22 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1961 | 10 | 23 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1961 | 10 | 24 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1961 | 10 | 25 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1961 | 10 | 26 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1961 | 10 | 27 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1961 | 10 | 28 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 10 | 29 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1961 | 10 | 30 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 10 | 31 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1961 | 11 | 1 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1961 | 11 | 2 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 11 | 3 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 11 | 4 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 11 | 5 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1961 | 11 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1961 | 11 | 7 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1961 | 11 | 8 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1961 | 11 | 9 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1961 | 11 | 10 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1961 | 11 | 11 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1961 | 11 | 12 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1961 | 11 | 13 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1961 | 11 | 14 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1961 | 11 | 15 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1961 | 11 | 16 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1961 | 11 | 17 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1961 | 11 | 18 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1961 | 11 | 19 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1961 | 11 | 20 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1961 | 11 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1961 | 11 | 22 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1961 | 11 | 23 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1961 | 11 | 24 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1961 | 11 | 25 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1961 | 11 | 26 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1961 | 11 | 27 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1961 | 11 | 28 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1961 | 11 | 29 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1961 | 11 | 30 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1961 | 12 | 1 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1961 | 12 | 2 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1961 | 12 | 3 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1961 | 12 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1961 | 12 | 5 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1961 | 12 | 6 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1961 | 12 | 7 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1961 | 12 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1961 | 12 | 9 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1961 | 12 | 10 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1961 | 12 | 11 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1961 | 12 | 12 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1961 | 12 | 13 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1961 | 12 | 14 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1961 | 12 | 15 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 12 | 16 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1961 | 12 | 17 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1961 | 12 | 18 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1961 | 12 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1961 | 12 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1961 | 12 | 21 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1961 | 12 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 12 | 23 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 12 | 24 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 12 | 25 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1961 | 12 | 26 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 12 | 27 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1961 | 12 | 28 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1961 | 12 | 29 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1961 | 12 | 30 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1961 | 12 | 31 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1962 | 1 | 1 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1962 | 1 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1962 | 1 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1962 | 1 | 4 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1962 | 1 | 5 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 1 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 1 | 7 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1962 | 1 | 8 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1962 | 1 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1962 | 1 | 10 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 1 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 1 | 12 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 1 | 13 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1962 | 1 | 14 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1962 | 1 | 15 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 1 | 16 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1962 | 1 | 17 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1962 | 1 | 18 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1962 | 1 | 19 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1962 | 1 | 20 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1962 | 1 | 21 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1962 | 1 | 22 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1962 | 1 | 23 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1962 | 1 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1962 | 1 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1962 | 1 | 26 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1962 | 1 | 27 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1962 | 1 | 28 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1962 | 1 | 29 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1962 | 1 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1962 | 1 | 31 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1962 | 2 | 1 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 2 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 3 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 4 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 5 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1962 | 2 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 2 | 7 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 2 | 8 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1962 | 2 | 9 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 10 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 11 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 2 | 12 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 2 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1962 | 2 | 14 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1962 | 2 | 15 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 16 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 2 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 2 | 18 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 2 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1962 | 2 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 2 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 2 | 22 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1962 | 2 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 2 | 24 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 2 | 25 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 26 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 27 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1962 | 2 | 28 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1962 | 3 | 1 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 2 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 3 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 4 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 5 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 6 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 7 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1962 | 3 | 8 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1962 | 3 | 9 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 3 | 10 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1962 | 3 | 11 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1962 | 3 | 12 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1962 | 3 | 13 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1962 | 3 | 14 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1962 | 3 | 15 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1962 | 3 | 16 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1962 | 3 | 17 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1962 | 3 | 18 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1962 | 3 | 19 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1962 | 3 | 20 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1962 | 3 | 21 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1962 | 3 | 22 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1962 | 3 | 23 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1962 | 3 | 24 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1962 | 3 | 25 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1962 | 3 | 26 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1962 | 3 | 27 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1962 | 3 | 28 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1962 | 3 | 29 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1962 | 3 | 30 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1962 | 3 | 31 | 848.9796 | 25 | 823.9796 | 28.302 | 139.3858 | 0.77441 | 27.5276 | 89.27% | 290.0792 | 272.6745 | 6544.1876
1962 | 4 | 1 | 1384.4898 | 25 | 1359.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
1962 | 4 | 2 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
1962 | 4 | 3 | 960 | 25 | 935 | 28.08 | 139.3858 | 0.77441 | 27.3056 | 89.27% | 287.7394 | 270.4751 | 6491.4015
1962 | 4 | 4 | 653.0612 | 25 | 628.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
1962 | 4 | 5 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1962 | 4 | 6 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1962 | 4 | 7 | 910.3673 | 25 | 885.3673 | 28.1793 | 139.3858 | 0.77441 | 27.4049 | 89.27% | 288.7855 | 271.4583 | 6515
1962 | 4 | 8 | 1462.8571 | 25 | 1437.8571 | 27.0743 | 139.3858 | 0.77441 | 26.2999 | 89.27% | 277.1415 | 260.513 | 6252.3114
1962 | 4 | 9 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1962 | 4 | 10 | 1221.2245 | 25 | 1196.2245 | 27.5576 | 139.3858 | 0.77441 | 26.7831 | 89.27% | 282.234 | 265.3 | 6367.1988
1962 | 4 | 11 | 867.2653 | 25 | 842.2653 | 28.2655 | 139.3858 | 0.77441 | 27.4911 | 89.27% | 289.6939 | 272.3122 | 6535.4934
1962 | 4 | 12 | 666.1224 | 25 | 641.1224 | 28.6678 | 139.3858 | 0.77441 | 27.8933 | 89.27% | 293.933 | 276.2971 | 6631.1294
1962 | 4 | 13 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1962 | 4 | 14 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1962 | 4 | 15 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1962 | 4 | 16 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1962 | 4 | 17 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1962 | 4 | 18 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1962 | 4 | 19 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1962 | 4 | 20 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1962 | 4 | 21 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1962 | 4 | 22 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1962 | 4 | 23 | 542.0408 | 25 | 517.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
1962 | 4 | 24 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1962 | 4 | 25 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1962 | 4 | 26 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1962 | 4 | 27 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1962 | 4 | 28 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1962 | 4 | 29 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1962 | 4 | 30 | 717.0612 | 25 | 692.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1962 | 5 | 1 | 808.4898 | 25 | 783.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
1962 | 5 | 2 | 576 | 25 | 551 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1962 | 5 | 3 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1962 | 5 | 4 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1962 | 5 | 5 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1962 | 5 | 6 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1962 | 5 | 7 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1962 | 5 | 8 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1962 | 5 | 9 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1962 | 5 | 10 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1962 | 5 | 11 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1962 | 5 | 12 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1962 | 5 | 13 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1962 | 5 | 14 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1962 | 5 | 15 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1962 | 5 | 16 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1962 | 5 | 17 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1962 | 5 | 18 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1962 | 5 | 19 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1962 | 5 | 20 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1962 | 5 | 21 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1962 | 5 | 22 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1962 | 5 | 23 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1962 | 5 | 24 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1962 | 5 | 25 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1962 | 5 | 26 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1962 | 5 | 27 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1962 | 5 | 28 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1962 | 5 | 29 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1962 | 5 | 30 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1962 | 5 | 31 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1962 | 6 | 1 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1962 | 6 | 2 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1962 | 6 | 3 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1962 | 6 | 4 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1962 | 6 | 5 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1962 | 6 | 6 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1962 | 6 | 7 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1962 | 6 | 8 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1962 | 6 | 9 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1962 | 6 | 10 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1962 | 6 | 11 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1962 | 6 | 12 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 6 | 13 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1962 | 6 | 14 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1962 | 6 | 15 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1962 | 6 | 16 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1962 | 6 | 17 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1962 | 6 | 18 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1962 | 6 | 19 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1962 | 6 | 20 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1962 | 6 | 21 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1962 | 6 | 22 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1962 | 6 | 23 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1962 | 6 | 24 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1962 | 6 | 25 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1962 | 6 | 26 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1962 | 6 | 27 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1962 | 6 | 28 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1962 | 6 | 29 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1962 | 6 | 30 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1962 | 7 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1962 | 7 | 2 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1962 | 7 | 3 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1962 | 7 | 4 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1962 | 7 | 5 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1962 | 7 | 6 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1962 | 7 | 7 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1962 | 7 | 8 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1962 | 7 | 9 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1962 | 7 | 10 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 7 | 11 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1962 | 7 | 12 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1962 | 7 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1962 | 7 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1962 | 7 | 15 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1962 | 7 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1962 | 7 | 17 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 7 | 18 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 7 | 19 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1962 | 7 | 20 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1962 | 7 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1962 | 7 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1962 | 7 | 23 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1962 | 7 | 24 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 7 | 25 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1962 | 7 | 26 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1962 | 7 | 27 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1962 | 7 | 28 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1962 | 7 | 29 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1962 | 7 | 30 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1962 | 7 | 31 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1962 | 8 | 1 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1962 | 8 | 2 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1962 | 8 | 3 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 8 | 4 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1962 | 8 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1962 | 8 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1962 | 8 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1962 | 8 | 8 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1962 | 8 | 9 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1962 | 8 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1962 | 8 | 11 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1962 | 8 | 12 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1962 | 8 | 13 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1962 | 8 | 14 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1962 | 8 | 15 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1962 | 8 | 16 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1962 | 8 | 17 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 8 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1962 | 8 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1962 | 8 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 8 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1962 | 8 | 22 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1962 | 8 | 23 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1962 | 8 | 24 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1962 | 8 | 25 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1962 | 8 | 26 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1962 | 8 | 27 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1962 | 8 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1962 | 8 | 29 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1962 | 8 | 30 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1962 | 8 | 31 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1962 | 9 | 1 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1962 | 9 | 2 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1962 | 9 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1962 | 9 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1962 | 9 | 5 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1962 | 9 | 6 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1962 | 9 | 7 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1962 | 9 | 8 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1962 | 9 | 9 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1962 | 9 | 10 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1962 | 9 | 11 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1962 | 9 | 12 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1962 | 9 | 13 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1962 | 9 | 14 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1962 | 9 | 15 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1962 | 9 | 16 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1962 | 9 | 17 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1962 | 9 | 18 | 225.9592 | 15 | 210.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1962 | 9 | 19 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1962 | 9 | 20 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1962 | 9 | 21 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1962 | 9 | 22 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1962 | 9 | 23 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1962 | 9 | 24 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1962 | 9 | 25 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1962 | 9 | 26 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1962 | 9 | 27 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1962 | 9 | 28 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1962 | 9 | 29 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1962 | 9 | 30 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1962 | 10 | 1 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1962 | 10 | 2 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1962 | 10 | 3 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1962 | 10 | 4 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1962 | 10 | 5 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1962 | 10 | 6 | 320 | 15 | 305 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1962 | 10 | 7 | 1972.2449 | 15 | 1957.2449 | 26.0555 | 139.3858 | 0.77441 | 25.2811 | 89.27% | 266.4059 | 250.4215 | 6010.1163
1962 | 10 | 8 | 1828.5714 | 15 | 1813.5714 | 26.3429 | 139.3858 | 0.77441 | 25.5684 | 89.27% | 269.4339 | 253.2678 | 6078.4277
1962 | 10 | 9 | 766.6939 | 15 | 751.6939 | 28.4666 | 139.3858 | 0.77441 | 27.6922 | 89.27% | 291.8134 | 274.3046 | 6583.3114
1962 | 10 | 10 | 496.3265 | 15 | 481.3265 | 29.0073 | 139.3858 | 0.77441 | 28.2329 | 89.27% | 297.5116 | 279.6609 | 6711.8611
1962 | 10 | 11 | 399.6735 | 15 | 384.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1962 | 10 | 12 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1962 | 10 | 13 | 314.7755 | 15 | 299.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1962 | 10 | 14 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1962 | 10 | 15 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1962 | 10 | 16 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1962 | 10 | 17 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1962 | 10 | 18 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1962 | 10 | 19 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1962 | 10 | 20 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1962 | 10 | 21 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1962 | 10 | 22 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1962 | 10 | 23 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1962 | 10 | 24 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1962 | 10 | 25 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1962 | 10 | 26 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1962 | 10 | 27 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1962 | 10 | 28 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1962 | 10 | 29 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1962 | 10 | 30 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1962 | 10 | 31 | 259.9184 | 15 | 244.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1962 | 11 | 1 | 978.2857 | 15 | 963.2857 | 28.0434 | 139.3858 | 0.77441 | 27.269 | 89.27% | 287.354 | 270.1128 | 6482.7073
1962 | 11 | 2 | 778.449 | 15 | 763.449 | 28.4431 | 139.3858 | 0.77441 | 27.6687 | 89.27% | 291.5657 | 274.0718 | 6577.7223
1962 | 11 | 3 | 448 | 15 | 433 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1962 | 11 | 4 | 523.7551 | 15 | 508.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1962 | 11 | 5 | 442.7755 | 15 | 427.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1962 | 11 | 6 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1962 | 11 | 7 | 269.0612 | 15 | 254.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1962 | 11 | 8 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1962 | 11 | 9 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1962 | 11 | 10 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1962 | 11 | 11 | 1410.6122 | 15 | 1395.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1962 | 11 | 12 | 1179.4286 | 15 | 1164.4286 | 27.6411 | 139.3858 | 0.77441 | 26.8667 | 89.27% | 283.1149 | 266.128 | 6387.0713
1962 | 11 | 13 | 630.8571 | 15 | 615.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1962 | 11 | 14 | 421.8776 | 15 | 406.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1962 | 11 | 15 | 329.1429 | 15 | 314.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1962 | 11 | 16 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1962 | 11 | 17 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1962 | 11 | 18 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1962 | 11 | 19 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1962 | 11 | 20 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1962 | 11 | 21 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1962 | 11 | 22 | 275.5918 | 15 | 260.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1962 | 11 | 23 | 438.8571 | 15 | 423.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1962 | 11 | 24 | 317.3878 | 15 | 302.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1962 | 11 | 25 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1962 | 11 | 26 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1962 | 11 | 27 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1962 | 11 | 28 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1962 | 11 | 29 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1962 | 11 | 30 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1962 | 12 | 1 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1962 | 12 | 2 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1962 | 12 | 3 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1962 | 12 | 4 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1962 | 12 | 5 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1962 | 12 | 6 | 573.3878 | 5 | 568.3878 | 28.8532 | 139.3858 | 0.77441 | 28.0788 | 89.27% | 295.8875 | 278.1342 | 6675.2214
1962 | 12 | 7 | 1567.3469 | 5 | 1562.3469 | 26.8653 | 139.3858 | 0.77441 | 26.0909 | 89.27% | 274.9393 | 258.4429 | 6202.6304
1962 | 12 | 8 | 842.449 | 5 | 837.449 | 28.3151 | 139.3858 | 0.77441 | 27.5407 | 89.27% | 290.2169 | 272.8039 | 6547.2927
1962 | 12 | 9 | 505.4694 | 5 | 500.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1962 | 12 | 10 | 442.7755 | 5 | 437.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1962 | 12 | 11 | 351.3469 | 5 | 346.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1962 | 12 | 12 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1962 | 12 | 13 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1962 | 12 | 14 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1962 | 12 | 15 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1962 | 12 | 16 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1962 | 12 | 17 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1962 | 12 | 18 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1962 | 12 | 19 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1962 | 12 | 20 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1962 | 12 | 21 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1962 | 12 | 22 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1962 | 12 | 23 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1962 | 12 | 24 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1962 | 12 | 25 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1962 | 12 | 26 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1962 | 12 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1962 | 12 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1962 | 12 | 29 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1962 | 12 | 30 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1962 | 12 | 31 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 1 | 1 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1963 | 1 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1963 | 1 | 3 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1963 | 1 | 4 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1963 | 1 | 5 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 6 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 7 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 8 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1963 | 1 | 9 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 10 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 11 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 12 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1963 | 1 | 13 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1963 | 1 | 14 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1963 | 1 | 15 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1963 | 1 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 1 | 17 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1963 | 1 | 18 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 1 | 19 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 1 | 20 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 1 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1963 | 1 | 22 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1963 | 1 | 23 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1963 | 1 | 24 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1963 | 1 | 25 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1963 | 1 | 26 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1963 | 1 | 27 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1963 | 1 | 28 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 1 | 29 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1963 | 1 | 30 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1963 | 1 | 31 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1963 | 2 | 1 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1963 | 2 | 2 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1963 | 2 | 3 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1963 | 2 | 4 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1963 | 2 | 5 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1963 | 2 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1963 | 2 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1963 | 2 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1963 | 2 | 10 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1963 | 2 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1963 | 2 | 12 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1963 | 2 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1963 | 2 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1963 | 2 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 16 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 18 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 19 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 20 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1963 | 2 | 21 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1963 | 2 | 22 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1963 | 2 | 23 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1963 | 2 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1963 | 2 | 25 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1963 | 2 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1963 | 2 | 27 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1963 | 2 | 28 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1963 | 3 | 1 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1963 | 3 | 2 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 3 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 4 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 5 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 6 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 7 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1963 | 3 | 8 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1963 | 3 | 9 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 10 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 11 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1963 | 3 | 12 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1963 | 3 | 13 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1963 | 3 | 14 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1963 | 3 | 15 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1963 | 3 | 16 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1963 | 3 | 17 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1963 | 3 | 18 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1963 | 3 | 19 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1963 | 3 | 20 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1963 | 3 | 21 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1963 | 3 | 22 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1963 | 3 | 23 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1963 | 3 | 24 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1963 | 3 | 25 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1963 | 3 | 26 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1963 | 3 | 27 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1963 | 3 | 28 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1963 | 3 | 29 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1963 | 3 | 30 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1963 | 3 | 31 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1963 | 4 | 1 | 547.2653 | 25 | 522.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1963 | 4 | 2 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1963 | 4 | 3 | 1086.6939 | 25 | 1061.6939 | 27.8266 | 139.3858 | 0.77441 | 27.0522 | 89.27% | 285.0693 | 267.9651 | 6431.1632
1963 | 4 | 4 | 944.3265 | 25 | 919.3265 | 28.1113 | 139.3858 | 0.77441 | 27.3369 | 89.27% | 288.0698 | 270.7856 | 6498.8536
1963 | 4 | 5 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1963 | 4 | 6 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1963 | 4 | 7 | 590.3673 | 25 | 565.3673 | 28.8193 | 139.3858 | 0.77441 | 28.0449 | 89.27% | 295.5296 | 277.7978 | 6667.1482
1963 | 4 | 8 | 680.4898 | 25 | 655.4898 | 28.639 | 139.3858 | 0.77441 | 27.8646 | 89.27% | 293.6302 | 276.0124 | 6624.2983
1963 | 4 | 9 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1963 | 4 | 10 | 701.3878 | 25 | 676.3878 | 28.5972 | 139.3858 | 0.77441 | 27.8228 | 89.27% | 293.1898 | 275.5984 | 6614.3621
1963 | 4 | 11 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1963 | 4 | 12 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1963 | 4 | 13 | 882.9388 | 25 | 857.9388 | 28.2341 | 139.3858 | 0.77441 | 27.4597 | 89.27% | 289.3635 | 272.0017 | 6528.0413
1963 | 4 | 14 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1963 | 4 | 15 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1963 | 4 | 16 | 752.3265 | 25 | 727.3265 | 28.4953 | 139.3858 | 0.77441 | 27.7209 | 89.27% | 292.1162 | 274.5893 | 6590.1426
1963 | 4 | 17 | 773.2245 | 25 | 748.2245 | 28.4536 | 139.3858 | 0.77441 | 27.6791 | 89.27% | 291.6758 | 274.1753 | 6580.2064
1963 | 4 | 18 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1963 | 4 | 19 | 905.1429 | 25 | 880.1429 | 28.1897 | 139.3858 | 0.77441 | 27.4153 | 89.27% | 288.8956 | 271.5618 | 6517.484
1963 | 4 | 20 | 966.5306 | 25 | 941.5306 | 28.0669 | 139.3858 | 0.77441 | 27.2925 | 89.27% | 287.6018 | 270.3457 | 6488.2964
1963 | 4 | 21 | 1080.1633 | 25 | 1055.1633 | 27.8397 | 139.3858 | 0.77441 | 27.0653 | 89.27% | 285.2069 | 268.0945 | 6434.2683
1963 | 4 | 22 | 1068.4082 | 25 | 1043.4082 | 27.8632 | 139.3858 | 0.77441 | 27.0888 | 89.27% | 285.4547 | 268.3274 | 6439.8574
1963 | 4 | 23 | 752.3265 | 25 | 727.3265 | 28.4953 | 139.3858 | 0.77441 | 27.7209 | 89.27% | 292.1162 | 274.5893 | 6590.1426
1963 | 4 | 24 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1963 | 4 | 25 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1963 | 4 | 26 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1963 | 4 | 27 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1963 | 4 | 28 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1963 | 4 | 29 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1963 | 4 | 30 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1963 | 5 | 1 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1963 | 5 | 2 | 542.0408 | 25 | 517.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
1963 | 5 | 3 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1963 | 5 | 4 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1963 | 5 | 5 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1963 | 5 | 6 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1963 | 5 | 7 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1963 | 5 | 8 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1963 | 5 | 9 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1963 | 5 | 10 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1963 | 5 | 11 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1963 | 5 | 12 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1963 | 5 | 13 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1963 | 5 | 14 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1963 | 5 | 15 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1963 | 5 | 16 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1963 | 5 | 17 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1963 | 5 | 18 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1963 | 5 | 19 | 719.6735 | 25 | 694.6735 | 28.5607 | 139.3858 | 0.77441 | 27.7862 | 89.27% | 292.8044 | 275.2362 | 6605.6679
1963 | 5 | 20 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1963 | 5 | 21 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1963 | 5 | 22 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1963 | 5 | 23 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1963 | 5 | 24 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1963 | 5 | 25 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1963 | 5 | 26 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1963 | 5 | 27 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1963 | 5 | 28 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1963 | 5 | 29 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1963 | 5 | 30 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1963 | 5 | 31 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1963 | 6 | 1 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1963 | 6 | 2 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1963 | 6 | 3 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1963 | 6 | 4 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1963 | 6 | 5 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1963 | 6 | 6 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1963 | 6 | 7 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1963 | 6 | 8 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1963 | 6 | 9 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1963 | 6 | 10 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1963 | 6 | 11 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1963 | 6 | 12 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1963 | 6 | 13 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1963 | 6 | 14 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1963 | 6 | 15 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1963 | 6 | 16 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1963 | 6 | 17 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1963 | 6 | 18 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1963 | 6 | 19 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1963 | 6 | 20 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1963 | 6 | 21 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1963 | 6 | 22 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1963 | 6 | 23 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1963 | 6 | 24 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1963 | 6 | 25 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1963 | 6 | 26 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1963 | 6 | 27 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1963 | 6 | 28 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1963 | 6 | 29 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1963 | 6 | 30 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1963 | 7 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1963 | 7 | 2 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1963 | 7 | 3 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1963 | 7 | 4 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1963 | 7 | 5 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1963 | 7 | 6 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1963 | 7 | 7 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1963 | 7 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1963 | 7 | 9 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1963 | 7 | 10 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1963 | 7 | 11 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1963 | 7 | 12 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1963 | 7 | 13 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1963 | 7 | 14 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1963 | 7 | 15 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1963 | 7 | 16 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1963 | 7 | 17 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1963 | 7 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1963 | 7 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1963 | 7 | 20 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1963 | 7 | 21 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1963 | 7 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1963 | 7 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1963 | 7 | 24 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1963 | 7 | 25 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1963 | 7 | 26 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1963 | 7 | 27 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1963 | 7 | 28 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1963 | 7 | 29 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1963 | 7 | 30 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1963 | 7 | 31 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1963 | 8 | 1 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1963 | 8 | 2 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1963 | 8 | 3 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1963 | 8 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1963 | 8 | 5 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1963 | 8 | 6 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1963 | 8 | 7 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1963 | 8 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1963 | 8 | 9 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1963 | 8 | 10 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1963 | 8 | 11 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1963 | 8 | 12 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1963 | 8 | 13 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1963 | 8 | 14 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1963 | 8 | 15 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1963 | 8 | 16 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1963 | 8 | 17 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1963 | 8 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1963 | 8 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1963 | 8 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1963 | 8 | 21 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1963 | 8 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1963 | 8 | 23 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1963 | 8 | 24 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1963 | 8 | 25 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1963 | 8 | 26 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1963 | 8 | 27 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1963 | 8 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1963 | 8 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1963 | 8 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1963 | 8 | 31 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1963 | 9 | 1 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1963 | 9 | 2 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1963 | 9 | 3 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1963 | 9 | 4 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1963 | 9 | 5 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1963 | 9 | 6 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1963 | 9 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1963 | 9 | 8 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1963 | 9 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1963 | 9 | 10 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1963 | 9 | 11 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1963 | 9 | 12 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1963 | 9 | 13 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1963 | 9 | 14 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1963 | 9 | 15 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1963 | 9 | 16 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1963 | 9 | 17 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1963 | 9 | 18 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1963 | 9 | 19 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1963 | 9 | 20 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 21 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 22 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 23 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 24 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 25 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1963 | 9 | 26 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 27 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1963 | 9 | 28 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1963 | 9 | 29 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1963 | 9 | 30 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1963 | 10 | 1 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1963 | 10 | 2 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1963 | 10 | 3 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1963 | 10 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1963 | 10 | 5 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1963 | 10 | 6 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1963 | 10 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1963 | 10 | 8 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1963 | 10 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1963 | 10 | 10 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1963 | 10 | 11 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1963 | 10 | 12 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1963 | 10 | 13 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1963 | 10 | 14 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1963 | 10 | 15 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1963 | 10 | 16 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1963 | 10 | 17 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1963 | 10 | 18 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1963 | 10 | 19 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1963 | 10 | 20 | 9.7959 | 15 | 0 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1963 | 10 | 21 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1963 | 10 | 22 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1963 | 10 | 23 | 9.4041 | 15 | 0 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1963 | 10 | 24 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1963 | 10 | 25 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1963 | 10 | 26 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1963 | 10 | 27 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1963 | 10 | 28 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1963 | 10 | 29 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1963 | 10 | 30 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1963 | 10 | 31 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1963 | 11 | 1 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1963 | 11 | 2 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1963 | 11 | 3 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1963 | 11 | 4 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1963 | 11 | 5 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1963 | 11 | 6 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1963 | 11 | 7 | 231.1837 | 15 | 216.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1963 | 11 | 8 | 3278.3673 | 15 | 3263.3673 | 23.4433 | 0 | 0 | 23.4433 | 0% | 0 | 0 | 0
1963 | 11 | 9 | 2703.6735 | 15 | 2688.6735 | 24.5927 | 0 | 0 | 24.5927 | 0% | 0 | 0 | 0
1963 | 11 | 10 | 1277.3878 | 15 | 1262.3878 | 27.4452 | 139.3858 | 0.77441 | 26.6708 | 89.27% | 281.0503 | 264.1873 | 6340.4953
1963 | 11 | 11 | 696.1633 | 15 | 681.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1963 | 11 | 12 | 650.449 | 15 | 635.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
1963 | 11 | 13 | 523.7551 | 15 | 508.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1963 | 11 | 14 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1963 | 11 | 15 | 338.2857 | 15 | 323.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1963 | 11 | 16 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1963 | 11 | 17 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1963 | 11 | 18 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1963 | 11 | 19 | 333.0612 | 15 | 318.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1963 | 11 | 20 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1963 | 11 | 21 | 253.3878 | 15 | 238.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1963 | 11 | 22 | 220.7347 | 15 | 205.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1963 | 11 | 23 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1963 | 11 | 24 | 548.5714 | 15 | 533.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
1963 | 11 | 25 | 417.9592 | 15 | 402.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1963 | 11 | 26 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1963 | 11 | 27 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1963 | 11 | 28 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1963 | 11 | 29 | 548.5714 | 15 | 533.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
1963 | 11 | 30 | 1280 | 15 | 1265 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
1963 | 12 | 1 | 1044.898 | 5 | 1039.898 | 27.9102 | 139.3858 | 0.77441 | 27.1358 | 89.27% | 285.9502 | 268.7932 | 6451.0356
1963 | 12 | 2 | 653.0612 | 5 | 648.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
1963 | 12 | 3 | 444.0816 | 5 | 439.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1963 | 12 | 4 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1963 | 12 | 5 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1963 | 12 | 6 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1963 | 12 | 7 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1963 | 12 | 8 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1963 | 12 | 9 | 608.6531 | 5 | 603.6531 | 28.7827 | 139.3858 | 0.77441 | 28.0083 | 89.27% | 295.1442 | 277.4356 | 6658.454
1963 | 12 | 10 | 1057.9592 | 5 | 1052.9592 | 27.8841 | 139.3858 | 0.77441 | 27.1097 | 89.27% | 285.6749 | 268.5344 | 6444.8255
1963 | 12 | 11 | 586.449 | 5 | 581.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1963 | 12 | 12 | 455.8367 | 5 | 450.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1963 | 12 | 13 | 297.7959 | 5 | 292.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1963 | 12 | 14 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1963 | 12 | 15 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1963 | 12 | 16 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1963 | 12 | 17 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1963 | 12 | 18 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1963 | 12 | 19 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1963 | 12 | 20 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1963 | 12 | 21 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1963 | 12 | 22 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1963 | 12 | 23 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1963 | 12 | 24 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1963 | 12 | 25 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1963 | 12 | 26 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1963 | 12 | 27 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1963 | 12 | 28 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1963 | 12 | 29 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1963 | 12 | 30 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1963 | 12 | 31 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1964 | 1 | 1 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1964 | 1 | 2 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1964 | 1 | 3 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1964 | 1 | 4 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1964 | 1 | 5 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1964 | 1 | 6 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1964 | 1 | 7 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1964 | 1 | 8 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1964 | 1 | 9 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1964 | 1 | 10 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1964 | 1 | 11 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1964 | 1 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1964 | 1 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1964 | 1 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1964 | 1 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1964 | 1 | 16 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1964 | 1 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1964 | 1 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1964 | 1 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1964 | 1 | 20 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1964 | 1 | 21 | 391.8367 | 5 | 386.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1964 | 1 | 22 | 731.4286 | 5 | 726.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1964 | 1 | 23 | 451.9184 | 5 | 446.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1964 | 1 | 24 | 321.3061 | 5 | 316.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1964 | 1 | 25 | 398.3673 | 5 | 393.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1964 | 1 | 26 | 973.0612 | 5 | 968.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1964 | 1 | 27 | 590.3673 | 5 | 585.3673 | 28.8193 | 139.3858 | 0.77441 | 28.0449 | 89.27% | 295.5296 | 277.7978 | 6667.1482
1964 | 1 | 28 | 347.4286 | 5 | 342.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1964 | 1 | 29 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1964 | 1 | 30 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1964 | 1 | 31 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1964 | 2 | 1 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1964 | 2 | 2 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1964 | 2 | 3 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1964 | 2 | 4 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1964 | 2 | 5 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1964 | 2 | 6 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1964 | 2 | 7 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1964 | 2 | 8 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1964 | 2 | 9 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1964 | 2 | 10 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1964 | 2 | 11 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1964 | 2 | 12 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1964 | 2 | 13 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1964 | 2 | 14 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1964 | 2 | 15 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1964 | 2 | 16 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1964 | 2 | 17 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1964 | 2 | 18 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1964 | 2 | 19 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1964 | 2 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1964 | 2 | 21 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1964 | 2 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1964 | 2 | 23 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1964 | 2 | 24 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1964 | 2 | 25 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1964 | 2 | 26 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1964 | 2 | 27 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1964 | 2 | 28 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1964 | 2 | 29 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1964 | 3 | 1 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1964 | 3 | 2 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1964 | 3 | 3 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1964 | 3 | 4 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1964 | 3 | 5 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1964 | 3 | 6 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1964 | 3 | 7 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1964 | 3 | 8 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1964 | 3 | 9 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1964 | 3 | 10 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1964 | 3 | 11 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1964 | 3 | 12 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1964 | 3 | 13 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1964 | 3 | 14 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1964 | 3 | 15 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1964 | 3 | 16 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1964 | 3 | 17 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1964 | 3 | 18 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1964 | 3 | 19 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1964 | 3 | 20 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1964 | 3 | 21 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1964 | 3 | 22 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1964 | 3 | 23 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1964 | 3 | 24 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1964 | 3 | 25 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1964 | 3 | 26 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1964 | 3 | 27 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1964 | 3 | 28 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1964 | 3 | 29 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1964 | 3 | 30 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1964 | 3 | 31 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1964 | 4 | 1 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1964 | 4 | 2 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1964 | 4 | 3 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1964 | 4 | 4 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1964 | 4 | 5 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1964 | 4 | 6 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1964 | 4 | 7 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1964 | 4 | 8 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1964 | 4 | 9 | 671.3469 | 25 | 646.3469 | 28.6573 | 139.3858 | 0.77441 | 27.8829 | 89.27% | 293.8229 | 276.1936 | 6628.6454
1964 | 4 | 10 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1964 | 4 | 11 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1964 | 4 | 12 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1964 | 4 | 13 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1964 | 4 | 14 | 1077.551 | 25 | 1052.551 | 27.8449 | 139.3858 | 0.77441 | 27.0705 | 89.27% | 285.262 | 268.1463 | 6435.5103
1964 | 4 | 15 | 1880.8163 | 25 | 1855.8163 | 26.2384 | 139.3858 | 0.77441 | 25.464 | 89.27% | 268.3328 | 252.2328 | 6053.5872
1964 | 4 | 16 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
1964 | 4 | 17 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1964 | 4 | 18 | 762.7755 | 25 | 737.7755 | 28.4744 | 139.3858 | 0.77441 | 27.7 | 89.27% | 291.896 | 274.3823 | 6585.1745
1964 | 4 | 19 | 808.4898 | 25 | 783.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
1964 | 4 | 20 | 581.2245 | 25 | 556.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1964 | 4 | 21 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1964 | 4 | 22 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1964 | 4 | 23 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1964 | 4 | 24 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1964 | 4 | 25 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1964 | 4 | 26 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1964 | 4 | 27 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1964 | 4 | 28 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1964 | 4 | 29 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1964 | 4 | 30 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1964 | 5 | 1 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1964 | 5 | 2 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1964 | 5 | 3 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1964 | 5 | 4 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1964 | 5 | 5 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1964 | 5 | 6 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1964 | 5 | 7 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1964 | 5 | 8 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1964 | 5 | 9 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1964 | 5 | 10 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1964 | 5 | 11 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1964 | 5 | 12 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1964 | 5 | 13 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1964 | 5 | 14 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1964 | 5 | 15 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1964 | 5 | 16 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1964 | 5 | 17 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1964 | 5 | 18 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1964 | 5 | 19 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1964 | 5 | 20 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1964 | 5 | 21 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1964 | 5 | 22 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1964 | 5 | 23 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1964 | 5 | 24 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1964 | 5 | 25 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1964 | 5 | 26 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1964 | 5 | 27 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1964 | 5 | 28 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1964 | 5 | 29 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1964 | 5 | 30 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1964 | 5 | 31 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1964 | 6 | 1 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1964 | 6 | 2 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1964 | 6 | 3 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1964 | 6 | 4 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1964 | 6 | 5 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1964 | 6 | 6 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1964 | 6 | 7 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1964 | 6 | 8 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1964 | 6 | 9 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1964 | 6 | 10 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1964 | 6 | 11 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1964 | 6 | 12 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1964 | 6 | 13 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1964 | 6 | 14 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1964 | 6 | 15 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 6 | 16 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 6 | 17 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1964 | 6 | 18 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 6 | 19 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 6 | 20 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1964 | 6 | 21 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1964 | 6 | 22 | 12.5388 | 25 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1964 | 6 | 23 | 11.2327 | 25 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1964 | 6 | 24 | 11.2327 | 25 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1964 | 6 | 25 | 10.8408 | 25 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1964 | 6 | 26 | 9.5347 | 25 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1964 | 6 | 27 | 10.8408 | 25 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1964 | 6 | 28 | 11.2327 | 25 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1964 | 6 | 29 | 11.6245 | 25 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1964 | 6 | 30 | 14.3673 | 25 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 7 | 1 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1964 | 7 | 2 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1964 | 7 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1964 | 7 | 4 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1964 | 7 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1964 | 7 | 6 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1964 | 7 | 7 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1964 | 7 | 8 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1964 | 7 | 9 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1964 | 7 | 10 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1964 | 7 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1964 | 7 | 12 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1964 | 7 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1964 | 7 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1964 | 7 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1964 | 7 | 16 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1964 | 7 | 17 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1964 | 7 | 18 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1964 | 7 | 19 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1964 | 7 | 20 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1964 | 7 | 21 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1964 | 7 | 22 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1964 | 7 | 23 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1964 | 7 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1964 | 7 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1964 | 7 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1964 | 7 | 27 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1964 | 7 | 28 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1964 | 7 | 29 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1964 | 7 | 30 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1964 | 7 | 31 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1964 | 8 | 1 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1964 | 8 | 2 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1964 | 8 | 3 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1964 | 8 | 4 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1964 | 8 | 5 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1964 | 8 | 6 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 8 | 7 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1964 | 8 | 8 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 8 | 9 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1964 | 8 | 10 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 8 | 11 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 8 | 12 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 8 | 13 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1964 | 8 | 14 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1964 | 8 | 15 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1964 | 8 | 16 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1964 | 8 | 17 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 8 | 18 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1964 | 8 | 19 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1964 | 8 | 20 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 8 | 21 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1964 | 8 | 22 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 8 | 23 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1964 | 8 | 24 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1964 | 8 | 25 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1964 | 8 | 26 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1964 | 8 | 27 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1964 | 8 | 28 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1964 | 8 | 29 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1964 | 8 | 30 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1964 | 8 | 31 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1964 | 9 | 1 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 9 | 2 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1964 | 9 | 3 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 9 | 4 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 9 | 5 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 9 | 6 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 9 | 7 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1964 | 9 | 8 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1964 | 9 | 9 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1964 | 9 | 10 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1964 | 9 | 11 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1964 | 9 | 12 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1964 | 9 | 13 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1964 | 9 | 14 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1964 | 9 | 15 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 9 | 16 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1964 | 9 | 17 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 9 | 18 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 9 | 19 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 9 | 20 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1964 | 9 | 21 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1964 | 9 | 22 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1964 | 9 | 23 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1964 | 9 | 24 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1964 | 9 | 25 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1964 | 9 | 26 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1964 | 9 | 27 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1964 | 9 | 28 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1964 | 9 | 29 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 9 | 30 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 1 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1964 | 10 | 2 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1964 | 10 | 3 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1964 | 10 | 4 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 5 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 6 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 7 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1964 | 10 | 8 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1964 | 10 | 9 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 10 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 11 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1964 | 10 | 12 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1964 | 10 | 13 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 14 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 15 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 16 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 17 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1964 | 10 | 18 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1964 | 10 | 19 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1964 | 10 | 20 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 10 | 21 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1964 | 10 | 22 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1964 | 10 | 23 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1964 | 10 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1964 | 10 | 25 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1964 | 10 | 26 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1964 | 10 | 27 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 10 | 28 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1964 | 10 | 29 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 10 | 30 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 10 | 31 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 11 | 1 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 11 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 11 | 3 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 11 | 4 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 11 | 5 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1964 | 11 | 6 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1964 | 11 | 7 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1964 | 11 | 8 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1964 | 11 | 9 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1964 | 11 | 10 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1964 | 11 | 11 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1964 | 11 | 12 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1964 | 11 | 13 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1964 | 11 | 14 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1964 | 11 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 11 | 16 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1964 | 11 | 17 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 11 | 18 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1964 | 11 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1964 | 11 | 20 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1964 | 11 | 21 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1964 | 11 | 22 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1964 | 11 | 23 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1964 | 11 | 24 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1964 | 11 | 25 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1964 | 11 | 26 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1964 | 11 | 27 | 651.7551 | 15 | 636.7551 | 28.6965 | 139.3858 | 0.77441 | 27.9221 | 89.27% | 294.2358 | 276.5817 | 6637.9606
1964 | 11 | 28 | 279.5102 | 15 | 264.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1964 | 11 | 29 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1964 | 11 | 30 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1964 | 12 | 1 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1964 | 12 | 2 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1964 | 12 | 3 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1964 | 12 | 4 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1964 | 12 | 5 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1964 | 12 | 6 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1964 | 12 | 7 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1964 | 12 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1964 | 12 | 9 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1964 | 12 | 10 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1964 | 12 | 11 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1964 | 12 | 12 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1964 | 12 | 13 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1964 | 12 | 14 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1964 | 12 | 15 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1964 | 12 | 16 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1964 | 12 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1964 | 12 | 18 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1964 | 12 | 19 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1964 | 12 | 20 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1964 | 12 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1964 | 12 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1964 | 12 | 23 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1964 | 12 | 24 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1964 | 12 | 25 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1964 | 12 | 26 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1964 | 12 | 27 | 448 | 5 | 443 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1964 | 12 | 28 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1964 | 12 | 29 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1964 | 12 | 30 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1964 | 12 | 31 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1965 | 1 | 1 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1965 | 1 | 2 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1965 | 1 | 3 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1965 | 1 | 4 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1965 | 1 | 5 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1965 | 1 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1965 | 1 | 7 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1965 | 1 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1965 | 1 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1965 | 1 | 10 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1965 | 1 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1965 | 1 | 12 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1965 | 1 | 13 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1965 | 1 | 14 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1965 | 1 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1965 | 1 | 16 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1965 | 1 | 17 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1965 | 1 | 18 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1965 | 1 | 19 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1965 | 1 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1965 | 1 | 21 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1965 | 1 | 22 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1965 | 1 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1965 | 1 | 24 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1965 | 1 | 25 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1965 | 1 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1965 | 1 | 27 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1965 | 1 | 28 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1965 | 1 | 29 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1965 | 1 | 30 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1965 | 1 | 31 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1965 | 2 | 1 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1965 | 2 | 2 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1965 | 2 | 3 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1965 | 2 | 4 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1965 | 2 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1965 | 2 | 6 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1965 | 2 | 7 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1965 | 2 | 8 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1965 | 2 | 9 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1965 | 2 | 10 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1965 | 2 | 11 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1965 | 2 | 12 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1965 | 2 | 13 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1965 | 2 | 14 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1965 | 2 | 15 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1965 | 2 | 16 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1965 | 2 | 17 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1965 | 2 | 18 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1965 | 2 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1965 | 2 | 20 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1965 | 2 | 21 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1965 | 2 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1965 | 2 | 23 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1965 | 2 | 24 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1965 | 2 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1965 | 2 | 26 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1965 | 2 | 27 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1965 | 2 | 28 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1965 | 3 | 1 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1965 | 3 | 2 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1965 | 3 | 3 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1965 | 3 | 4 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1965 | 3 | 5 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1965 | 3 | 6 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1965 | 3 | 7 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1965 | 3 | 8 | 542.0408 | 25 | 517.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
1965 | 3 | 9 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1965 | 3 | 10 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1965 | 3 | 11 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1965 | 3 | 12 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1965 | 3 | 13 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1965 | 3 | 14 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1965 | 3 | 15 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1965 | 3 | 16 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1965 | 3 | 17 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1965 | 3 | 18 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1965 | 3 | 19 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1965 | 3 | 20 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1965 | 3 | 21 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1965 | 3 | 22 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1965 | 3 | 23 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1965 | 3 | 24 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1965 | 3 | 25 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1965 | 3 | 26 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1965 | 3 | 27 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1965 | 3 | 28 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1965 | 3 | 29 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1965 | 3 | 30 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1965 | 3 | 31 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1965 | 4 | 1 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1965 | 4 | 2 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1965 | 4 | 3 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1965 | 4 | 4 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1965 | 4 | 5 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1965 | 4 | 6 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1965 | 4 | 7 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1965 | 4 | 8 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1965 | 4 | 9 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1965 | 4 | 10 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1965 | 4 | 11 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1965 | 4 | 12 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1965 | 4 | 13 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1965 | 4 | 14 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1965 | 4 | 15 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1965 | 4 | 16 | 795.4286 | 25 | 770.4286 | 28.4091 | 139.3858 | 0.77441 | 27.6347 | 89.27% | 291.2079 | 273.7354 | 6569.6491
1965 | 4 | 17 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1965 | 4 | 18 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1965 | 4 | 19 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1965 | 4 | 20 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1965 | 4 | 21 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1965 | 4 | 22 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1965 | 4 | 23 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1965 | 4 | 24 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1965 | 4 | 25 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1965 | 4 | 26 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1965 | 4 | 27 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1965 | 4 | 28 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1965 | 4 | 29 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1965 | 4 | 30 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1965 | 5 | 1 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1965 | 5 | 2 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1965 | 5 | 3 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1965 | 5 | 4 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1965 | 5 | 5 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1965 | 5 | 6 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1965 | 5 | 7 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1965 | 5 | 8 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1965 | 5 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1965 | 5 | 10 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1965 | 5 | 11 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1965 | 5 | 12 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1965 | 5 | 13 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1965 | 5 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1965 | 5 | 15 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1965 | 5 | 16 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1965 | 5 | 17 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1965 | 5 | 18 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1965 | 5 | 19 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1965 | 5 | 20 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1965 | 5 | 21 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1965 | 5 | 22 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1965 | 5 | 23 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1965 | 5 | 24 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1965 | 5 | 25 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1965 | 5 | 26 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1965 | 5 | 27 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1965 | 5 | 28 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1965 | 5 | 29 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1965 | 5 | 30 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1965 | 5 | 31 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1965 | 6 | 1 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1965 | 6 | 2 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1965 | 6 | 3 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1965 | 6 | 4 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1965 | 6 | 5 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1965 | 6 | 6 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1965 | 6 | 7 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1965 | 6 | 8 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1965 | 6 | 9 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1965 | 6 | 10 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1965 | 6 | 11 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1965 | 6 | 12 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1965 | 6 | 13 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1965 | 6 | 14 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1965 | 6 | 15 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1965 | 6 | 16 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1965 | 6 | 17 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1965 | 6 | 18 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1965 | 6 | 19 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1965 | 6 | 20 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1965 | 6 | 21 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1965 | 6 | 22 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1965 | 6 | 23 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1965 | 6 | 24 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1965 | 6 | 25 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1965 | 6 | 26 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1965 | 6 | 27 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1965 | 6 | 28 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1965 | 6 | 29 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1965 | 6 | 30 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1965 | 7 | 1 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1965 | 7 | 2 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1965 | 7 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1965 | 7 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1965 | 7 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1965 | 7 | 6 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1965 | 7 | 7 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1965 | 7 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1965 | 7 | 9 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1965 | 7 | 10 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1965 | 7 | 11 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1965 | 7 | 12 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1965 | 7 | 13 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1965 | 7 | 14 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1965 | 7 | 15 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1965 | 7 | 16 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1965 | 7 | 17 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1965 | 7 | 18 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1965 | 7 | 19 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1965 | 7 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1965 | 7 | 21 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1965 | 7 | 22 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1965 | 7 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1965 | 7 | 24 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1965 | 7 | 25 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1965 | 7 | 26 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1965 | 7 | 27 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1965 | 7 | 28 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1965 | 7 | 29 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1965 | 7 | 30 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1965 | 7 | 31 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1965 | 8 | 1 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1965 | 8 | 2 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1965 | 8 | 3 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1965 | 8 | 4 | 4.5714 | 5 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1965 | 8 | 5 | 3.9184 | 5 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
1965 | 8 | 6 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1965 | 8 | 7 | 3.3959 | 5 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
1965 | 8 | 8 | 3.3959 | 5 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
1965 | 8 | 9 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1965 | 8 | 10 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1965 | 8 | 11 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1965 | 8 | 12 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1965 | 8 | 13 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1965 | 8 | 14 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1965 | 8 | 15 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1965 | 8 | 16 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1965 | 8 | 17 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1965 | 8 | 18 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1965 | 8 | 19 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1965 | 8 | 20 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1965 | 8 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1965 | 8 | 22 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1965 | 8 | 23 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1965 | 8 | 24 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1965 | 8 | 25 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1965 | 8 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1965 | 8 | 27 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1965 | 8 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1965 | 8 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1965 | 8 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1965 | 8 | 31 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1965 | 9 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1965 | 9 | 2 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1965 | 9 | 3 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1965 | 9 | 4 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1965 | 9 | 5 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1965 | 9 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1965 | 9 | 7 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1965 | 9 | 8 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1965 | 9 | 9 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1965 | 9 | 10 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1965 | 9 | 11 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1965 | 9 | 12 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1965 | 9 | 13 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1965 | 9 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1965 | 9 | 15 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1965 | 9 | 16 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1965 | 9 | 17 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1965 | 9 | 18 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1965 | 9 | 19 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1965 | 9 | 20 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1965 | 9 | 21 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1965 | 9 | 22 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1965 | 9 | 23 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1965 | 9 | 24 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1965 | 9 | 25 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1965 | 9 | 26 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1965 | 9 | 27 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1965 | 9 | 28 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1965 | 9 | 29 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1965 | 9 | 30 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1965 | 10 | 1 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1965 | 10 | 2 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1965 | 10 | 3 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1965 | 10 | 4 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1965 | 10 | 5 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1965 | 10 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1965 | 10 | 7 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1965 | 10 | 8 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1965 | 10 | 9 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1965 | 10 | 10 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1965 | 10 | 11 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1965 | 10 | 12 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1965 | 10 | 13 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1965 | 10 | 14 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1965 | 10 | 15 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1965 | 10 | 16 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1965 | 10 | 17 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1965 | 10 | 18 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1965 | 10 | 19 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1965 | 10 | 20 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1965 | 10 | 21 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1965 | 10 | 22 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1965 | 10 | 23 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1965 | 10 | 24 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1965 | 10 | 25 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1965 | 10 | 26 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1965 | 10 | 27 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1965 | 10 | 28 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1965 | 10 | 29 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1965 | 10 | 30 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1965 | 10 | 31 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1965 | 11 | 1 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1965 | 11 | 2 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1965 | 11 | 3 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1965 | 11 | 4 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1965 | 11 | 5 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1965 | 11 | 6 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1965 | 11 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1965 | 11 | 8 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1965 | 11 | 9 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1965 | 11 | 10 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1965 | 11 | 11 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1965 | 11 | 12 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1965 | 11 | 13 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1965 | 11 | 14 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1965 | 11 | 15 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1965 | 11 | 16 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1965 | 11 | 17 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1965 | 11 | 18 | 323.9184 | 15 | 308.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1965 | 11 | 19 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1965 | 11 | 20 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1965 | 11 | 21 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1965 | 11 | 22 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1965 | 11 | 23 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1965 | 11 | 24 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1965 | 11 | 25 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1965 | 11 | 26 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1965 | 11 | 27 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1965 | 11 | 28 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1965 | 11 | 29 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1965 | 11 | 30 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1965 | 12 | 1 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1965 | 12 | 2 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1965 | 12 | 3 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1965 | 12 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1965 | 12 | 5 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1965 | 12 | 6 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1965 | 12 | 7 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1965 | 12 | 8 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1965 | 12 | 9 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1965 | 12 | 10 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1965 | 12 | 11 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1965 | 12 | 12 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1965 | 12 | 13 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1965 | 12 | 14 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1965 | 12 | 15 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1965 | 12 | 16 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1965 | 12 | 17 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1965 | 12 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1965 | 12 | 19 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1965 | 12 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1965 | 12 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1965 | 12 | 22 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1965 | 12 | 23 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1965 | 12 | 24 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1965 | 12 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1965 | 12 | 26 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1965 | 12 | 27 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1965 | 12 | 28 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1965 | 12 | 29 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1965 | 12 | 30 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1965 | 12 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1966 | 1 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1966 | 1 | 2 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1966 | 1 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1966 | 1 | 4 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1966 | 1 | 5 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1966 | 1 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1966 | 1 | 7 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1966 | 1 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1966 | 1 | 9 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1966 | 1 | 10 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1966 | 1 | 11 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1966 | 1 | 12 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1966 | 1 | 13 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 1 | 14 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1966 | 1 | 15 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 1 | 16 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 18 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 19 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 20 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 22 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 23 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 1 | 24 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 1 | 25 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1966 | 1 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1966 | 1 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1966 | 1 | 28 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1966 | 1 | 29 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 1 | 30 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 1 | 31 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 2 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1966 | 2 | 2 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1966 | 2 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1966 | 2 | 4 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1966 | 2 | 5 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1966 | 2 | 6 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 2 | 7 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 2 | 8 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 2 | 9 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1966 | 2 | 10 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1966 | 2 | 11 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1966 | 2 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1966 | 2 | 13 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1966 | 2 | 14 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1966 | 2 | 15 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1966 | 2 | 16 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1966 | 2 | 17 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1966 | 2 | 18 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1966 | 2 | 19 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1966 | 2 | 20 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1966 | 2 | 21 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1966 | 2 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1966 | 2 | 23 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1966 | 2 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1966 | 2 | 25 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1966 | 2 | 26 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1966 | 2 | 27 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1966 | 2 | 28 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1966 | 3 | 1 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1966 | 3 | 2 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1966 | 3 | 3 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1966 | 3 | 4 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1966 | 3 | 5 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1966 | 3 | 6 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1966 | 3 | 7 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1966 | 3 | 8 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1966 | 3 | 9 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1966 | 3 | 10 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1966 | 3 | 11 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1966 | 3 | 12 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1966 | 3 | 13 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1966 | 3 | 14 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1966 | 3 | 15 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1966 | 3 | 16 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1966 | 3 | 17 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1966 | 3 | 18 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1966 | 3 | 19 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1966 | 3 | 20 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1966 | 3 | 21 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1966 | 3 | 22 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1966 | 3 | 23 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1966 | 3 | 24 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1966 | 3 | 25 | 1099.7551 | 25 | 1074.7551 | 27.8005 | 139.3858 | 0.77441 | 27.0261 | 89.27% | 284.794 | 267.7064 | 6424.9531
1966 | 3 | 26 | 1671.8367 | 25 | 1646.8367 | 26.6563 | 139.3858 | 0.77441 | 25.8819 | 89.27% | 272.7371 | 256.3729 | 6152.9493
1966 | 3 | 27 | 974.3673 | 25 | 949.3673 | 28.0513 | 139.3858 | 0.77441 | 27.2769 | 89.27% | 287.4366 | 270.1904 | 6484.5703
1966 | 3 | 28 | 680.4898 | 25 | 655.4898 | 28.639 | 139.3858 | 0.77441 | 27.8646 | 89.27% | 293.6302 | 276.0124 | 6624.2983
1966 | 3 | 29 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1966 | 3 | 30 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1966 | 3 | 31 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1966 | 4 | 1 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1966 | 4 | 2 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1966 | 4 | 3 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1966 | 4 | 4 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1966 | 4 | 5 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1966 | 4 | 6 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1966 | 4 | 7 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1966 | 4 | 8 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1966 | 4 | 9 | 590.3673 | 25 | 565.3673 | 28.8193 | 139.3858 | 0.77441 | 28.0449 | 89.27% | 295.5296 | 277.7978 | 6667.1482
1966 | 4 | 10 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1966 | 4 | 11 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1966 | 4 | 12 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1966 | 4 | 13 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1966 | 4 | 14 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1966 | 4 | 15 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1966 | 4 | 16 | 808.4898 | 25 | 783.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
1966 | 4 | 17 | 860.7347 | 25 | 835.7347 | 28.2785 | 139.3858 | 0.77441 | 27.5041 | 89.27% | 289.8315 | 272.4416 | 6538.5985
1966 | 4 | 18 | 899.9184 | 25 | 874.9184 | 28.2002 | 139.3858 | 0.77441 | 27.4258 | 89.27% | 289.0057 | 271.6653 | 6519.9681
1966 | 4 | 19 | 882.9388 | 25 | 857.9388 | 28.2341 | 139.3858 | 0.77441 | 27.4597 | 89.27% | 289.3635 | 272.0017 | 6528.0413
1966 | 4 | 20 | 824.1633 | 25 | 799.1633 | 28.3517 | 139.3858 | 0.77441 | 27.5773 | 89.27% | 290.6023 | 273.1661 | 6555.9868
1966 | 4 | 21 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1966 | 4 | 22 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1966 | 4 | 23 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1966 | 4 | 24 | 747.102 | 25 | 722.102 | 28.5058 | 139.3858 | 0.77441 | 27.7314 | 89.27% | 292.2264 | 274.6928 | 6592.6266
1966 | 4 | 25 | 717.0612 | 25 | 692.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1966 | 4 | 26 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1966 | 4 | 27 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1966 | 4 | 28 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1966 | 4 | 29 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1966 | 4 | 30 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1966 | 5 | 1 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1966 | 5 | 2 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1966 | 5 | 3 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1966 | 5 | 4 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1966 | 5 | 5 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1966 | 5 | 6 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1966 | 5 | 7 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1966 | 5 | 8 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1966 | 5 | 9 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1966 | 5 | 10 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1966 | 5 | 11 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1966 | 5 | 12 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1966 | 5 | 13 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1966 | 5 | 14 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1966 | 5 | 15 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1966 | 5 | 16 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1966 | 5 | 17 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1966 | 5 | 18 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1966 | 5 | 19 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1966 | 5 | 20 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1966 | 5 | 21 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1966 | 5 | 22 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1966 | 5 | 23 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1966 | 5 | 24 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1966 | 5 | 25 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1966 | 5 | 26 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1966 | 5 | 27 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1966 | 5 | 28 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1966 | 5 | 29 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1966 | 5 | 30 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1966 | 5 | 31 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1966 | 6 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1966 | 6 | 2 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1966 | 6 | 3 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1966 | 6 | 4 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1966 | 6 | 5 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1966 | 6 | 6 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1966 | 6 | 7 | 489.7959 | 25 | 464.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
1966 | 6 | 8 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1966 | 6 | 9 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1966 | 6 | 10 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1966 | 6 | 11 | 576 | 25 | 551 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1966 | 6 | 12 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1966 | 6 | 13 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1966 | 6 | 14 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1966 | 6 | 15 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1966 | 6 | 16 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1966 | 6 | 17 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1966 | 6 | 18 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1966 | 6 | 19 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1966 | 6 | 20 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1966 | 6 | 21 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1966 | 6 | 22 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1966 | 6 | 23 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1966 | 6 | 24 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1966 | 6 | 25 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1966 | 6 | 26 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1966 | 6 | 27 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1966 | 6 | 28 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1966 | 6 | 29 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1966 | 6 | 30 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1966 | 7 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1966 | 7 | 2 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1966 | 7 | 3 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1966 | 7 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1966 | 7 | 5 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1966 | 7 | 6 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1966 | 7 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1966 | 7 | 8 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1966 | 7 | 9 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1966 | 7 | 10 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1966 | 7 | 11 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1966 | 7 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1966 | 7 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1966 | 7 | 14 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1966 | 7 | 15 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1966 | 7 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1966 | 7 | 17 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1966 | 7 | 18 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1966 | 7 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1966 | 7 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1966 | 7 | 21 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1966 | 7 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1966 | 7 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1966 | 7 | 24 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1966 | 7 | 25 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1966 | 7 | 26 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1966 | 7 | 27 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1966 | 7 | 28 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1966 | 7 | 29 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1966 | 7 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1966 | 7 | 31 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1966 | 8 | 1 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1966 | 8 | 2 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1966 | 8 | 3 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1966 | 8 | 4 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1966 | 8 | 5 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1966 | 8 | 6 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1966 | 8 | 7 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1966 | 8 | 8 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1966 | 8 | 9 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1966 | 8 | 10 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1966 | 8 | 11 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1966 | 8 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1966 | 8 | 13 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1966 | 8 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1966 | 8 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1966 | 8 | 16 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1966 | 8 | 17 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1966 | 8 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1966 | 8 | 19 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1966 | 8 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1966 | 8 | 21 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1966 | 8 | 22 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1966 | 8 | 23 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1966 | 8 | 24 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1966 | 8 | 25 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1966 | 8 | 26 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1966 | 8 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1966 | 8 | 28 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1966 | 8 | 29 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1966 | 8 | 30 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1966 | 8 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1966 | 9 | 1 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1966 | 9 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1966 | 9 | 3 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1966 | 9 | 4 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1966 | 9 | 5 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1966 | 9 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1966 | 9 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1966 | 9 | 8 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1966 | 9 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1966 | 9 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1966 | 9 | 11 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1966 | 9 | 12 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1966 | 9 | 13 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1966 | 9 | 14 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1966 | 9 | 15 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1966 | 9 | 16 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1966 | 9 | 17 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1966 | 9 | 18 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1966 | 9 | 19 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1966 | 9 | 20 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1966 | 9 | 21 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1966 | 9 | 22 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1966 | 9 | 23 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1966 | 9 | 24 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1966 | 9 | 25 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1966 | 9 | 26 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1966 | 9 | 27 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1966 | 9 | 28 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1966 | 9 | 29 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1966 | 9 | 30 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1966 | 10 | 1 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1966 | 10 | 2 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1966 | 10 | 3 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1966 | 10 | 4 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1966 | 10 | 5 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1966 | 10 | 6 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1966 | 10 | 7 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1966 | 10 | 8 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1966 | 10 | 9 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1966 | 10 | 10 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1966 | 10 | 11 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1966 | 10 | 12 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1966 | 10 | 13 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1966 | 10 | 14 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1966 | 10 | 15 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1966 | 10 | 16 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1966 | 10 | 17 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1966 | 10 | 18 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1966 | 10 | 19 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1966 | 10 | 20 | 446.6939 | 15 | 431.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1966 | 10 | 21 | 449.3061 | 15 | 434.3061 | 29.1014 | 139.3858 | 0.77441 | 28.327 | 89.27% | 298.5026 | 280.5924 | 6734.2176
1966 | 10 | 22 | 261.2245 | 15 | 246.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1966 | 10 | 23 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1966 | 10 | 24 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1966 | 10 | 25 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1966 | 10 | 26 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1966 | 10 | 27 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1966 | 10 | 28 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1966 | 10 | 29 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1966 | 10 | 30 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1966 | 10 | 31 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1966 | 11 | 1 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1966 | 11 | 2 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1966 | 11 | 3 | 1893.8776 | 15 | 1878.8776 | 26.2122 | 139.3858 | 0.77441 | 25.4378 | 89.27% | 268.0575 | 251.974 | 6047.3771
1966 | 11 | 4 | 2468.5714 | 15 | 2453.5714 | 25.0629 | 139.3858 | 0.77441 | 24.2884 | 89.27% | 255.9455 | 240.5888 | 5774.1313
1966 | 11 | 5 | 905.1429 | 15 | 890.1429 | 28.1897 | 139.3858 | 0.77441 | 27.4153 | 89.27% | 288.8956 | 271.5618 | 6517.484
1966 | 11 | 6 | 523.7551 | 15 | 508.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1966 | 11 | 7 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1966 | 11 | 8 | 297.7959 | 15 | 282.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1966 | 11 | 9 | 263.8367 | 15 | 248.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1966 | 11 | 10 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1966 | 11 | 11 | 263.8367 | 15 | 248.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1966 | 11 | 12 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1966 | 11 | 13 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1966 | 11 | 14 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1966 | 11 | 15 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1966 | 11 | 16 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1966 | 11 | 17 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1966 | 11 | 18 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1966 | 11 | 19 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1966 | 11 | 20 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1966 | 11 | 21 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1966 | 11 | 22 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1966 | 11 | 23 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1966 | 11 | 24 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1966 | 11 | 25 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1966 | 11 | 26 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1966 | 11 | 27 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1966 | 11 | 28 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1966 | 11 | 29 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1966 | 11 | 30 | 317.3878 | 15 | 302.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1966 | 12 | 1 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1966 | 12 | 2 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1966 | 12 | 3 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1966 | 12 | 4 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1966 | 12 | 5 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1966 | 12 | 6 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1966 | 12 | 7 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1966 | 12 | 8 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1966 | 12 | 9 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1966 | 12 | 10 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1966 | 12 | 11 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1966 | 12 | 12 | 218.1224 | 5 | 213.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1966 | 12 | 13 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1966 | 12 | 14 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1966 | 12 | 15 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1966 | 12 | 16 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1966 | 12 | 17 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1966 | 12 | 18 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1966 | 12 | 19 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1966 | 12 | 20 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1966 | 12 | 21 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1966 | 12 | 22 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1966 | 12 | 23 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1966 | 12 | 24 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1966 | 12 | 25 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1966 | 12 | 26 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1966 | 12 | 27 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1966 | 12 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1966 | 12 | 29 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1966 | 12 | 30 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1966 | 12 | 31 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1967 | 1 | 1 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1967 | 1 | 2 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1967 | 1 | 3 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1967 | 1 | 4 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1967 | 1 | 5 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1967 | 1 | 6 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1967 | 1 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 8 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1967 | 1 | 9 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1967 | 1 | 10 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1967 | 1 | 12 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 13 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1967 | 1 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 16 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1967 | 1 | 17 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 1 | 18 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1967 | 1 | 19 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1967 | 1 | 20 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1967 | 1 | 21 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1967 | 1 | 22 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1967 | 1 | 23 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1967 | 1 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1967 | 1 | 25 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1967 | 1 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1967 | 1 | 27 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1967 | 1 | 28 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 29 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1967 | 1 | 30 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 1 | 31 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 2 | 1 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1967 | 2 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1967 | 2 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 2 | 4 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1967 | 2 | 5 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 2 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1967 | 2 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1967 | 2 | 8 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1967 | 2 | 9 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1967 | 2 | 10 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1967 | 2 | 11 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1967 | 2 | 12 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1967 | 2 | 13 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 14 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 15 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 17 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 18 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 19 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 20 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 21 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 22 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 23 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 25 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 2 | 26 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1967 | 2 | 27 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1967 | 2 | 28 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1967 | 3 | 1 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1967 | 3 | 2 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1967 | 3 | 3 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1967 | 3 | 4 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1967 | 3 | 5 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1967 | 3 | 6 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1967 | 3 | 7 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1967 | 3 | 8 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1967 | 3 | 9 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1967 | 3 | 10 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1967 | 3 | 11 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1967 | 3 | 12 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1967 | 3 | 13 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1967 | 3 | 14 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1967 | 3 | 15 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1967 | 3 | 16 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1967 | 3 | 17 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1967 | 3 | 18 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1967 | 3 | 19 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1967 | 3 | 20 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1967 | 3 | 21 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1967 | 3 | 22 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1967 | 3 | 23 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1967 | 3 | 24 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1967 | 3 | 25 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1967 | 3 | 26 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1967 | 3 | 27 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1967 | 3 | 28 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1967 | 3 | 29 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1967 | 3 | 30 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1967 | 3 | 31 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1967 | 4 | 1 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1967 | 4 | 2 | 488.4898 | 25 | 463.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
1967 | 4 | 3 | 1076.2449 | 25 | 1051.2449 | 27.8475 | 139.3858 | 0.77441 | 27.0731 | 89.27% | 285.2895 | 268.1721 | 6436.1313
1967 | 4 | 4 | 1035.7551 | 25 | 1010.7551 | 27.9285 | 139.3858 | 0.77441 | 27.1541 | 89.27% | 286.1429 | 268.9743 | 6455.3827
1967 | 4 | 5 | 650.449 | 25 | 625.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
1967 | 4 | 6 | 547.2653 | 25 | 522.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1967 | 4 | 7 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1967 | 4 | 8 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1967 | 4 | 9 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1967 | 4 | 10 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1967 | 4 | 11 | 655.6735 | 25 | 630.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1967 | 4 | 12 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1967 | 4 | 13 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1967 | 4 | 14 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1967 | 4 | 15 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1967 | 4 | 16 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1967 | 4 | 17 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1967 | 4 | 18 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1967 | 4 | 19 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1967 | 4 | 20 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1967 | 4 | 21 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1967 | 4 | 22 | 690.9388 | 25 | 665.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
1967 | 4 | 23 | 706.6122 | 25 | 681.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
1967 | 4 | 24 | 666.1224 | 25 | 641.1224 | 28.6678 | 139.3858 | 0.77441 | 27.8933 | 89.27% | 293.933 | 276.2971 | 6631.1294
1967 | 4 | 25 | 625.6327 | 25 | 600.6327 | 28.7487 | 139.3858 | 0.77441 | 27.9743 | 89.27% | 294.7864 | 277.0992 | 6650.3808
1967 | 4 | 26 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1967 | 4 | 27 | 542.0408 | 25 | 517.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
1967 | 4 | 28 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1967 | 4 | 29 | 481.9592 | 25 | 456.9592 | 29.0361 | 139.3858 | 0.77441 | 28.2617 | 89.27% | 297.8144 | 279.9455 | 6718.6923
1967 | 4 | 30 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1967 | 5 | 1 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1967 | 5 | 2 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1967 | 5 | 3 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1967 | 5 | 4 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1967 | 5 | 5 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
1967 | 5 | 6 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1967 | 5 | 7 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1967 | 5 | 8 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1967 | 5 | 9 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1967 | 5 | 10 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
1967 | 5 | 11 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1967 | 5 | 12 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1967 | 5 | 13 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1967 | 5 | 14 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1967 | 5 | 15 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1967 | 5 | 16 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1967 | 5 | 17 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1967 | 5 | 18 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1967 | 5 | 19 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1967 | 5 | 20 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1967 | 5 | 21 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1967 | 5 | 22 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1967 | 5 | 23 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1967 | 5 | 24 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1967 | 5 | 25 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1967 | 5 | 26 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1967 | 5 | 27 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1967 | 5 | 28 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1967 | 5 | 29 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1967 | 5 | 30 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1967 | 5 | 31 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1967 | 6 | 1 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1967 | 6 | 2 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1967 | 6 | 3 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1967 | 6 | 4 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1967 | 6 | 5 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1967 | 6 | 6 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1967 | 6 | 7 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1967 | 6 | 8 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1967 | 6 | 9 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1967 | 6 | 10 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1967 | 6 | 11 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1967 | 6 | 12 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1967 | 6 | 13 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1967 | 6 | 14 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1967 | 6 | 15 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1967 | 6 | 16 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1967 | 6 | 17 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1967 | 6 | 18 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1967 | 6 | 19 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1967 | 6 | 20 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1967 | 6 | 21 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1967 | 6 | 22 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1967 | 6 | 23 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1967 | 6 | 24 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1967 | 6 | 25 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1967 | 6 | 26 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1967 | 6 | 27 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1967 | 6 | 28 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1967 | 6 | 29 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1967 | 6 | 30 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1967 | 7 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 7 | 2 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1967 | 7 | 3 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1967 | 7 | 4 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1967 | 7 | 5 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1967 | 7 | 6 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1967 | 7 | 7 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1967 | 7 | 8 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1967 | 7 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1967 | 7 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1967 | 7 | 11 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1967 | 7 | 12 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 7 | 13 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1967 | 7 | 14 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1967 | 7 | 15 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1967 | 7 | 16 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1967 | 7 | 17 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1967 | 7 | 18 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1967 | 7 | 19 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1967 | 7 | 20 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1967 | 7 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1967 | 7 | 22 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1967 | 7 | 23 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1967 | 7 | 24 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1967 | 7 | 25 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1967 | 7 | 26 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1967 | 7 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1967 | 7 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1967 | 7 | 29 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1967 | 7 | 30 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1967 | 7 | 31 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1967 | 8 | 1 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1967 | 8 | 2 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1967 | 8 | 3 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1967 | 8 | 4 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1967 | 8 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1967 | 8 | 6 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1967 | 8 | 7 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1967 | 8 | 8 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1967 | 8 | 9 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1967 | 8 | 10 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1967 | 8 | 11 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1967 | 8 | 12 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1967 | 8 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1967 | 8 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1967 | 8 | 15 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1967 | 8 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1967 | 8 | 17 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1967 | 8 | 18 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1967 | 8 | 19 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1967 | 8 | 20 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1967 | 8 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1967 | 8 | 22 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1967 | 8 | 23 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1967 | 8 | 24 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1967 | 8 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1967 | 8 | 26 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1967 | 8 | 27 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1967 | 8 | 28 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1967 | 8 | 29 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1967 | 8 | 30 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1967 | 8 | 31 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1967 | 9 | 1 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1967 | 9 | 2 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1967 | 9 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1967 | 9 | 4 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1967 | 9 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1967 | 9 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1967 | 9 | 7 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1967 | 9 | 8 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1967 | 9 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1967 | 9 | 10 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1967 | 9 | 11 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1967 | 9 | 12 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1967 | 9 | 13 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1967 | 9 | 14 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1967 | 9 | 15 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1967 | 9 | 16 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1967 | 9 | 17 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1967 | 9 | 18 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1967 | 9 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1967 | 9 | 20 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1967 | 9 | 21 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1967 | 9 | 22 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1967 | 9 | 23 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1967 | 9 | 24 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1967 | 9 | 25 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1967 | 9 | 26 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1967 | 9 | 27 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1967 | 9 | 28 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1967 | 9 | 29 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1967 | 9 | 30 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1967 | 10 | 1 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1967 | 10 | 2 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1967 | 10 | 3 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1967 | 10 | 4 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1967 | 10 | 5 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1967 | 10 | 6 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1967 | 10 | 7 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1967 | 10 | 8 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1967 | 10 | 9 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1967 | 10 | 10 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1967 | 10 | 11 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1967 | 10 | 12 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1967 | 10 | 13 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1967 | 10 | 14 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1967 | 10 | 15 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1967 | 10 | 16 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1967 | 10 | 17 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1967 | 10 | 18 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1967 | 10 | 19 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1967 | 10 | 20 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1967 | 10 | 21 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1967 | 10 | 22 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1967 | 10 | 23 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1967 | 10 | 24 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1967 | 10 | 25 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1967 | 10 | 26 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1967 | 10 | 27 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1967 | 10 | 28 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1967 | 10 | 29 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1967 | 10 | 30 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1967 | 10 | 31 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1967 | 11 | 1 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1967 | 11 | 2 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1967 | 11 | 3 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1967 | 11 | 4 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1967 | 11 | 5 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1967 | 11 | 6 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1967 | 11 | 7 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1967 | 11 | 8 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1967 | 11 | 9 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1967 | 11 | 10 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1967 | 11 | 11 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1967 | 11 | 12 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1967 | 11 | 13 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1967 | 11 | 14 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1967 | 11 | 15 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1967 | 11 | 16 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1967 | 11 | 17 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1967 | 11 | 18 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1967 | 11 | 19 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1967 | 11 | 20 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1967 | 11 | 21 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1967 | 11 | 22 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1967 | 11 | 23 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1967 | 11 | 24 | 350.0408 | 15 | 335.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1967 | 11 | 25 | 279.5102 | 15 | 264.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1967 | 11 | 26 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1967 | 11 | 27 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1967 | 11 | 28 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1967 | 11 | 29 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1967 | 11 | 30 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1967 | 12 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1967 | 12 | 2 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1967 | 12 | 3 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1967 | 12 | 4 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1967 | 12 | 5 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1967 | 12 | 6 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1967 | 12 | 7 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1967 | 12 | 8 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1967 | 12 | 9 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1967 | 12 | 10 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1967 | 12 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1967 | 12 | 12 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1967 | 12 | 13 | 464.9796 | 5 | 459.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1967 | 12 | 14 | 399.6735 | 5 | 394.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1967 | 12 | 15 | 284.7347 | 5 | 279.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1967 | 12 | 16 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1967 | 12 | 17 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1967 | 12 | 18 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1967 | 12 | 19 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1967 | 12 | 20 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1967 | 12 | 21 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1967 | 12 | 22 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1967 | 12 | 23 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1967 | 12 | 24 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1967 | 12 | 25 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1967 | 12 | 26 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1967 | 12 | 27 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1967 | 12 | 28 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1967 | 12 | 29 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1967 | 12 | 30 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1967 | 12 | 31 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1968 | 1 | 1 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1968 | 1 | 2 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1968 | 1 | 3 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1968 | 1 | 4 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1968 | 1 | 5 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1968 | 1 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1968 | 1 | 7 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1968 | 1 | 8 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1968 | 1 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1968 | 1 | 10 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1968 | 1 | 11 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1968 | 1 | 12 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1968 | 1 | 13 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1968 | 1 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1968 | 1 | 15 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1968 | 1 | 16 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1968 | 1 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1968 | 1 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1968 | 1 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1968 | 1 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1968 | 1 | 21 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1968 | 1 | 22 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1968 | 1 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1968 | 1 | 24 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1968 | 1 | 25 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1968 | 1 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1968 | 1 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1968 | 1 | 28 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1968 | 1 | 29 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1968 | 1 | 30 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1968 | 1 | 31 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1968 | 2 | 1 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1968 | 2 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1968 | 2 | 3 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1968 | 2 | 4 | 351.3469 | 5 | 346.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1968 | 2 | 5 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1968 | 2 | 6 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1968 | 2 | 7 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1968 | 2 | 8 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1968 | 2 | 9 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1968 | 2 | 10 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1968 | 2 | 11 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1968 | 2 | 12 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1968 | 2 | 13 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1968 | 2 | 14 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1968 | 2 | 15 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1968 | 2 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1968 | 2 | 17 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1968 | 2 | 18 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1968 | 2 | 19 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1968 | 2 | 20 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1968 | 2 | 21 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1968 | 2 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1968 | 2 | 23 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1968 | 2 | 24 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1968 | 2 | 25 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1968 | 2 | 26 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1968 | 2 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1968 | 2 | 28 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1968 | 2 | 29 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1968 | 3 | 1 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1968 | 3 | 2 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1968 | 3 | 3 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1968 | 3 | 4 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1968 | 3 | 5 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1968 | 3 | 6 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1968 | 3 | 7 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1968 | 3 | 8 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1968 | 3 | 9 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1968 | 3 | 10 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1968 | 3 | 11 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1968 | 3 | 12 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1968 | 3 | 13 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1968 | 3 | 14 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1968 | 3 | 15 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1968 | 3 | 16 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1968 | 3 | 17 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1968 | 3 | 18 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1968 | 3 | 19 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
1968 | 3 | 20 | 905.1429 | 25 | 880.1429 | 28.1897 | 139.3858 | 0.77441 | 27.4153 | 89.27% | 288.8956 | 271.5618 | 6517.484
1968 | 3 | 21 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1968 | 3 | 22 | 1129.7959 | 25 | 1104.7959 | 27.7404 | 139.3858 | 0.77441 | 26.966 | 89.27% | 284.1609 | 267.1112 | 6410.6698
1968 | 3 | 23 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1968 | 3 | 24 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1968 | 3 | 25 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1968 | 3 | 26 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1968 | 3 | 27 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
1968 | 3 | 28 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1968 | 3 | 29 | 777.1429 | 25 | 752.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1968 | 3 | 30 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1968 | 3 | 31 | 839.8367 | 25 | 814.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
1968 | 4 | 1 | 845.0612 | 25 | 820.0612 | 28.3099 | 139.3858 | 0.77441 | 27.5355 | 89.27% | 290.1618 | 272.7521 | 6546.0506
1968 | 4 | 2 | 701.3878 | 25 | 676.3878 | 28.5972 | 139.3858 | 0.77441 | 27.8228 | 89.27% | 293.1898 | 275.5984 | 6614.3621
1968 | 4 | 3 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1968 | 4 | 4 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
1968 | 4 | 5 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1968 | 4 | 6 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1968 | 4 | 7 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1968 | 4 | 8 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1968 | 4 | 9 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1968 | 4 | 10 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1968 | 4 | 11 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1968 | 4 | 12 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1968 | 4 | 13 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1968 | 4 | 14 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1968 | 4 | 15 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1968 | 4 | 16 | 824.1633 | 25 | 799.1633 | 28.3517 | 139.3858 | 0.77441 | 27.5773 | 89.27% | 290.6023 | 273.1661 | 6555.9868
1968 | 4 | 17 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1968 | 4 | 18 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1968 | 4 | 19 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1968 | 4 | 20 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1968 | 4 | 21 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1968 | 4 | 22 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1968 | 4 | 23 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1968 | 4 | 24 | 2951.8367 | 25 | 2926.8367 | 24.0963 | 0 | 0 | 24.0963 | 0% | 0 | 0 | 0
1968 | 4 | 25 | 2964.898 | 25 | 2939.898 | 24.0702 | 0 | 0 | 24.0702 | 0% | 0 | 0 | 0
1968 | 4 | 26 | 1724.0816 | 25 | 1699.0816 | 26.5518 | 139.3858 | 0.77441 | 25.7774 | 89.27% | 271.636 | 255.3379 | 6128.1088
1968 | 4 | 27 | 845.0612 | 25 | 820.0612 | 28.3099 | 139.3858 | 0.77441 | 27.5355 | 89.27% | 290.1618 | 272.7521 | 6546.0506
1968 | 4 | 28 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1968 | 4 | 29 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1968 | 4 | 30 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1968 | 5 | 1 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1968 | 5 | 2 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1968 | 5 | 3 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1968 | 5 | 4 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1968 | 5 | 5 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1968 | 5 | 6 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1968 | 5 | 7 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1968 | 5 | 8 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1968 | 5 | 9 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1968 | 5 | 10 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1968 | 5 | 11 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1968 | 5 | 12 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1968 | 5 | 13 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1968 | 5 | 14 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1968 | 5 | 15 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1968 | 5 | 16 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1968 | 5 | 17 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1968 | 5 | 18 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1968 | 5 | 19 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1968 | 5 | 20 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1968 | 5 | 21 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1968 | 5 | 22 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1968 | 5 | 23 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1968 | 5 | 24 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1968 | 5 | 25 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1968 | 5 | 26 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1968 | 5 | 27 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1968 | 5 | 28 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1968 | 5 | 29 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1968 | 5 | 30 | 393.1429 | 25 | 368.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1968 | 5 | 31 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1968 | 6 | 1 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1968 | 6 | 2 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1968 | 6 | 3 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1968 | 6 | 4 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1968 | 6 | 5 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1968 | 6 | 6 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1968 | 6 | 7 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1968 | 6 | 8 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1968 | 6 | 9 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1968 | 6 | 10 | 707.9184 | 25 | 682.9184 | 28.5842 | 139.3858 | 0.77441 | 27.8098 | 89.27% | 293.0522 | 275.469 | 6611.257
1968 | 6 | 11 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1968 | 6 | 12 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1968 | 6 | 13 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1968 | 6 | 14 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1968 | 6 | 15 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1968 | 6 | 16 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1968 | 6 | 17 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1968 | 6 | 18 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1968 | 6 | 19 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1968 | 6 | 20 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1968 | 6 | 21 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1968 | 6 | 22 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1968 | 6 | 23 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1968 | 6 | 24 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1968 | 6 | 25 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1968 | 6 | 26 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1968 | 6 | 27 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1968 | 6 | 28 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1968 | 6 | 29 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1968 | 6 | 30 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1968 | 7 | 1 | 304.3265 | 5 | 299.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1968 | 7 | 2 | 329.1429 | 5 | 324.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1968 | 7 | 3 | 218.1224 | 5 | 213.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1968 | 7 | 4 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1968 | 7 | 5 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1968 | 7 | 6 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1968 | 7 | 7 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1968 | 7 | 8 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1968 | 7 | 9 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1968 | 7 | 10 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1968 | 7 | 11 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1968 | 7 | 12 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1968 | 7 | 13 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1968 | 7 | 14 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1968 | 7 | 15 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1968 | 7 | 16 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1968 | 7 | 17 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1968 | 7 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1968 | 7 | 19 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1968 | 7 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1968 | 7 | 21 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1968 | 7 | 22 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1968 | 7 | 23 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1968 | 7 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1968 | 7 | 25 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1968 | 7 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1968 | 7 | 27 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1968 | 7 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1968 | 7 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1968 | 7 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1968 | 7 | 31 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1968 | 8 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1968 | 8 | 2 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1968 | 8 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1968 | 8 | 4 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1968 | 8 | 5 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1968 | 8 | 6 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1968 | 8 | 7 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1968 | 8 | 8 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1968 | 8 | 9 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1968 | 8 | 10 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1968 | 8 | 11 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1968 | 8 | 12 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1968 | 8 | 13 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1968 | 8 | 14 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1968 | 8 | 15 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1968 | 8 | 16 | 4.5714 | 5 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1968 | 8 | 17 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1968 | 8 | 18 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1968 | 8 | 19 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1968 | 8 | 20 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1968 | 8 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1968 | 8 | 22 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1968 | 8 | 23 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1968 | 8 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1968 | 8 | 25 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1968 | 8 | 26 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1968 | 8 | 27 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1968 | 8 | 28 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1968 | 8 | 29 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1968 | 8 | 30 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1968 | 8 | 31 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1968 | 9 | 1 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1968 | 9 | 2 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1968 | 9 | 3 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1968 | 9 | 4 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1968 | 9 | 5 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1968 | 9 | 6 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1968 | 9 | 7 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1968 | 9 | 8 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1968 | 9 | 9 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1968 | 9 | 10 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1968 | 9 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1968 | 9 | 12 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1968 | 9 | 13 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1968 | 9 | 14 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1968 | 9 | 15 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1968 | 9 | 16 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1968 | 9 | 17 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1968 | 9 | 18 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1968 | 9 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1968 | 9 | 20 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1968 | 9 | 21 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1968 | 9 | 22 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1968 | 9 | 23 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1968 | 9 | 24 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1968 | 9 | 25 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1968 | 9 | 26 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1968 | 9 | 27 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1968 | 9 | 28 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1968 | 9 | 29 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1968 | 9 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1968 | 10 | 1 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1968 | 10 | 2 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1968 | 10 | 3 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1968 | 10 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1968 | 10 | 5 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1968 | 10 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1968 | 10 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1968 | 10 | 8 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1968 | 10 | 9 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1968 | 10 | 10 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1968 | 10 | 11 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1968 | 10 | 12 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1968 | 10 | 13 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1968 | 10 | 14 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1968 | 10 | 15 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1968 | 10 | 16 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1968 | 10 | 17 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1968 | 10 | 18 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1968 | 10 | 19 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1968 | 10 | 20 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1968 | 10 | 21 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1968 | 10 | 22 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1968 | 10 | 23 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1968 | 10 | 24 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1968 | 10 | 25 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1968 | 10 | 26 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1968 | 10 | 27 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1968 | 10 | 28 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1968 | 10 | 29 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1968 | 10 | 30 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1968 | 10 | 31 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1968 | 11 | 1 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1968 | 11 | 2 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1968 | 11 | 3 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1968 | 11 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1968 | 11 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1968 | 11 | 6 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1968 | 11 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1968 | 11 | 8 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1968 | 11 | 9 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1968 | 11 | 10 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1968 | 11 | 11 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1968 | 11 | 12 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1968 | 11 | 13 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1968 | 11 | 14 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1968 | 11 | 15 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1968 | 11 | 16 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1968 | 11 | 17 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1968 | 11 | 18 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1968 | 11 | 19 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1968 | 11 | 20 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1968 | 11 | 21 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1968 | 11 | 22 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1968 | 11 | 23 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1968 | 11 | 24 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1968 | 11 | 25 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1968 | 11 | 26 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1968 | 11 | 27 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1968 | 11 | 28 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1968 | 11 | 29 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1968 | 11 | 30 | 282.1224 | 15 | 267.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1968 | 12 | 1 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1968 | 12 | 2 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1968 | 12 | 3 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1968 | 12 | 4 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1968 | 12 | 5 | 606.0408 | 5 | 601.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1968 | 12 | 6 | 509.3878 | 5 | 504.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1968 | 12 | 7 | 323.9184 | 5 | 318.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1968 | 12 | 8 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1968 | 12 | 9 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1968 | 12 | 10 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1968 | 12 | 11 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1968 | 12 | 12 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1968 | 12 | 13 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1968 | 12 | 14 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1968 | 12 | 15 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1968 | 12 | 16 | 522.449 | 5 | 517.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1968 | 12 | 17 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1968 | 12 | 18 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1968 | 12 | 19 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1968 | 12 | 20 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1968 | 12 | 21 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1968 | 12 | 22 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1968 | 12 | 23 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1968 | 12 | 24 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1968 | 12 | 25 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1968 | 12 | 26 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1968 | 12 | 27 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1968 | 12 | 28 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1968 | 12 | 29 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1968 | 12 | 30 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1968 | 12 | 31 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1969 | 1 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1969 | 1 | 2 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1969 | 1 | 3 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1969 | 1 | 4 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1969 | 1 | 5 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1969 | 1 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1969 | 1 | 7 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1969 | 1 | 8 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1969 | 1 | 9 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1969 | 1 | 10 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1969 | 1 | 11 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1969 | 1 | 12 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1969 | 1 | 13 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1969 | 1 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1969 | 1 | 15 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1969 | 1 | 16 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1969 | 1 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1969 | 1 | 18 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1969 | 1 | 19 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1969 | 1 | 20 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1969 | 1 | 21 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1969 | 1 | 22 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1969 | 1 | 23 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1969 | 1 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1969 | 1 | 25 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1969 | 1 | 26 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1969 | 1 | 27 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1969 | 1 | 28 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1969 | 1 | 29 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1969 | 1 | 30 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1969 | 1 | 31 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1969 | 2 | 1 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1969 | 2 | 2 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1969 | 2 | 3 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1969 | 2 | 4 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1969 | 2 | 5 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1969 | 2 | 6 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1969 | 2 | 7 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1969 | 2 | 8 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1969 | 2 | 9 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1969 | 2 | 10 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1969 | 2 | 11 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1969 | 2 | 12 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1969 | 2 | 13 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1969 | 2 | 14 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1969 | 2 | 15 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1969 | 2 | 16 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1969 | 2 | 17 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1969 | 2 | 18 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1969 | 2 | 19 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1969 | 2 | 20 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1969 | 2 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1969 | 2 | 22 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1969 | 2 | 23 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1969 | 2 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1969 | 2 | 25 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1969 | 2 | 26 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1969 | 2 | 27 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1969 | 2 | 28 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1969 | 3 | 1 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1969 | 3 | 2 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1969 | 3 | 3 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1969 | 3 | 4 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1969 | 3 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1969 | 3 | 6 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1969 | 3 | 7 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1969 | 3 | 8 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1969 | 3 | 9 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1969 | 3 | 10 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1969 | 3 | 11 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1969 | 3 | 12 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1969 | 3 | 13 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1969 | 3 | 14 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1969 | 3 | 15 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1969 | 3 | 16 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1969 | 3 | 17 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1969 | 3 | 18 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1969 | 3 | 19 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1969 | 3 | 20 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1969 | 3 | 21 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1969 | 3 | 22 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1969 | 3 | 23 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1969 | 3 | 24 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1969 | 3 | 25 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1969 | 3 | 26 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1969 | 3 | 27 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1969 | 3 | 28 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1969 | 3 | 29 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1969 | 3 | 30 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1969 | 3 | 31 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1969 | 4 | 1 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1969 | 4 | 2 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1969 | 4 | 3 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1969 | 4 | 4 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1969 | 4 | 5 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1969 | 4 | 6 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1969 | 4 | 7 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1969 | 4 | 8 | 581.2245 | 25 | 556.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1969 | 4 | 9 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1969 | 4 | 10 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1969 | 4 | 11 | 1050.1224 | 25 | 1025.1224 | 27.8998 | 139.3858 | 0.77441 | 27.1253 | 89.27% | 285.8401 | 268.6896 | 6448.5516
1969 | 4 | 12 | 1043.5918 | 25 | 1018.5918 | 27.9128 | 139.3858 | 0.77441 | 27.1384 | 89.27% | 285.9777 | 268.819 | 6451.6566
1969 | 4 | 13 | 877.7143 | 25 | 852.7143 | 28.2446 | 139.3858 | 0.77441 | 27.4702 | 89.27% | 289.4736 | 272.1052 | 6530.5253
1969 | 4 | 14 | 1093.2245 | 25 | 1068.2245 | 27.8136 | 139.3858 | 0.77441 | 27.0391 | 89.27% | 284.9317 | 267.8358 | 6428.0581
1969 | 4 | 15 | 1541.2245 | 25 | 1516.2245 | 26.9176 | 139.3858 | 0.77441 | 26.1431 | 89.27% | 275.4898 | 258.9604 | 6215.0506
1969 | 4 | 16 | 1854.6939 | 25 | 1829.6939 | 26.2906 | 139.3858 | 0.77441 | 25.5162 | 89.27% | 268.8833 | 252.7503 | 6066.0075
1969 | 4 | 17 | 2155.102 | 25 | 2130.102 | 25.6898 | 139.3858 | 0.77441 | 24.9154 | 89.27% | 262.5521 | 246.7989 | 5923.1744
1969 | 4 | 18 | 2220.4082 | 25 | 2195.4082 | 25.5592 | 139.3858 | 0.77441 | 24.7848 | 89.27% | 261.1757 | 245.5052 | 5892.1238
1969 | 4 | 19 | 2625.3061 | 25 | 2600.3061 | 24.7494 | 0 | 0 | 24.7494 | 0% | 0 | 0 | 0
1969 | 4 | 20 | 1567.3469 | 25 | 1542.3469 | 26.8653 | 139.3858 | 0.77441 | 26.0909 | 89.27% | 274.9393 | 258.4429 | 6202.6304
1969 | 4 | 21 | 1086.6939 | 25 | 1061.6939 | 27.8266 | 139.3858 | 0.77441 | 27.0522 | 89.27% | 285.0693 | 267.9651 | 6431.1632
1969 | 4 | 22 | 1003.102 | 25 | 978.102 | 27.9938 | 139.3858 | 0.77441 | 27.2194 | 89.27% | 286.831 | 269.6212 | 6470.908
1969 | 4 | 23 | 2220.4082 | 25 | 2195.4082 | 25.5592 | 139.3858 | 0.77441 | 24.7848 | 89.27% | 261.1757 | 245.5052 | 5892.1238
1969 | 4 | 24 | 2102.8571 | 25 | 2077.8571 | 25.7943 | 139.3858 | 0.77441 | 25.0199 | 89.27% | 263.6531 | 247.834 | 5948.015
1969 | 4 | 25 | 1295.6735 | 25 | 1270.6735 | 27.4087 | 139.3858 | 0.77441 | 26.6342 | 89.27% | 280.6649 | 263.825 | 6331.8011
1969 | 4 | 26 | 1175.5102 | 25 | 1150.5102 | 27.649 | 139.3858 | 0.77441 | 26.8746 | 89.27% | 283.1974 | 266.2056 | 6388.9343
1969 | 4 | 27 | 1098.449 | 25 | 1073.449 | 27.8031 | 139.3858 | 0.77441 | 27.0287 | 89.27% | 284.8215 | 267.7323 | 6425.5741
1969 | 4 | 28 | 1111.5102 | 25 | 1086.5102 | 27.777 | 139.3858 | 0.77441 | 27.0026 | 89.27% | 284.5463 | 267.4735 | 6419.3639
1969 | 4 | 29 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1969 | 4 | 30 | 1287.8367 | 25 | 1262.8367 | 27.4243 | 139.3858 | 0.77441 | 26.6499 | 89.27% | 280.8301 | 263.9803 | 6335.5272
1969 | 5 | 1 | 1003.102 | 25 | 978.102 | 27.9938 | 139.3858 | 0.77441 | 27.2194 | 89.27% | 286.831 | 269.6212 | 6470.908
1969 | 5 | 2 | 877.7143 | 25 | 852.7143 | 28.2446 | 139.3858 | 0.77441 | 27.4702 | 89.27% | 289.4736 | 272.1052 | 6530.5253
1969 | 5 | 3 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1969 | 5 | 4 | 768 | 25 | 743 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
1969 | 5 | 5 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1969 | 5 | 6 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1969 | 5 | 7 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1969 | 5 | 8 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1969 | 5 | 9 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1969 | 5 | 10 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1969 | 5 | 11 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1969 | 5 | 12 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1969 | 5 | 13 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1969 | 5 | 14 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1969 | 5 | 15 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1969 | 5 | 16 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1969 | 5 | 17 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1969 | 5 | 18 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1969 | 5 | 19 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1969 | 5 | 20 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1969 | 5 | 21 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1969 | 5 | 22 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1969 | 5 | 23 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1969 | 5 | 24 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1969 | 5 | 25 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1969 | 5 | 26 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1969 | 5 | 27 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1969 | 5 | 28 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1969 | 5 | 29 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1969 | 5 | 30 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1969 | 5 | 31 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1969 | 6 | 1 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1969 | 6 | 2 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1969 | 6 | 3 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1969 | 6 | 4 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1969 | 6 | 5 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1969 | 6 | 6 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1969 | 6 | 7 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1969 | 6 | 8 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1969 | 6 | 9 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1969 | 6 | 10 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1969 | 6 | 11 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1969 | 6 | 12 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1969 | 6 | 13 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1969 | 6 | 14 | 1074.9388 | 25 | 1049.9388 | 27.8501 | 139.3858 | 0.77441 | 27.0757 | 89.27% | 285.317 | 268.198 | 6436.7523
1969 | 6 | 15 | 474.1224 | 25 | 449.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
1969 | 6 | 16 | 841.1429 | 25 | 816.1429 | 28.3177 | 139.3858 | 0.77441 | 27.5433 | 89.27% | 290.2444 | 272.8297 | 6547.9137
1969 | 6 | 17 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1969 | 6 | 18 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1969 | 6 | 19 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1969 | 6 | 20 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1969 | 6 | 21 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1969 | 6 | 22 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1969 | 6 | 23 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1969 | 6 | 24 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1969 | 6 | 25 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1969 | 6 | 26 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1969 | 6 | 27 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1969 | 6 | 28 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1969 | 6 | 29 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1969 | 6 | 30 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1969 | 7 | 1 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1969 | 7 | 2 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1969 | 7 | 3 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1969 | 7 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1969 | 7 | 5 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1969 | 7 | 6 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1969 | 7 | 7 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1969 | 7 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1969 | 7 | 9 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1969 | 7 | 10 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1969 | 7 | 11 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1969 | 7 | 12 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1969 | 7 | 13 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1969 | 7 | 14 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1969 | 7 | 15 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1969 | 7 | 16 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1969 | 7 | 17 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1969 | 7 | 18 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1969 | 7 | 19 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1969 | 7 | 20 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1969 | 7 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1969 | 7 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1969 | 7 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1969 | 7 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1969 | 7 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1969 | 7 | 26 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1969 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1969 | 7 | 28 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1969 | 7 | 29 | 340.898 | 5 | 335.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
1969 | 7 | 30 | 421.8776 | 5 | 416.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1969 | 7 | 31 | 304.3265 | 5 | 299.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1969 | 8 | 1 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1969 | 8 | 2 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1969 | 8 | 3 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1969 | 8 | 4 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1969 | 8 | 5 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1969 | 8 | 6 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1969 | 8 | 7 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1969 | 8 | 8 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1969 | 8 | 9 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1969 | 8 | 10 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1969 | 8 | 11 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1969 | 8 | 12 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1969 | 8 | 13 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1969 | 8 | 14 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1969 | 8 | 15 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1969 | 8 | 16 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1969 | 8 | 17 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1969 | 8 | 18 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1969 | 8 | 19 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1969 | 8 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1969 | 8 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1969 | 8 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1969 | 8 | 23 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1969 | 8 | 24 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1969 | 8 | 25 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1969 | 8 | 26 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1969 | 8 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1969 | 8 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1969 | 8 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1969 | 8 | 30 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1969 | 8 | 31 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1969 | 9 | 1 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1969 | 9 | 2 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1969 | 9 | 3 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 9 | 4 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1969 | 9 | 5 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1969 | 9 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 9 | 7 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 9 | 8 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1969 | 9 | 9 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1969 | 9 | 10 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1969 | 9 | 11 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1969 | 9 | 12 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1969 | 9 | 13 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1969 | 9 | 14 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1969 | 9 | 15 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1969 | 9 | 16 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1969 | 9 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1969 | 9 | 18 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1969 | 9 | 19 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1969 | 9 | 20 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1969 | 9 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1969 | 9 | 22 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 9 | 23 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1969 | 9 | 24 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1969 | 9 | 25 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1969 | 9 | 26 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1969 | 9 | 27 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1969 | 9 | 28 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1969 | 9 | 29 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1969 | 9 | 30 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 10 | 1 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1969 | 10 | 2 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1969 | 10 | 3 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1969 | 10 | 4 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1969 | 10 | 5 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1969 | 10 | 6 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1969 | 10 | 7 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1969 | 10 | 8 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 10 | 9 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 10 | 10 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1969 | 10 | 11 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1969 | 10 | 12 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 10 | 13 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 10 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 10 | 15 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1969 | 10 | 16 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1969 | 10 | 17 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1969 | 10 | 18 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1969 | 10 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1969 | 10 | 20 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1969 | 10 | 21 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1969 | 10 | 22 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 10 | 23 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1969 | 10 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 10 | 25 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1969 | 10 | 26 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1969 | 10 | 27 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1969 | 10 | 28 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1969 | 10 | 29 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1969 | 10 | 30 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1969 | 10 | 31 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 11 | 1 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 11 | 2 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1969 | 11 | 3 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1969 | 11 | 4 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1969 | 11 | 5 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1969 | 11 | 6 | 1255.1837 | 15 | 1240.1837 | 27.4896 | 139.3858 | 0.77441 | 26.7152 | 89.27% | 281.5183 | 264.6272 | 6351.0525
1969 | 11 | 7 | 1273.4694 | 15 | 1258.4694 | 27.4531 | 139.3858 | 0.77441 | 26.6787 | 89.27% | 281.1329 | 264.2649 | 6342.3583
1969 | 11 | 8 | 1802.449 | 15 | 1787.449 | 26.3951 | 139.3858 | 0.77441 | 25.6207 | 89.27% | 269.9844 | 253.7853 | 6090.848
1969 | 11 | 9 | 1084.0816 | 15 | 1069.0816 | 27.8318 | 139.3858 | 0.77441 | 27.0574 | 89.27% | 285.1243 | 268.0169 | 6432.4052
1969 | 11 | 10 | 630.8571 | 15 | 615.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1969 | 11 | 11 | 547.2653 | 15 | 532.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1969 | 11 | 12 | 720.9796 | 15 | 705.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1969 | 11 | 13 | 547.2653 | 15 | 532.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1969 | 11 | 14 | 421.8776 | 15 | 406.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1969 | 11 | 15 | 431.0204 | 15 | 416.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1969 | 11 | 16 | 342.2041 | 15 | 327.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1969 | 11 | 17 | 279.5102 | 15 | 264.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1969 | 11 | 18 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1969 | 11 | 19 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1969 | 11 | 20 | 841.1429 | 15 | 826.1429 | 28.3177 | 139.3858 | 0.77441 | 27.5433 | 89.27% | 290.2444 | 272.8297 | 6547.9137
1969 | 11 | 21 | 1125.8776 | 15 | 1110.8776 | 27.7482 | 139.3858 | 0.77441 | 26.9738 | 89.27% | 284.2435 | 267.1889 | 6412.5328
1969 | 11 | 22 | 576 | 15 | 561 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1969 | 11 | 23 | 377.4694 | 15 | 362.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1969 | 11 | 24 | 314.7755 | 15 | 299.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1969 | 11 | 25 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1969 | 11 | 26 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1969 | 11 | 27 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1969 | 11 | 28 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1969 | 11 | 29 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1969 | 11 | 30 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1969 | 12 | 1 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1969 | 12 | 2 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1969 | 12 | 3 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1969 | 12 | 4 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1969 | 12 | 5 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1969 | 12 | 6 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1969 | 12 | 7 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1969 | 12 | 8 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1969 | 12 | 9 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1969 | 12 | 10 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1969 | 12 | 11 | 1264.3265 | 5 | 1259.3265 | 27.4713 | 139.3858 | 0.77441 | 26.6969 | 89.27% | 281.3256 | 264.4461 | 6346.7054
1969 | 12 | 12 | 1554.2857 | 5 | 1549.2857 | 26.8914 | 139.3858 | 0.77441 | 26.117 | 89.27% | 275.2146 | 258.7017 | 6208.8405
1969 | 12 | 13 | 731.4286 | 5 | 726.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1969 | 12 | 14 | 464.9796 | 5 | 459.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1969 | 12 | 15 | 351.3469 | 5 | 346.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1969 | 12 | 16 | 292.5714 | 5 | 287.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1969 | 12 | 17 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1969 | 12 | 18 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1969 | 12 | 19 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1969 | 12 | 20 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1969 | 12 | 21 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1969 | 12 | 22 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1969 | 12 | 23 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1969 | 12 | 24 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1969 | 12 | 25 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1969 | 12 | 26 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1969 | 12 | 27 | 770.6122 | 5 | 765.6122 | 28.4588 | 139.3858 | 0.77441 | 27.6844 | 89.27% | 291.7309 | 274.227 | 6581.4484
1969 | 12 | 28 | 3382.8571 | 5 | 3377.8571 | 23.2343 | 0 | 0 | 23.2343 | 0% | 0 | 0 | 0
1969 | 12 | 29 | 1776.3265 | 5 | 1771.3265 | 26.4473 | 139.3858 | 0.77441 | 25.6729 | 89.27% | 270.5349 | 254.3028 | 6103.2683
1969 | 12 | 30 | 996.5714 | 5 | 991.5714 | 28.0069 | 139.3858 | 0.77441 | 27.2324 | 89.27% | 286.9687 | 269.7505 | 6474.0131
1969 | 12 | 31 | 706.6122 | 5 | 701.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
1970 | 1 | 1 | 556.4082 | 5 | 551.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1970 | 1 | 2 | 399.6735 | 5 | 394.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1970 | 1 | 3 | 329.1429 | 5 | 324.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1970 | 1 | 4 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1970 | 1 | 5 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1970 | 1 | 6 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1970 | 1 | 7 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1970 | 1 | 8 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1970 | 1 | 9 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1970 | 1 | 10 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1970 | 1 | 11 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1970 | 1 | 12 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1970 | 1 | 13 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1970 | 1 | 14 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1970 | 1 | 15 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1970 | 1 | 16 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1970 | 1 | 17 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1970 | 1 | 18 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1970 | 1 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1970 | 1 | 20 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1970 | 1 | 21 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1970 | 1 | 22 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1970 | 1 | 23 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1970 | 1 | 24 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1970 | 1 | 25 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1970 | 1 | 26 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1970 | 1 | 27 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1970 | 1 | 28 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1970 | 1 | 29 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1970 | 1 | 30 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1970 | 1 | 31 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1970 | 2 | 1 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1970 | 2 | 2 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1970 | 2 | 3 | 279.5102 | 5 | 274.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1970 | 2 | 4 | 1815.5102 | 5 | 1810.5102 | 26.369 | 139.3858 | 0.77441 | 25.5946 | 89.27% | 269.7091 | 253.5266 | 6084.6379
1970 | 2 | 5 | 996.5714 | 5 | 991.5714 | 28.0069 | 139.3858 | 0.77441 | 27.2324 | 89.27% | 286.9687 | 269.7505 | 6474.0131
1970 | 2 | 6 | 595.5918 | 5 | 590.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1970 | 2 | 7 | 410.1224 | 5 | 405.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1970 | 2 | 8 | 333.0612 | 5 | 328.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1970 | 2 | 9 | 295.1837 | 5 | 290.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1970 | 2 | 10 | 266.449 | 5 | 261.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1970 | 2 | 11 | 2050.6122 | 5 | 2045.6122 | 25.8988 | 139.3858 | 0.77441 | 25.1244 | 89.27% | 264.7542 | 248.869 | 5972.8555
1970 | 2 | 12 | 2429.3878 | 5 | 2424.3878 | 25.1412 | 139.3858 | 0.77441 | 24.3668 | 89.27% | 256.7714 | 241.3651 | 5792.7617
1970 | 2 | 13 | 679.1837 | 5 | 674.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
1970 | 2 | 14 | 581.2245 | 5 | 576.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1970 | 2 | 15 | 411.4286 | 5 | 406.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1970 | 2 | 16 | 338.2857 | 5 | 333.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1970 | 2 | 17 | 284.7347 | 5 | 279.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1970 | 2 | 18 | 266.449 | 5 | 261.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1970 | 2 | 19 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1970 | 2 | 20 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1970 | 2 | 21 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1970 | 2 | 22 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1970 | 2 | 23 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1970 | 2 | 24 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1970 | 2 | 25 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1970 | 2 | 26 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1970 | 2 | 27 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1970 | 2 | 28 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1970 | 3 | 1 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1970 | 3 | 2 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1970 | 3 | 3 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1970 | 3 | 4 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1970 | 3 | 5 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1970 | 3 | 6 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1970 | 3 | 7 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1970 | 3 | 8 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1970 | 3 | 9 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1970 | 3 | 10 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1970 | 3 | 11 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1970 | 3 | 12 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1970 | 3 | 13 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1970 | 3 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1970 | 3 | 15 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1970 | 3 | 16 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1970 | 3 | 17 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1970 | 3 | 18 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1970 | 3 | 19 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1970 | 3 | 20 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1970 | 3 | 21 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1970 | 3 | 22 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1970 | 3 | 23 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1970 | 3 | 24 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1970 | 3 | 25 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1970 | 3 | 26 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1970 | 3 | 27 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1970 | 3 | 28 | 378.7755 | 25 | 353.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1970 | 3 | 29 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1970 | 3 | 30 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1970 | 3 | 31 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1970 | 4 | 1 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1970 | 4 | 2 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1970 | 4 | 3 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1970 | 4 | 4 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1970 | 4 | 5 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1970 | 4 | 6 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1970 | 4 | 7 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1970 | 4 | 8 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1970 | 4 | 9 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1970 | 4 | 10 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1970 | 4 | 11 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1970 | 4 | 12 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1970 | 4 | 13 | 655.6735 | 25 | 630.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1970 | 4 | 14 | 834.6122 | 25 | 809.6122 | 28.3308 | 139.3858 | 0.77441 | 27.5564 | 89.27% | 290.382 | 272.9591 | 6551.0187
1970 | 4 | 15 | 1026.6122 | 25 | 1001.6122 | 27.9468 | 139.3858 | 0.77441 | 27.1724 | 89.27% | 286.3355 | 269.1554 | 6459.7298
1970 | 4 | 16 | 1118.0408 | 25 | 1093.0408 | 27.7639 | 139.3858 | 0.77441 | 26.9895 | 89.27% | 284.4086 | 267.3441 | 6416.2589
1970 | 4 | 17 | 1162.449 | 25 | 1137.449 | 27.6751 | 139.3858 | 0.77441 | 26.9007 | 89.27% | 283.4727 | 266.4644 | 6395.1444
1970 | 4 | 18 | 1142.8571 | 25 | 1117.8571 | 27.7143 | 139.3858 | 0.77441 | 26.9399 | 89.27% | 283.8856 | 266.8525 | 6404.4596
1970 | 4 | 19 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1970 | 4 | 20 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1970 | 4 | 21 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1970 | 4 | 22 | 762.7755 | 25 | 737.7755 | 28.4744 | 139.3858 | 0.77441 | 27.7 | 89.27% | 291.896 | 274.3823 | 6585.1745
1970 | 4 | 23 | 726.2041 | 25 | 701.2041 | 28.5476 | 139.3858 | 0.77441 | 27.7732 | 89.27% | 292.6668 | 275.1068 | 6602.5628
1970 | 4 | 24 | 833.3061 | 25 | 808.3061 | 28.3334 | 139.3858 | 0.77441 | 27.559 | 89.27% | 290.4096 | 272.985 | 6551.6398
1970 | 4 | 25 | 1789.3878 | 25 | 1764.3878 | 26.4212 | 139.3858 | 0.77441 | 25.6468 | 89.27% | 270.2597 | 254.0441 | 6097.0581
1970 | 4 | 26 | 1273.4694 | 25 | 1248.4694 | 27.4531 | 139.3858 | 0.77441 | 26.6787 | 89.27% | 281.1329 | 264.2649 | 6342.3583
1970 | 4 | 27 | 1026.6122 | 25 | 1001.6122 | 27.9468 | 139.3858 | 0.77441 | 27.1724 | 89.27% | 286.3355 | 269.1554 | 6459.7298
1970 | 4 | 28 | 910.3673 | 25 | 885.3673 | 28.1793 | 139.3858 | 0.77441 | 27.4049 | 89.27% | 288.7855 | 271.4583 | 6515
1970 | 4 | 29 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1970 | 4 | 30 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1970 | 5 | 1 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1970 | 5 | 2 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1970 | 5 | 3 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1970 | 5 | 4 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1970 | 5 | 5 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1970 | 5 | 6 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1970 | 5 | 7 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1970 | 5 | 8 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1970 | 5 | 9 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1970 | 5 | 10 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1970 | 5 | 11 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1970 | 5 | 12 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1970 | 5 | 13 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1970 | 5 | 14 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1970 | 5 | 15 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1970 | 5 | 16 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1970 | 5 | 17 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1970 | 5 | 18 | 1086.6939 | 25 | 1061.6939 | 27.8266 | 139.3858 | 0.77441 | 27.0522 | 89.27% | 285.0693 | 267.9651 | 6431.1632
1970 | 5 | 19 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1970 | 5 | 20 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1970 | 5 | 21 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1970 | 5 | 22 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1970 | 5 | 23 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1970 | 5 | 24 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1970 | 5 | 25 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1970 | 5 | 26 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1970 | 5 | 27 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1970 | 5 | 28 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1970 | 5 | 29 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1970 | 5 | 30 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1970 | 5 | 31 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1970 | 6 | 1 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1970 | 6 | 2 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1970 | 6 | 3 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1970 | 6 | 4 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1970 | 6 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1970 | 6 | 6 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1970 | 6 | 7 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1970 | 6 | 8 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1970 | 6 | 9 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1970 | 6 | 10 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1970 | 6 | 11 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1970 | 6 | 12 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1970 | 6 | 13 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1970 | 6 | 14 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1970 | 6 | 15 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1970 | 6 | 16 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1970 | 6 | 17 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1970 | 6 | 18 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1970 | 6 | 19 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1970 | 6 | 20 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1970 | 6 | 21 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1970 | 6 | 22 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1970 | 6 | 23 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1970 | 6 | 24 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1970 | 6 | 25 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1970 | 6 | 26 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1970 | 6 | 27 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1970 | 6 | 28 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1970 | 6 | 29 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1970 | 6 | 30 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1970 | 7 | 1 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1970 | 7 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1970 | 7 | 3 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1970 | 7 | 4 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1970 | 7 | 5 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1970 | 7 | 6 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1970 | 7 | 7 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1970 | 7 | 8 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1970 | 7 | 9 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1970 | 7 | 10 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1970 | 7 | 11 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1970 | 7 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1970 | 7 | 13 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1970 | 7 | 14 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1970 | 7 | 15 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1970 | 7 | 16 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1970 | 7 | 17 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1970 | 7 | 18 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1970 | 7 | 19 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1970 | 7 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1970 | 7 | 21 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1970 | 7 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1970 | 7 | 23 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1970 | 7 | 24 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1970 | 7 | 25 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1970 | 7 | 26 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1970 | 7 | 27 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1970 | 7 | 28 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1970 | 7 | 29 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1970 | 7 | 30 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1970 | 7 | 31 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1970 | 8 | 1 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1970 | 8 | 2 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1970 | 8 | 3 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1970 | 8 | 4 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1970 | 8 | 5 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1970 | 8 | 6 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1970 | 8 | 7 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1970 | 8 | 8 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1970 | 8 | 9 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1970 | 8 | 10 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1970 | 8 | 11 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1970 | 8 | 12 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1970 | 8 | 13 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1970 | 8 | 14 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1970 | 8 | 15 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1970 | 8 | 16 | 3.3959 | 5 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
1970 | 8 | 17 | 3.1347 | 5 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
1970 | 8 | 18 | 2.6122 | 5 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1970 | 8 | 19 | 1.8286 | 5 | 0 | 29.9963 | 0 | 0 | 29.9963 | 0% | 0 | 0 | 0
1970 | 8 | 20 | 1.5673 | 5 | 0 | 29.9969 | 0 | 0 | 29.9969 | 0% | 0 | 0 | 0
1970 | 8 | 21 | 2.0898 | 5 | 0 | 29.9958 | 0 | 0 | 29.9958 | 0% | 0 | 0 | 0
1970 | 8 | 22 | 1.698 | 5 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
1970 | 8 | 23 | 3.0041 | 5 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1970 | 8 | 24 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1970 | 8 | 25 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1970 | 8 | 26 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1970 | 8 | 27 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1970 | 8 | 28 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1970 | 8 | 29 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1970 | 8 | 30 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1970 | 8 | 31 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1970 | 9 | 1 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1970 | 9 | 2 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1970 | 9 | 3 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1970 | 9 | 4 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1970 | 9 | 5 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1970 | 9 | 6 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1970 | 9 | 7 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1970 | 9 | 8 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1970 | 9 | 9 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1970 | 9 | 10 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1970 | 9 | 11 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1970 | 9 | 12 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1970 | 9 | 13 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1970 | 9 | 14 | 4.8327 | 15 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1970 | 9 | 15 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1970 | 9 | 16 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1970 | 9 | 17 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1970 | 9 | 18 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1970 | 9 | 19 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1970 | 9 | 20 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1970 | 9 | 21 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1970 | 9 | 22 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1970 | 9 | 23 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1970 | 9 | 24 | 4.5714 | 15 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1970 | 9 | 25 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1970 | 9 | 26 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1970 | 9 | 27 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1970 | 9 | 28 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1970 | 9 | 29 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1970 | 9 | 30 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1970 | 10 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1970 | 10 | 2 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1970 | 10 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1970 | 10 | 4 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1970 | 10 | 5 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1970 | 10 | 6 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1970 | 10 | 7 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1970 | 10 | 8 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1970 | 10 | 9 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1970 | 10 | 10 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1970 | 10 | 11 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1970 | 10 | 12 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1970 | 10 | 13 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1970 | 10 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1970 | 10 | 15 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1970 | 10 | 16 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1970 | 10 | 17 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1970 | 10 | 18 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1970 | 10 | 19 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1970 | 10 | 20 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1970 | 10 | 21 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1970 | 10 | 22 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1970 | 10 | 23 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1970 | 10 | 24 | 1091.9184 | 15 | 1076.9184 | 27.8162 | 139.3858 | 0.77441 | 27.0418 | 89.27% | 284.9592 | 267.8616 | 6428.6791
1970 | 10 | 25 | 545.9592 | 15 | 530.9592 | 28.9081 | 139.3858 | 0.77441 | 28.1337 | 89.27% | 296.4655 | 278.6776 | 6688.2626
1970 | 10 | 26 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1970 | 10 | 27 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1970 | 10 | 28 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1970 | 10 | 29 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1970 | 10 | 30 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1970 | 10 | 31 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1970 | 11 | 1 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1970 | 11 | 2 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1970 | 11 | 3 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1970 | 11 | 4 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1970 | 11 | 5 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1970 | 11 | 6 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1970 | 11 | 7 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1970 | 11 | 8 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1970 | 11 | 9 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1970 | 11 | 10 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1970 | 11 | 11 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1970 | 11 | 12 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1970 | 11 | 13 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1970 | 11 | 14 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1970 | 11 | 15 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1970 | 11 | 16 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1970 | 11 | 17 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1970 | 11 | 18 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1970 | 11 | 19 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1970 | 11 | 20 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1970 | 11 | 21 | 394.449 | 15 | 379.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1970 | 11 | 22 | 323.9184 | 15 | 308.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1970 | 11 | 23 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1970 | 11 | 24 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1970 | 11 | 25 | 160.6531 | 15 | 145.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1970 | 11 | 26 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1970 | 11 | 27 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1970 | 11 | 28 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1970 | 11 | 29 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1970 | 11 | 30 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1970 | 12 | 1 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1970 | 12 | 2 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1970 | 12 | 3 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1970 | 12 | 4 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1970 | 12 | 5 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1970 | 12 | 6 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1970 | 12 | 7 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1970 | 12 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1970 | 12 | 9 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1970 | 12 | 10 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1970 | 12 | 11 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1970 | 12 | 12 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1970 | 12 | 13 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1970 | 12 | 14 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1970 | 12 | 15 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1970 | 12 | 16 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1970 | 12 | 17 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1970 | 12 | 18 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1970 | 12 | 19 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1970 | 12 | 20 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1970 | 12 | 21 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1970 | 12 | 22 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1970 | 12 | 23 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1970 | 12 | 24 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1970 | 12 | 25 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1970 | 12 | 26 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1970 | 12 | 27 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1970 | 12 | 28 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1970 | 12 | 29 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1970 | 12 | 30 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1970 | 12 | 31 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1971 | 1 | 1 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1971 | 1 | 2 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1971 | 1 | 3 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1971 | 1 | 4 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1971 | 1 | 5 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1971 | 1 | 6 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1971 | 1 | 7 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1971 | 1 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1971 | 1 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1971 | 1 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1971 | 1 | 11 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1971 | 1 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1971 | 1 | 13 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1971 | 1 | 14 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1971 | 1 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1971 | 1 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1971 | 1 | 17 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1971 | 1 | 18 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1971 | 1 | 19 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1971 | 1 | 20 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 1 | 21 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 1 | 22 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 1 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 1 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 1 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1971 | 1 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1971 | 1 | 27 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1971 | 1 | 28 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1971 | 1 | 29 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1971 | 1 | 30 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1971 | 1 | 31 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1971 | 2 | 1 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1971 | 2 | 2 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1971 | 2 | 3 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1971 | 2 | 4 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1971 | 2 | 5 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1971 | 2 | 6 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1971 | 2 | 7 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1971 | 2 | 8 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1971 | 2 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1971 | 2 | 10 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1971 | 2 | 11 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1971 | 2 | 12 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1971 | 2 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1971 | 2 | 14 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1971 | 2 | 15 | 323.9184 | 5 | 318.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1971 | 2 | 16 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1971 | 2 | 17 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1971 | 2 | 18 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1971 | 2 | 19 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1971 | 2 | 20 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1971 | 2 | 21 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1971 | 2 | 22 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1971 | 2 | 23 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1971 | 2 | 24 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1971 | 2 | 25 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1971 | 2 | 26 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1971 | 2 | 27 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1971 | 2 | 28 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1971 | 3 | 1 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1971 | 3 | 2 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1971 | 3 | 3 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1971 | 3 | 4 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1971 | 3 | 5 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1971 | 3 | 6 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1971 | 3 | 7 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1971 | 3 | 8 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1971 | 3 | 9 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1971 | 3 | 10 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1971 | 3 | 11 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1971 | 3 | 12 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1971 | 3 | 13 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1971 | 3 | 14 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1971 | 3 | 15 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1971 | 3 | 16 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1971 | 3 | 17 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1971 | 3 | 18 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1971 | 3 | 19 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1971 | 3 | 20 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1971 | 3 | 21 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1971 | 3 | 22 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1971 | 3 | 23 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1971 | 3 | 24 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1971 | 3 | 25 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1971 | 3 | 26 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1971 | 3 | 27 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1971 | 3 | 28 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1971 | 3 | 29 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1971 | 3 | 30 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1971 | 3 | 31 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1971 | 4 | 1 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1971 | 4 | 2 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1971 | 4 | 3 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1971 | 4 | 4 | 576 | 25 | 551 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1971 | 4 | 5 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1971 | 4 | 6 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1971 | 4 | 7 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1971 | 4 | 8 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1971 | 4 | 9 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1971 | 4 | 10 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1971 | 4 | 11 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1971 | 4 | 12 | 839.8367 | 25 | 814.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
1971 | 4 | 13 | 1031.8367 | 25 | 1006.8367 | 27.9363 | 139.3858 | 0.77441 | 27.1619 | 89.27% | 286.2254 | 269.0519 | 6457.2458
1971 | 4 | 14 | 1098.449 | 25 | 1073.449 | 27.8031 | 139.3858 | 0.77441 | 27.0287 | 89.27% | 284.8215 | 267.7323 | 6425.5741
1971 | 4 | 15 | 860.7347 | 25 | 835.7347 | 28.2785 | 139.3858 | 0.77441 | 27.5041 | 89.27% | 289.8315 | 272.4416 | 6538.5985
1971 | 4 | 16 | 650.449 | 25 | 625.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
1971 | 4 | 17 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1971 | 4 | 18 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1971 | 4 | 19 | 973.0612 | 25 | 948.0612 | 28.0539 | 139.3858 | 0.77441 | 27.2795 | 89.27% | 287.4642 | 270.2163 | 6485.1913
1971 | 4 | 20 | 1410.6122 | 25 | 1385.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1971 | 4 | 21 | 1502.0408 | 25 | 1477.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1971 | 4 | 22 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
1971 | 4 | 23 | 1061.8776 | 25 | 1036.8776 | 27.8762 | 139.3858 | 0.77441 | 27.1018 | 89.27% | 285.5923 | 268.4568 | 6442.9624
1971 | 4 | 24 | 850.2857 | 25 | 825.2857 | 28.2994 | 139.3858 | 0.77441 | 27.525 | 89.27% | 290.0517 | 272.6486 | 6543.5666
1971 | 4 | 25 | 850.2857 | 25 | 825.2857 | 28.2994 | 139.3858 | 0.77441 | 27.525 | 89.27% | 290.0517 | 272.6486 | 6543.5666
1971 | 4 | 26 | 850.2857 | 25 | 825.2857 | 28.2994 | 139.3858 | 0.77441 | 27.525 | 89.27% | 290.0517 | 272.6486 | 6543.5666
1971 | 4 | 27 | 777.1429 | 25 | 752.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1971 | 4 | 28 | 701.3878 | 25 | 676.3878 | 28.5972 | 139.3858 | 0.77441 | 27.8228 | 89.27% | 293.1898 | 275.5984 | 6614.3621
1971 | 4 | 29 | 701.3878 | 25 | 676.3878 | 28.5972 | 139.3858 | 0.77441 | 27.8228 | 89.27% | 293.1898 | 275.5984 | 6614.3621
1971 | 4 | 30 | 625.6327 | 25 | 600.6327 | 28.7487 | 139.3858 | 0.77441 | 27.9743 | 89.27% | 294.7864 | 277.0992 | 6650.3808
1971 | 5 | 1 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1971 | 5 | 2 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1971 | 5 | 3 | 811.102 | 25 | 786.102 | 28.3778 | 139.3858 | 0.77441 | 27.6034 | 89.27% | 290.8775 | 273.4249 | 6562.197
1971 | 5 | 4 | 2416.3265 | 25 | 2391.3265 | 25.1673 | 139.3858 | 0.77441 | 24.3929 | 89.27% | 257.0466 | 241.6238 | 5798.9718
1971 | 5 | 5 | 1397.551 | 25 | 1372.551 | 27.2049 | 139.3858 | 0.77441 | 26.4305 | 89.27% | 278.5178 | 261.8068 | 6283.3621
1971 | 5 | 6 | 839.8367 | 25 | 814.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
1971 | 5 | 7 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1971 | 5 | 8 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1971 | 5 | 9 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1971 | 5 | 10 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1971 | 5 | 11 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1971 | 5 | 12 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1971 | 5 | 13 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1971 | 5 | 14 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1971 | 5 | 15 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1971 | 5 | 16 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1971 | 5 | 17 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1971 | 5 | 18 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1971 | 5 | 19 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1971 | 5 | 20 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1971 | 5 | 21 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1971 | 5 | 22 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1971 | 5 | 23 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1971 | 5 | 24 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1971 | 5 | 25 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1971 | 5 | 26 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1971 | 5 | 27 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1971 | 5 | 28 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1971 | 5 | 29 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1971 | 5 | 30 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1971 | 5 | 31 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1971 | 6 | 1 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1971 | 6 | 2 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1971 | 6 | 3 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1971 | 6 | 4 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1971 | 6 | 5 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1971 | 6 | 6 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1971 | 6 | 7 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1971 | 6 | 8 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1971 | 6 | 9 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1971 | 6 | 10 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1971 | 6 | 11 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1971 | 6 | 12 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1971 | 6 | 13 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1971 | 6 | 14 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1971 | 6 | 15 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1971 | 6 | 16 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1971 | 6 | 17 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1971 | 6 | 18 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1971 | 6 | 19 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1971 | 6 | 20 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1971 | 6 | 21 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1971 | 6 | 22 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1971 | 6 | 23 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1971 | 6 | 24 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1971 | 6 | 25 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1971 | 6 | 26 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1971 | 6 | 27 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1971 | 6 | 28 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1971 | 6 | 29 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1971 | 6 | 30 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1971 | 7 | 1 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1971 | 7 | 2 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1971 | 7 | 3 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1971 | 7 | 4 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1971 | 7 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1971 | 7 | 6 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1971 | 7 | 7 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1971 | 7 | 8 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1971 | 7 | 9 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1971 | 7 | 10 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1971 | 7 | 11 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1971 | 7 | 12 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1971 | 7 | 13 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1971 | 7 | 14 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1971 | 7 | 15 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1971 | 7 | 16 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1971 | 7 | 17 | 4.8327 | 5 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1971 | 7 | 18 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1971 | 7 | 19 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1971 | 7 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1971 | 7 | 21 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1971 | 7 | 22 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1971 | 7 | 23 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1971 | 7 | 24 | 407.5102 | 5 | 402.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1971 | 7 | 25 | 355.2653 | 5 | 350.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1971 | 7 | 26 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1971 | 7 | 27 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1971 | 7 | 28 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1971 | 7 | 29 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 7 | 30 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1971 | 7 | 31 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1971 | 8 | 1 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1971 | 8 | 2 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1971 | 8 | 3 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1971 | 8 | 4 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1971 | 8 | 5 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1971 | 8 | 6 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1971 | 8 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1971 | 8 | 8 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1971 | 8 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1971 | 8 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1971 | 8 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1971 | 8 | 12 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1971 | 8 | 13 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1971 | 8 | 14 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1971 | 8 | 15 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1971 | 8 | 16 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1971 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1971 | 8 | 18 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1971 | 8 | 19 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1971 | 8 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1971 | 8 | 21 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1971 | 8 | 22 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1971 | 8 | 23 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1971 | 8 | 24 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1971 | 8 | 25 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1971 | 8 | 26 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1971 | 8 | 27 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1971 | 8 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1971 | 8 | 29 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1971 | 8 | 30 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1971 | 8 | 31 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1971 | 9 | 1 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 9 | 2 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1971 | 9 | 3 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1971 | 9 | 4 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1971 | 9 | 5 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1971 | 9 | 6 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1971 | 9 | 7 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1971 | 9 | 8 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1971 | 9 | 9 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1971 | 9 | 10 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1971 | 9 | 11 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1971 | 9 | 12 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1971 | 9 | 13 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1971 | 9 | 14 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1971 | 9 | 15 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1971 | 9 | 16 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1971 | 9 | 17 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1971 | 9 | 18 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1971 | 9 | 19 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 9 | 20 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 9 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 9 | 22 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1971 | 9 | 23 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 9 | 24 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1971 | 9 | 25 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1971 | 9 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1971 | 9 | 27 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1971 | 9 | 28 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1971 | 9 | 29 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1971 | 9 | 30 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1971 | 10 | 1 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1971 | 10 | 2 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1971 | 10 | 3 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1971 | 10 | 4 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1971 | 10 | 5 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1971 | 10 | 6 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1971 | 10 | 7 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1971 | 10 | 8 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1971 | 10 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1971 | 10 | 10 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 10 | 11 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1971 | 10 | 12 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1971 | 10 | 13 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1971 | 10 | 14 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1971 | 10 | 15 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1971 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1971 | 10 | 17 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1971 | 10 | 18 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1971 | 10 | 19 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1971 | 10 | 20 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 10 | 21 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1971 | 10 | 22 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1971 | 10 | 23 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 10 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1971 | 10 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 10 | 26 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1971 | 10 | 27 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1971 | 10 | 28 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1971 | 10 | 29 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1971 | 10 | 30 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1971 | 10 | 31 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1971 | 11 | 1 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1971 | 11 | 2 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1971 | 11 | 3 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1971 | 11 | 4 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1971 | 11 | 5 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1971 | 11 | 6 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1971 | 11 | 7 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1971 | 11 | 8 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1971 | 11 | 9 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1971 | 11 | 10 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1971 | 11 | 11 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1971 | 11 | 12 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1971 | 11 | 13 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1971 | 11 | 14 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1971 | 11 | 15 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1971 | 11 | 16 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 11 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 11 | 18 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 11 | 19 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 11 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1971 | 11 | 21 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1971 | 11 | 22 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1971 | 11 | 23 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1971 | 11 | 24 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 11 | 25 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1971 | 11 | 26 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1971 | 11 | 27 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1971 | 11 | 28 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1971 | 11 | 29 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1971 | 11 | 30 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1971 | 12 | 1 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1971 | 12 | 2 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1971 | 12 | 3 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1971 | 12 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1971 | 12 | 5 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1971 | 12 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1971 | 12 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1971 | 12 | 8 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1971 | 12 | 9 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1971 | 12 | 10 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1971 | 12 | 11 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1971 | 12 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1971 | 12 | 13 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1971 | 12 | 14 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1971 | 12 | 15 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1971 | 12 | 16 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1971 | 12 | 17 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1971 | 12 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1971 | 12 | 19 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1971 | 12 | 20 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1971 | 12 | 21 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1971 | 12 | 22 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1971 | 12 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1971 | 12 | 24 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1971 | 12 | 25 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1971 | 12 | 26 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1971 | 12 | 27 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1971 | 12 | 28 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1971 | 12 | 29 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1971 | 12 | 30 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1971 | 12 | 31 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1972 | 1 | 1 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 1 | 2 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 1 | 3 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 1 | 4 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 1 | 5 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 1 | 6 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1972 | 1 | 7 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 1 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 1 | 9 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1972 | 1 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1972 | 1 | 11 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1972 | 1 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1972 | 1 | 13 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1972 | 1 | 14 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1972 | 1 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1972 | 1 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1972 | 1 | 17 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1972 | 1 | 18 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1972 | 1 | 19 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1972 | 1 | 20 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1972 | 1 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1972 | 1 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1972 | 1 | 23 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 1 | 24 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1972 | 1 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1972 | 1 | 26 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1972 | 1 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1972 | 1 | 28 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1972 | 1 | 29 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1972 | 1 | 30 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1972 | 1 | 31 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1972 | 2 | 1 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 2 | 2 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1972 | 2 | 3 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 2 | 4 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1972 | 2 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1972 | 2 | 6 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1972 | 2 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1972 | 2 | 8 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1972 | 2 | 9 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 2 | 10 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1972 | 2 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 2 | 12 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1972 | 2 | 13 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1972 | 2 | 14 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1972 | 2 | 15 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1972 | 2 | 16 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1972 | 2 | 17 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1972 | 2 | 18 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1972 | 2 | 19 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1972 | 2 | 20 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1972 | 2 | 21 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1972 | 2 | 22 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1972 | 2 | 23 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1972 | 2 | 24 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1972 | 2 | 25 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1972 | 2 | 26 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1972 | 2 | 27 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1972 | 2 | 28 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1972 | 2 | 29 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1972 | 3 | 1 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1972 | 3 | 2 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1972 | 3 | 3 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1972 | 3 | 4 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1972 | 3 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1972 | 3 | 6 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1972 | 3 | 7 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1972 | 3 | 8 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1972 | 3 | 9 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1972 | 3 | 10 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1972 | 3 | 11 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1972 | 3 | 12 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1972 | 3 | 13 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1972 | 3 | 14 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1972 | 3 | 15 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1972 | 3 | 16 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1972 | 3 | 17 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1972 | 3 | 18 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1972 | 3 | 19 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1972 | 3 | 20 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1972 | 3 | 21 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1972 | 3 | 22 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1972 | 3 | 23 | 693.551 | 25 | 668.551 | 28.6129 | 139.3858 | 0.77441 | 27.8385 | 89.27% | 293.355 | 275.7537 | 6618.0882
1972 | 3 | 24 | 839.8367 | 25 | 814.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
1972 | 3 | 25 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1972 | 3 | 26 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1972 | 3 | 27 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1972 | 3 | 28 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1972 | 3 | 29 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1972 | 3 | 30 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1972 | 3 | 31 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1972 | 4 | 1 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1972 | 4 | 2 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1972 | 4 | 3 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1972 | 4 | 4 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1972 | 4 | 5 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1972 | 4 | 6 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1972 | 4 | 7 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1972 | 4 | 8 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1972 | 4 | 9 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1972 | 4 | 10 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1972 | 4 | 11 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1972 | 4 | 12 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1972 | 4 | 13 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1972 | 4 | 14 | 410.1224 | 25 | 385.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1972 | 4 | 15 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1972 | 4 | 16 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1972 | 4 | 17 | 664.8163 | 25 | 639.8163 | 28.6704 | 139.3858 | 0.77441 | 27.896 | 89.27% | 293.9606 | 276.3229 | 6631.7504
1972 | 4 | 18 | 1013.551 | 25 | 988.551 | 27.9729 | 139.3858 | 0.77441 | 27.1985 | 89.27% | 286.6108 | 269.4142 | 6465.9399
1972 | 4 | 19 | 1162.449 | 25 | 1137.449 | 27.6751 | 139.3858 | 0.77441 | 26.9007 | 89.27% | 283.4727 | 266.4644 | 6395.1444
1972 | 4 | 20 | 1182.0408 | 25 | 1157.0408 | 27.6359 | 139.3858 | 0.77441 | 26.8615 | 89.27% | 283.0598 | 266.0762 | 6385.8292
1972 | 4 | 21 | 939.102 | 25 | 914.102 | 28.1218 | 139.3858 | 0.77441 | 27.3474 | 89.27% | 288.1799 | 270.8891 | 6501.3377
1972 | 4 | 22 | 855.5102 | 25 | 830.5102 | 28.289 | 139.3858 | 0.77441 | 27.5146 | 89.27% | 289.9416 | 272.5451 | 6541.0825
1972 | 4 | 23 | 910.3673 | 25 | 885.3673 | 28.1793 | 139.3858 | 0.77441 | 27.4049 | 89.27% | 288.7855 | 271.4583 | 6515
1972 | 4 | 24 | 922.1224 | 25 | 897.1224 | 28.1558 | 139.3858 | 0.77441 | 27.3813 | 89.27% | 288.5377 | 271.2255 | 6509.4109
1972 | 4 | 25 | 1098.449 | 25 | 1073.449 | 27.8031 | 139.3858 | 0.77441 | 27.0287 | 89.27% | 284.8215 | 267.7323 | 6425.5741
1972 | 4 | 26 | 1008.3265 | 25 | 983.3265 | 27.9833 | 139.3858 | 0.77441 | 27.2089 | 89.27% | 286.7209 | 269.5177 | 6468.424
1972 | 4 | 27 | 834.6122 | 25 | 809.6122 | 28.3308 | 139.3858 | 0.77441 | 27.5564 | 89.27% | 290.382 | 272.9591 | 6551.0187
1972 | 4 | 28 | 706.6122 | 25 | 681.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
1972 | 4 | 29 | 798.0408 | 25 | 773.0408 | 28.4039 | 139.3858 | 0.77441 | 27.6295 | 89.27% | 291.1528 | 273.6836 | 6568.4071
1972 | 4 | 30 | 966.5306 | 25 | 941.5306 | 28.0669 | 139.3858 | 0.77441 | 27.2925 | 89.27% | 287.6018 | 270.3457 | 6488.2964
1972 | 5 | 1 | 1124.5714 | 25 | 1099.5714 | 27.7509 | 139.3858 | 0.77441 | 26.9764 | 89.27% | 284.271 | 267.2147 | 6413.1538
1972 | 5 | 2 | 1195.102 | 25 | 1170.102 | 27.6098 | 139.3858 | 0.77441 | 26.8354 | 89.27% | 282.7845 | 265.8175 | 6379.6191
1972 | 5 | 3 | 1227.7551 | 25 | 1202.7551 | 27.5445 | 139.3858 | 0.77441 | 26.7701 | 89.27% | 282.0964 | 265.1706 | 6364.0938
1972 | 5 | 4 | 1502.0408 | 25 | 1477.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1972 | 5 | 5 | 1227.7551 | 25 | 1202.7551 | 27.5445 | 139.3858 | 0.77441 | 26.7701 | 89.27% | 282.0964 | 265.1706 | 6364.0938
1972 | 5 | 6 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1972 | 5 | 7 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1972 | 5 | 8 | 706.6122 | 25 | 681.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
1972 | 5 | 9 | 547.2653 | 25 | 522.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1972 | 5 | 10 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1972 | 5 | 11 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1972 | 5 | 12 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1972 | 5 | 13 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1972 | 5 | 14 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1972 | 5 | 15 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1972 | 5 | 16 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1972 | 5 | 17 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1972 | 5 | 18 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1972 | 5 | 19 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1972 | 5 | 20 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1972 | 5 | 21 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1972 | 5 | 22 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1972 | 5 | 23 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1972 | 5 | 24 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1972 | 5 | 25 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1972 | 5 | 26 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1972 | 5 | 27 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1972 | 5 | 28 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1972 | 5 | 29 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1972 | 5 | 30 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1972 | 5 | 31 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1972 | 6 | 1 | 736.6531 | 25 | 711.6531 | 28.5267 | 139.3858 | 0.77441 | 27.7523 | 89.27% | 292.4466 | 274.8998 | 6597.5947
1972 | 6 | 2 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1972 | 6 | 3 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1972 | 6 | 4 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1972 | 6 | 5 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1972 | 6 | 6 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1972 | 6 | 7 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1972 | 6 | 8 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1972 | 6 | 9 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1972 | 6 | 10 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1972 | 6 | 11 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1972 | 6 | 12 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1972 | 6 | 13 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1972 | 6 | 14 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1972 | 6 | 15 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1972 | 6 | 16 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1972 | 6 | 17 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1972 | 6 | 18 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1972 | 6 | 19 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1972 | 6 | 20 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1972 | 6 | 21 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1972 | 6 | 22 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1972 | 6 | 23 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1972 | 6 | 24 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1972 | 6 | 25 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1972 | 6 | 26 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1972 | 6 | 27 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1972 | 6 | 28 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1972 | 6 | 29 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1972 | 6 | 30 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1972 | 7 | 1 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1972 | 7 | 2 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1972 | 7 | 3 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1972 | 7 | 4 | 664.8163 | 5 | 659.8163 | 28.6704 | 139.3858 | 0.77441 | 27.896 | 89.27% | 293.9606 | 276.3229 | 6631.7504
1972 | 7 | 5 | 357.8776 | 5 | 352.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1972 | 7 | 6 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1972 | 7 | 7 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1972 | 7 | 8 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1972 | 7 | 9 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1972 | 7 | 10 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1972 | 7 | 11 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1972 | 7 | 12 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1972 | 7 | 13 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1972 | 7 | 14 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1972 | 7 | 15 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1972 | 7 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1972 | 7 | 17 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1972 | 7 | 18 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1972 | 7 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1972 | 7 | 20 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1972 | 7 | 21 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1972 | 7 | 22 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1972 | 7 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1972 | 7 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1972 | 7 | 25 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1972 | 7 | 26 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1972 | 7 | 27 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1972 | 7 | 28 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1972 | 7 | 29 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1972 | 7 | 30 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1972 | 7 | 31 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1972 | 8 | 1 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1972 | 8 | 2 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1972 | 8 | 3 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1972 | 8 | 4 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1972 | 8 | 5 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1972 | 8 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1972 | 8 | 7 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1972 | 8 | 8 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1972 | 8 | 9 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1972 | 8 | 10 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1972 | 8 | 11 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1972 | 8 | 12 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1972 | 8 | 13 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1972 | 8 | 14 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1972 | 8 | 15 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1972 | 8 | 16 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 8 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1972 | 8 | 18 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1972 | 8 | 19 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1972 | 8 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1972 | 8 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1972 | 8 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1972 | 8 | 23 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1972 | 8 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1972 | 8 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1972 | 8 | 26 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1972 | 8 | 27 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1972 | 8 | 28 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1972 | 8 | 29 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1972 | 8 | 30 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1972 | 8 | 31 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1972 | 9 | 1 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1972 | 9 | 2 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1972 | 9 | 3 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1972 | 9 | 4 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1972 | 9 | 5 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1972 | 9 | 6 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1972 | 9 | 7 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1972 | 9 | 8 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1972 | 9 | 9 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1972 | 9 | 10 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1972 | 9 | 11 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1972 | 9 | 12 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1972 | 9 | 13 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1972 | 9 | 14 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1972 | 9 | 15 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1972 | 9 | 16 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1972 | 9 | 17 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1972 | 9 | 18 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1972 | 9 | 19 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1972 | 9 | 20 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1972 | 9 | 21 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1972 | 9 | 22 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1972 | 9 | 23 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1972 | 9 | 24 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1972 | 9 | 25 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1972 | 9 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1972 | 9 | 27 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1972 | 9 | 28 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1972 | 9 | 29 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1972 | 9 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1972 | 10 | 1 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1972 | 10 | 2 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1972 | 10 | 3 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1972 | 10 | 4 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1972 | 10 | 5 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1972 | 10 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1972 | 10 | 7 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1972 | 10 | 8 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1972 | 10 | 9 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1972 | 10 | 10 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1972 | 10 | 11 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1972 | 10 | 12 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1972 | 10 | 13 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1972 | 10 | 14 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1972 | 10 | 15 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1972 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1972 | 10 | 17 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1972 | 10 | 18 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1972 | 10 | 19 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1972 | 10 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1972 | 10 | 21 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1972 | 10 | 22 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1972 | 10 | 23 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1972 | 10 | 24 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1972 | 10 | 25 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1972 | 10 | 26 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1972 | 10 | 27 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1972 | 10 | 28 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1972 | 10 | 29 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1972 | 10 | 30 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1972 | 10 | 31 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1972 | 11 | 1 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1972 | 11 | 2 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1972 | 11 | 3 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1972 | 11 | 4 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1972 | 11 | 5 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1972 | 11 | 6 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1972 | 11 | 7 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1972 | 11 | 8 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1972 | 11 | 9 | 347.4286 | 15 | 332.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1972 | 11 | 10 | 431.0204 | 15 | 416.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1972 | 11 | 11 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1972 | 11 | 12 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1972 | 11 | 13 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1972 | 11 | 14 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1972 | 11 | 15 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1972 | 11 | 16 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1972 | 11 | 17 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1972 | 11 | 18 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1972 | 11 | 19 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1972 | 11 | 20 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1972 | 11 | 21 | 314.7755 | 15 | 299.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1972 | 11 | 22 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1972 | 11 | 23 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1972 | 11 | 24 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1972 | 11 | 25 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1972 | 11 | 26 | 470.2041 | 15 | 455.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1972 | 11 | 27 | 1238.2041 | 15 | 1223.2041 | 27.5236 | 139.3858 | 0.77441 | 26.7492 | 89.27% | 281.8761 | 264.9636 | 6359.1257
1972 | 11 | 28 | 655.6735 | 15 | 640.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1972 | 11 | 29 | 538.1224 | 15 | 523.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1972 | 11 | 30 | 381.3878 | 15 | 366.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1972 | 12 | 1 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1972 | 12 | 2 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1972 | 12 | 3 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1972 | 12 | 4 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1972 | 12 | 5 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1972 | 12 | 6 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1972 | 12 | 7 | 587.7551 | 5 | 582.7551 | 28.8245 | 139.3858 | 0.77441 | 28.0501 | 89.27% | 295.5847 | 277.8496 | 6668.3902
1972 | 12 | 8 | 463.6735 | 5 | 458.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1972 | 12 | 9 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1972 | 12 | 10 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1972 | 12 | 11 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1972 | 12 | 12 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1972 | 12 | 13 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1972 | 12 | 14 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1972 | 12 | 15 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1972 | 12 | 16 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1972 | 12 | 17 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1972 | 12 | 18 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1972 | 12 | 19 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1972 | 12 | 20 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1972 | 12 | 21 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1972 | 12 | 22 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1972 | 12 | 23 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1972 | 12 | 24 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1972 | 12 | 25 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1972 | 12 | 26 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1972 | 12 | 27 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1972 | 12 | 28 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1972 | 12 | 29 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1972 | 12 | 30 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1972 | 12 | 31 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1973 | 1 | 1 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1973 | 1 | 2 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1973 | 1 | 3 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1973 | 1 | 4 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1973 | 1 | 5 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1973 | 1 | 6 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1973 | 1 | 7 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1973 | 1 | 8 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1973 | 1 | 9 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1973 | 1 | 10 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1973 | 1 | 11 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1973 | 1 | 12 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1973 | 1 | 13 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1973 | 1 | 14 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1973 | 1 | 15 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1973 | 1 | 16 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1973 | 1 | 17 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1973 | 1 | 18 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1973 | 1 | 19 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1973 | 1 | 20 | 246.8571 | 5 | 241.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
1973 | 1 | 21 | 500.2449 | 5 | 495.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1973 | 1 | 22 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1973 | 1 | 23 | 634.7755 | 5 | 629.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1973 | 1 | 24 | 839.8367 | 5 | 834.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
1973 | 1 | 25 | 552.4898 | 5 | 547.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1973 | 1 | 26 | 406.2041 | 5 | 401.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1973 | 1 | 27 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1973 | 1 | 28 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1973 | 1 | 29 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1973 | 1 | 30 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1973 | 1 | 31 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1973 | 2 | 1 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1973 | 2 | 2 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1973 | 2 | 3 | 710.5306 | 5 | 705.5306 | 28.5789 | 139.3858 | 0.77441 | 27.8045 | 89.27% | 292.9971 | 275.4173 | 6610.015
1973 | 2 | 4 | 879.0204 | 5 | 874.0204 | 28.242 | 139.3858 | 0.77441 | 27.4675 | 89.27% | 289.4461 | 272.0793 | 6529.9043
1973 | 2 | 5 | 600.8163 | 5 | 595.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1973 | 2 | 6 | 414.0408 | 5 | 409.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1973 | 2 | 7 | 338.2857 | 5 | 333.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1973 | 2 | 8 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1973 | 2 | 9 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1973 | 2 | 10 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1973 | 2 | 11 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1973 | 2 | 12 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1973 | 2 | 13 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1973 | 2 | 14 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1973 | 2 | 15 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1973 | 2 | 16 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1973 | 2 | 17 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1973 | 2 | 18 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1973 | 2 | 19 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1973 | 2 | 20 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1973 | 2 | 21 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1973 | 2 | 22 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1973 | 2 | 23 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1973 | 2 | 24 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1973 | 2 | 25 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1973 | 2 | 26 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1973 | 2 | 27 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1973 | 2 | 28 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1973 | 3 | 1 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1973 | 3 | 2 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1973 | 3 | 3 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1973 | 3 | 4 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1973 | 3 | 5 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1973 | 3 | 6 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1973 | 3 | 7 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1973 | 3 | 8 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1973 | 3 | 9 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1973 | 3 | 10 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1973 | 3 | 11 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1973 | 3 | 12 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1973 | 3 | 13 | 835.9184 | 25 | 810.9184 | 28.3282 | 139.3858 | 0.77441 | 27.5538 | 89.27% | 290.3545 | 272.9332 | 6550.3977
1973 | 3 | 14 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1973 | 3 | 15 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1973 | 3 | 16 | 474.1224 | 25 | 449.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
1973 | 3 | 17 | 916.898 | 25 | 891.898 | 28.1662 | 139.3858 | 0.77441 | 27.3918 | 89.27% | 288.6478 | 271.329 | 6511.8949
1973 | 3 | 18 | 2285.7143 | 25 | 2260.7143 | 25.4286 | 139.3858 | 0.77441 | 24.6542 | 89.27% | 259.7993 | 244.2114 | 5861.0731
1973 | 3 | 19 | 1124.5714 | 25 | 1099.5714 | 27.7509 | 139.3858 | 0.77441 | 26.9764 | 89.27% | 284.271 | 267.2147 | 6413.1538
1973 | 3 | 20 | 747.102 | 25 | 722.102 | 28.5058 | 139.3858 | 0.77441 | 27.7314 | 89.27% | 292.2264 | 274.6928 | 6592.6266
1973 | 3 | 21 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1973 | 3 | 22 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1973 | 3 | 23 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1973 | 3 | 24 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1973 | 3 | 25 | 481.9592 | 25 | 456.9592 | 29.0361 | 139.3858 | 0.77441 | 28.2617 | 89.27% | 297.8144 | 279.9455 | 6718.6923
1973 | 3 | 26 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1973 | 3 | 27 | 655.6735 | 25 | 630.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1973 | 3 | 28 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1973 | 3 | 29 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1973 | 3 | 30 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1973 | 3 | 31 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1973 | 4 | 1 | 496.3265 | 25 | 471.3265 | 29.0073 | 139.3858 | 0.77441 | 28.2329 | 89.27% | 297.5116 | 279.6609 | 6711.8611
1973 | 4 | 2 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1973 | 4 | 3 | 829.3878 | 25 | 804.3878 | 28.3412 | 139.3858 | 0.77441 | 27.5668 | 89.27% | 290.4921 | 273.0626 | 6553.5028
1973 | 4 | 4 | 685.7143 | 25 | 660.7143 | 28.6286 | 139.3858 | 0.77441 | 27.8542 | 89.27% | 293.5201 | 275.9089 | 6621.8142
1973 | 4 | 5 | 650.449 | 25 | 625.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
1973 | 4 | 6 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1973 | 4 | 7 | 586.449 | 25 | 561.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1973 | 4 | 8 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1973 | 4 | 9 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1973 | 4 | 10 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1973 | 4 | 11 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1973 | 4 | 12 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1973 | 4 | 13 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1973 | 4 | 14 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1973 | 4 | 15 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1973 | 4 | 16 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1973 | 4 | 17 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1973 | 4 | 18 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1973 | 4 | 19 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1973 | 4 | 20 | 576 | 25 | 551 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1973 | 4 | 21 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1973 | 4 | 22 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1973 | 4 | 23 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1973 | 4 | 24 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1973 | 4 | 25 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1973 | 4 | 26 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1973 | 4 | 27 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1973 | 4 | 28 | 963.9184 | 25 | 938.9184 | 28.0722 | 139.3858 | 0.77441 | 27.2978 | 89.27% | 287.6568 | 270.3974 | 6489.5384
1973 | 4 | 29 | 1124.5714 | 25 | 1099.5714 | 27.7509 | 139.3858 | 0.77441 | 26.9764 | 89.27% | 284.271 | 267.2147 | 6413.1538
1973 | 4 | 30 | 808.4898 | 25 | 783.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
1973 | 5 | 1 | 547.2653 | 25 | 522.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1973 | 5 | 2 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1973 | 5 | 3 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1973 | 5 | 4 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1973 | 5 | 5 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1973 | 5 | 6 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1973 | 5 | 7 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1973 | 5 | 8 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1973 | 5 | 9 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1973 | 5 | 10 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1973 | 5 | 11 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1973 | 5 | 12 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1973 | 5 | 13 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1973 | 5 | 14 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1973 | 5 | 15 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1973 | 5 | 16 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1973 | 5 | 17 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1973 | 5 | 18 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1973 | 5 | 19 | 609.9592 | 25 | 584.9592 | 28.7801 | 139.3858 | 0.77441 | 28.0057 | 89.27% | 295.1167 | 277.4097 | 6657.833
1973 | 5 | 20 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1973 | 5 | 21 | 845.0612 | 25 | 820.0612 | 28.3099 | 139.3858 | 0.77441 | 27.5355 | 89.27% | 290.1618 | 272.7521 | 6546.0506
1973 | 5 | 22 | 1266.9388 | 25 | 1241.9388 | 27.4661 | 139.3858 | 0.77441 | 26.6917 | 89.27% | 281.2705 | 264.3943 | 6345.4634
1973 | 5 | 23 | 834.6122 | 25 | 809.6122 | 28.3308 | 139.3858 | 0.77441 | 27.5564 | 89.27% | 290.382 | 272.9591 | 6551.0187
1973 | 5 | 24 | 532.898 | 25 | 507.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
1973 | 5 | 25 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1973 | 5 | 26 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1973 | 5 | 27 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1973 | 5 | 28 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1973 | 5 | 29 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1973 | 5 | 30 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1973 | 5 | 31 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1973 | 6 | 1 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1973 | 6 | 2 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1973 | 6 | 3 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1973 | 6 | 4 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1973 | 6 | 5 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1973 | 6 | 6 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1973 | 6 | 7 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1973 | 6 | 8 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1973 | 6 | 9 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1973 | 6 | 10 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1973 | 6 | 11 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1973 | 6 | 12 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1973 | 6 | 13 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1973 | 6 | 14 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1973 | 6 | 15 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1973 | 6 | 16 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1973 | 6 | 17 | 846.3673 | 25 | 821.3673 | 28.3073 | 139.3858 | 0.77441 | 27.5329 | 89.27% | 290.1343 | 272.7262 | 6545.4296
1973 | 6 | 18 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1973 | 6 | 19 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1973 | 6 | 20 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1973 | 6 | 21 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1973 | 6 | 22 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1973 | 6 | 23 | 741.8776 | 25 | 716.8776 | 28.5162 | 139.3858 | 0.77441 | 27.7418 | 89.27% | 292.3365 | 274.7963 | 6595.1107
1973 | 6 | 24 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1973 | 6 | 25 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1973 | 6 | 26 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1973 | 6 | 27 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1973 | 6 | 28 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1973 | 6 | 29 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1973 | 6 | 30 | 988.7347 | 25 | 963.7347 | 28.0225 | 139.3858 | 0.77441 | 27.2481 | 89.27% | 287.1338 | 269.9058 | 6477.7392
1973 | 7 | 1 | 2311.8367 | 5 | 2306.8367 | 25.3763 | 139.3858 | 0.77441 | 24.6019 | 89.27% | 259.2488 | 243.6939 | 5848.6529
1973 | 7 | 2 | 1247.3469 | 5 | 1242.3469 | 27.5053 | 139.3858 | 0.77441 | 26.7309 | 89.27% | 281.6834 | 264.7824 | 6354.7786
1973 | 7 | 3 | 717.0612 | 5 | 712.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1973 | 7 | 4 | 523.7551 | 5 | 518.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1973 | 7 | 5 | 813.7143 | 5 | 808.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1973 | 7 | 6 | 798.0408 | 5 | 793.0408 | 28.4039 | 139.3858 | 0.77441 | 27.6295 | 89.27% | 291.1528 | 273.6836 | 6568.4071
1973 | 7 | 7 | 491.102 | 5 | 486.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1973 | 7 | 8 | 335.6735 | 5 | 330.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1973 | 7 | 9 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1973 | 7 | 10 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1973 | 7 | 11 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1973 | 7 | 12 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1973 | 7 | 13 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1973 | 7 | 14 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1973 | 7 | 15 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1973 | 7 | 16 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1973 | 7 | 17 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1973 | 7 | 18 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1973 | 7 | 19 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1973 | 7 | 20 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1973 | 7 | 21 | 291.2653 | 5 | 286.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1973 | 7 | 22 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1973 | 7 | 23 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1973 | 7 | 24 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1973 | 7 | 25 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1973 | 7 | 26 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1973 | 7 | 27 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1973 | 7 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1973 | 7 | 29 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1973 | 7 | 30 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1973 | 7 | 31 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1973 | 8 | 1 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1973 | 8 | 2 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1973 | 8 | 3 | 963.9184 | 5 | 958.9184 | 28.0722 | 139.3858 | 0.77441 | 27.2978 | 89.27% | 287.6568 | 270.3974 | 6489.5384
1973 | 8 | 4 | 1933.0612 | 5 | 1928.0612 | 26.1339 | 139.3858 | 0.77441 | 25.3595 | 89.27% | 267.2317 | 251.1978 | 6028.7467
1973 | 8 | 5 | 1003.102 | 5 | 998.102 | 27.9938 | 139.3858 | 0.77441 | 27.2194 | 89.27% | 286.831 | 269.6212 | 6470.908
1973 | 8 | 6 | 509.3878 | 5 | 504.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1973 | 8 | 7 | 321.3061 | 5 | 316.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1973 | 8 | 8 | 448 | 5 | 443 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1973 | 8 | 9 | 304.3265 | 5 | 299.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1973 | 8 | 10 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1973 | 8 | 11 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1973 | 8 | 12 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1973 | 8 | 13 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1973 | 8 | 14 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1973 | 8 | 15 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1973 | 8 | 16 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1973 | 8 | 17 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1973 | 8 | 18 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1973 | 8 | 19 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1973 | 8 | 20 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1973 | 8 | 21 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1973 | 8 | 22 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1973 | 8 | 23 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1973 | 8 | 24 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1973 | 8 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1973 | 8 | 26 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1973 | 8 | 27 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1973 | 8 | 28 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1973 | 8 | 29 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1973 | 8 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1973 | 8 | 31 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1973 | 9 | 1 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1973 | 9 | 2 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1973 | 9 | 3 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1973 | 9 | 4 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1973 | 9 | 5 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1973 | 9 | 6 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1973 | 9 | 7 | 411.4286 | 15 | 396.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1973 | 9 | 8 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1973 | 9 | 9 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1973 | 9 | 10 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1973 | 9 | 11 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1973 | 9 | 12 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1973 | 9 | 13 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1973 | 9 | 14 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1973 | 9 | 15 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1973 | 9 | 16 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1973 | 9 | 17 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1973 | 9 | 18 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1973 | 9 | 19 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1973 | 9 | 20 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1973 | 9 | 21 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1973 | 9 | 22 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1973 | 9 | 23 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1973 | 9 | 24 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1973 | 9 | 25 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1973 | 9 | 26 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1973 | 9 | 27 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1973 | 9 | 28 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1973 | 9 | 29 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1973 | 9 | 30 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1973 | 10 | 1 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1973 | 10 | 2 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1973 | 10 | 3 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1973 | 10 | 4 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1973 | 10 | 5 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1973 | 10 | 6 | 242.9388 | 15 | 227.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1973 | 10 | 7 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1973 | 10 | 8 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1973 | 10 | 9 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1973 | 10 | 10 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1973 | 10 | 11 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1973 | 10 | 12 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1973 | 10 | 13 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1973 | 10 | 14 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1973 | 10 | 15 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1973 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1973 | 10 | 17 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1973 | 10 | 18 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1973 | 10 | 19 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1973 | 10 | 20 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1973 | 10 | 21 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1973 | 10 | 22 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1973 | 10 | 23 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1973 | 10 | 24 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1973 | 10 | 25 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1973 | 10 | 26 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1973 | 10 | 27 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1973 | 10 | 28 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1973 | 10 | 29 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1973 | 10 | 30 | 372.2449 | 15 | 357.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1973 | 10 | 31 | 798.0408 | 15 | 783.0408 | 28.4039 | 139.3858 | 0.77441 | 27.6295 | 89.27% | 291.1528 | 273.6836 | 6568.4071
1973 | 11 | 1 | 522.449 | 15 | 507.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1973 | 11 | 2 | 690.9388 | 15 | 675.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
1973 | 11 | 3 | 414.0408 | 15 | 399.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1973 | 11 | 4 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1973 | 11 | 5 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1973 | 11 | 6 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1973 | 11 | 7 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1973 | 11 | 8 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1973 | 11 | 9 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1973 | 11 | 10 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1973 | 11 | 11 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1973 | 11 | 12 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1973 | 11 | 13 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1973 | 11 | 14 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1973 | 11 | 15 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1973 | 11 | 16 | 335.6735 | 15 | 320.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1973 | 11 | 17 | 329.1429 | 15 | 314.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1973 | 11 | 18 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1973 | 11 | 19 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1973 | 11 | 20 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1973 | 11 | 21 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1973 | 11 | 22 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1973 | 11 | 23 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1973 | 11 | 24 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1973 | 11 | 25 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1973 | 11 | 26 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1973 | 11 | 27 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1973 | 11 | 28 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1973 | 11 | 29 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1973 | 11 | 30 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1973 | 12 | 1 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1973 | 12 | 2 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1973 | 12 | 3 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1973 | 12 | 4 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1973 | 12 | 5 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1973 | 12 | 6 | 368.3265 | 5 | 363.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1973 | 12 | 7 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1973 | 12 | 8 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1973 | 12 | 9 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1973 | 12 | 10 | 910.3673 | 5 | 905.3673 | 28.1793 | 139.3858 | 0.77441 | 27.4049 | 89.27% | 288.7855 | 271.4583 | 6515
1973 | 12 | 11 | 615.1837 | 5 | 610.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1973 | 12 | 12 | 395.7551 | 5 | 390.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1973 | 12 | 13 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1973 | 12 | 14 | 741.8776 | 5 | 736.8776 | 28.5162 | 139.3858 | 0.77441 | 27.7418 | 89.27% | 292.3365 | 274.7963 | 6595.1107
1973 | 12 | 15 | 2716.7347 | 5 | 2711.7347 | 24.5665 | 0 | 0 | 24.5665 | 0% | 0 | 0 | 0
1973 | 12 | 16 | 1080.1633 | 5 | 1075.1633 | 27.8397 | 139.3858 | 0.77441 | 27.0653 | 89.27% | 285.2069 | 268.0945 | 6434.2683
1973 | 12 | 17 | 1286.5306 | 5 | 1281.5306 | 27.4269 | 139.3858 | 0.77441 | 26.6525 | 89.27% | 280.8576 | 264.0062 | 6336.1482
1973 | 12 | 18 | 2821.2245 | 5 | 2816.2245 | 24.3576 | 0 | 0 | 24.3576 | 0% | 0 | 0 | 0
1973 | 12 | 19 | 1142.8571 | 5 | 1137.8571 | 27.7143 | 139.3858 | 0.77441 | 26.9399 | 89.27% | 283.8856 | 266.8525 | 6404.4596
1973 | 12 | 20 | 690.9388 | 5 | 685.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
1973 | 12 | 21 | 2063.6735 | 5 | 2058.6735 | 25.8727 | 139.3858 | 0.77441 | 25.0982 | 89.27% | 264.479 | 248.6102 | 5966.6454
1973 | 12 | 22 | 2964.898 | 5 | 2959.898 | 24.0702 | 0 | 0 | 24.0702 | 0% | 0 | 0 | 0
1973 | 12 | 23 | 1136.3265 | 5 | 1131.3265 | 27.7273 | 139.3858 | 0.77441 | 26.9529 | 89.27% | 284.0233 | 266.9819 | 6407.5647
1973 | 12 | 24 | 640 | 5 | 635 | 28.72 | 139.3858 | 0.77441 | 27.9456 | 89.27% | 294.4836 | 276.8146 | 6643.5497
1973 | 12 | 25 | 434.9388 | 5 | 429.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1973 | 12 | 26 | 403.5918 | 5 | 398.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1973 | 12 | 27 | 556.4082 | 5 | 551.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1973 | 12 | 28 | 586.449 | 5 | 581.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1973 | 12 | 29 | 505.4694 | 5 | 500.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1973 | 12 | 30 | 403.5918 | 5 | 398.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1973 | 12 | 31 | 323.9184 | 5 | 318.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1974 | 1 | 1 | 300.4082 | 5 | 295.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1974 | 1 | 2 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1974 | 1 | 3 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1974 | 1 | 4 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1974 | 1 | 5 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1974 | 1 | 6 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1974 | 1 | 7 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1974 | 1 | 8 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1974 | 1 | 9 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1974 | 1 | 10 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1974 | 1 | 11 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1974 | 1 | 12 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1974 | 1 | 13 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1974 | 1 | 14 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1974 | 1 | 15 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1974 | 1 | 16 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1974 | 1 | 17 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1974 | 1 | 18 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1974 | 1 | 19 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1974 | 1 | 20 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1974 | 1 | 21 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1974 | 1 | 22 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1974 | 1 | 23 | 263.8367 | 5 | 258.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1974 | 1 | 24 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1974 | 1 | 25 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1974 | 1 | 26 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1974 | 1 | 27 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1974 | 1 | 28 | 410.1224 | 5 | 405.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1974 | 1 | 29 | 373.551 | 5 | 368.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1974 | 1 | 30 | 304.3265 | 5 | 299.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1974 | 1 | 31 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1974 | 2 | 1 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1974 | 2 | 2 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1974 | 2 | 3 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1974 | 2 | 4 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1974 | 2 | 5 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1974 | 2 | 6 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1974 | 2 | 7 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1974 | 2 | 8 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1974 | 2 | 9 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1974 | 2 | 10 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1974 | 2 | 11 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1974 | 2 | 12 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1974 | 2 | 13 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1974 | 2 | 14 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1974 | 2 | 15 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1974 | 2 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1974 | 2 | 17 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1974 | 2 | 18 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1974 | 2 | 19 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1974 | 2 | 20 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1974 | 2 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1974 | 2 | 22 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1974 | 2 | 23 | 279.5102 | 5 | 274.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1974 | 2 | 24 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1974 | 2 | 25 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1974 | 2 | 26 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1974 | 2 | 27 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1974 | 2 | 28 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1974 | 3 | 1 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1974 | 3 | 2 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1974 | 3 | 3 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1974 | 3 | 4 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1974 | 3 | 5 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1974 | 3 | 6 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1974 | 3 | 7 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1974 | 3 | 8 | 698.7755 | 25 | 673.7755 | 28.6024 | 139.3858 | 0.77441 | 27.828 | 89.27% | 293.2449 | 275.6502 | 6615.6041
1974 | 3 | 9 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1974 | 3 | 10 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1974 | 3 | 11 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1974 | 3 | 12 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1974 | 3 | 13 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1974 | 3 | 14 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1974 | 3 | 15 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1974 | 3 | 16 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1974 | 3 | 17 | 1619.5918 | 25 | 1594.5918 | 26.7608 | 139.3858 | 0.77441 | 25.9864 | 89.27% | 273.8382 | 257.4079 | 6177.7898
1974 | 3 | 18 | 1384.4898 | 25 | 1359.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
1974 | 3 | 19 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1974 | 3 | 20 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1974 | 3 | 21 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1974 | 3 | 22 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1974 | 3 | 23 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1974 | 3 | 24 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1974 | 3 | 25 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1974 | 3 | 26 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1974 | 3 | 27 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1974 | 3 | 28 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1974 | 3 | 29 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1974 | 3 | 30 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1974 | 3 | 31 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1974 | 4 | 1 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1974 | 4 | 2 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1974 | 4 | 3 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1974 | 4 | 4 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1974 | 4 | 5 | 845.0612 | 25 | 820.0612 | 28.3099 | 139.3858 | 0.77441 | 27.5355 | 89.27% | 290.1618 | 272.7521 | 6546.0506
1974 | 4 | 6 | 1410.6122 | 25 | 1385.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1974 | 4 | 7 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1974 | 4 | 8 | 671.3469 | 25 | 646.3469 | 28.6573 | 139.3858 | 0.77441 | 27.8829 | 89.27% | 293.8229 | 276.1936 | 6628.6454
1974 | 4 | 9 | 462.3673 | 25 | 437.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
1974 | 4 | 10 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1974 | 4 | 11 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1974 | 4 | 12 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1974 | 4 | 13 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1974 | 4 | 14 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1974 | 4 | 15 | 1064.4898 | 25 | 1039.4898 | 27.871 | 139.3858 | 0.77441 | 27.0966 | 89.27% | 285.5373 | 268.405 | 6441.7204
1974 | 4 | 16 | 1034.449 | 25 | 1009.449 | 27.9311 | 139.3858 | 0.77441 | 27.1567 | 89.27% | 286.1704 | 269.0002 | 6456.0037
1974 | 4 | 17 | 768 | 25 | 743 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
1974 | 4 | 18 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1974 | 4 | 19 | 741.8776 | 25 | 716.8776 | 28.5162 | 139.3858 | 0.77441 | 27.7418 | 89.27% | 292.3365 | 274.7963 | 6595.1107
1974 | 4 | 20 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1974 | 4 | 21 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1974 | 4 | 22 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1974 | 4 | 23 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1974 | 4 | 24 | 976.9796 | 25 | 951.9796 | 28.046 | 139.3858 | 0.77441 | 27.2716 | 89.27% | 287.3816 | 270.1387 | 6483.3283
1974 | 4 | 25 | 850.2857 | 25 | 825.2857 | 28.2994 | 139.3858 | 0.77441 | 27.525 | 89.27% | 290.0517 | 272.6486 | 6543.5666
1974 | 4 | 26 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1974 | 4 | 27 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1974 | 4 | 28 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1974 | 4 | 29 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1974 | 4 | 30 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1974 | 5 | 1 | 671.3469 | 25 | 646.3469 | 28.6573 | 139.3858 | 0.77441 | 27.8829 | 89.27% | 293.8229 | 276.1936 | 6628.6454
1974 | 5 | 2 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1974 | 5 | 3 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1974 | 5 | 4 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1974 | 5 | 5 | 410.1224 | 25 | 385.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
1974 | 5 | 6 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1974 | 5 | 7 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1974 | 5 | 8 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1974 | 5 | 9 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1974 | 5 | 10 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1974 | 5 | 11 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1974 | 5 | 12 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1974 | 5 | 13 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1974 | 5 | 14 | 877.7143 | 25 | 852.7143 | 28.2446 | 139.3858 | 0.77441 | 27.4702 | 89.27% | 289.4736 | 272.1052 | 6530.5253
1974 | 5 | 15 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1974 | 5 | 16 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1974 | 5 | 17 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1974 | 5 | 18 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1974 | 5 | 19 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1974 | 5 | 20 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1974 | 5 | 21 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1974 | 5 | 22 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1974 | 5 | 23 | 513.3061 | 25 | 488.3061 | 28.9734 | 139.3858 | 0.77441 | 28.199 | 89.27% | 297.1537 | 279.3245 | 6703.788
1974 | 5 | 24 | 824.1633 | 25 | 799.1633 | 28.3517 | 139.3858 | 0.77441 | 27.5773 | 89.27% | 290.6023 | 273.1661 | 6555.9868
1974 | 5 | 25 | 680.4898 | 25 | 655.4898 | 28.639 | 139.3858 | 0.77441 | 27.8646 | 89.27% | 293.6302 | 276.0124 | 6624.2983
1974 | 5 | 26 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1974 | 5 | 27 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1974 | 5 | 28 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1974 | 5 | 29 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1974 | 5 | 30 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1974 | 5 | 31 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1974 | 6 | 1 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1974 | 6 | 2 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1974 | 6 | 3 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1974 | 6 | 4 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1974 | 6 | 5 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1974 | 6 | 6 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1974 | 6 | 7 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1974 | 6 | 8 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1974 | 6 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1974 | 6 | 10 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1974 | 6 | 11 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1974 | 6 | 12 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1974 | 6 | 13 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1974 | 6 | 14 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1974 | 6 | 15 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1974 | 6 | 16 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1974 | 6 | 17 | 1176.8163 | 25 | 1151.8163 | 27.6464 | 139.3858 | 0.77441 | 26.872 | 89.27% | 283.1699 | 266.1797 | 6388.3133
1974 | 6 | 18 | 1035.7551 | 25 | 1010.7551 | 27.9285 | 139.3858 | 0.77441 | 27.1541 | 89.27% | 286.1429 | 268.9743 | 6455.3827
1974 | 6 | 19 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1974 | 6 | 20 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1974 | 6 | 21 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1974 | 6 | 22 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1974 | 6 | 23 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1974 | 6 | 24 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1974 | 6 | 25 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1974 | 6 | 26 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1974 | 6 | 27 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1974 | 6 | 28 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1974 | 6 | 29 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1974 | 6 | 30 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1974 | 7 | 1 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1974 | 7 | 2 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1974 | 7 | 3 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1974 | 7 | 4 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1974 | 7 | 5 | 333.0612 | 5 | 328.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1974 | 7 | 6 | 385.3061 | 5 | 380.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1974 | 7 | 7 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1974 | 7 | 8 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1974 | 7 | 9 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1974 | 7 | 10 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1974 | 7 | 11 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1974 | 7 | 12 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1974 | 7 | 13 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1974 | 7 | 14 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1974 | 7 | 15 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1974 | 7 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1974 | 7 | 17 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1974 | 7 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1974 | 7 | 19 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1974 | 7 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1974 | 7 | 21 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1974 | 7 | 22 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1974 | 7 | 23 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1974 | 7 | 24 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1974 | 7 | 25 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1974 | 7 | 26 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1974 | 7 | 27 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1974 | 7 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1974 | 7 | 29 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1974 | 7 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1974 | 7 | 31 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1974 | 8 | 1 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1974 | 8 | 2 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1974 | 8 | 3 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1974 | 8 | 4 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1974 | 8 | 5 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1974 | 8 | 6 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1974 | 8 | 7 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1974 | 8 | 8 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1974 | 8 | 9 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1974 | 8 | 10 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1974 | 8 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1974 | 8 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1974 | 8 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1974 | 8 | 14 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1974 | 8 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1974 | 8 | 16 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1974 | 8 | 17 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1974 | 8 | 18 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1974 | 8 | 19 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1974 | 8 | 20 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1974 | 8 | 21 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1974 | 8 | 22 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1974 | 8 | 23 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1974 | 8 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1974 | 8 | 25 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1974 | 8 | 26 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1974 | 8 | 27 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1974 | 8 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1974 | 8 | 29 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1974 | 8 | 30 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1974 | 8 | 31 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1974 | 9 | 1 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1974 | 9 | 2 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1974 | 9 | 3 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1974 | 9 | 4 | 266.449 | 15 | 251.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1974 | 9 | 5 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1974 | 9 | 6 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1974 | 9 | 7 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1974 | 9 | 8 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1974 | 9 | 9 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1974 | 9 | 10 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1974 | 9 | 11 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1974 | 9 | 12 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1974 | 9 | 13 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1974 | 9 | 14 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1974 | 9 | 15 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1974 | 9 | 16 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1974 | 9 | 17 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1974 | 9 | 18 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1974 | 9 | 19 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1974 | 9 | 20 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1974 | 9 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1974 | 9 | 22 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1974 | 9 | 23 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1974 | 9 | 24 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1974 | 9 | 25 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1974 | 9 | 26 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1974 | 9 | 27 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1974 | 9 | 28 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1974 | 9 | 29 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1974 | 9 | 30 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1974 | 10 | 1 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1974 | 10 | 2 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1974 | 10 | 3 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1974 | 10 | 4 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1974 | 10 | 5 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1974 | 10 | 6 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1974 | 10 | 7 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1974 | 10 | 8 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1974 | 10 | 9 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1974 | 10 | 10 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1974 | 10 | 11 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1974 | 10 | 12 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1974 | 10 | 13 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1974 | 10 | 14 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1974 | 10 | 15 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1974 | 10 | 16 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1974 | 10 | 17 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1974 | 10 | 18 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1974 | 10 | 19 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1974 | 10 | 20 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1974 | 10 | 21 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1974 | 10 | 22 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1974 | 10 | 23 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1974 | 10 | 24 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1974 | 10 | 25 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1974 | 10 | 26 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1974 | 10 | 27 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1974 | 10 | 28 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1974 | 10 | 29 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1974 | 10 | 30 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1974 | 10 | 31 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1974 | 11 | 1 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1974 | 11 | 2 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1974 | 11 | 3 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1974 | 11 | 4 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1974 | 11 | 5 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1974 | 11 | 6 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1974 | 11 | 7 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1974 | 11 | 8 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1974 | 11 | 9 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1974 | 11 | 10 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1974 | 11 | 11 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1974 | 11 | 12 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1974 | 11 | 13 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1974 | 11 | 14 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1974 | 11 | 15 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1974 | 11 | 16 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1974 | 11 | 17 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1974 | 11 | 18 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1974 | 11 | 19 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1974 | 11 | 20 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1974 | 11 | 21 | 377.4694 | 15 | 362.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1974 | 11 | 22 | 344.8163 | 15 | 329.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1974 | 11 | 23 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1974 | 11 | 24 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1974 | 11 | 25 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1974 | 11 | 26 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1974 | 11 | 27 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1974 | 11 | 28 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1974 | 11 | 29 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1974 | 11 | 30 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1974 | 12 | 1 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1974 | 12 | 2 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1974 | 12 | 3 | 338.2857 | 5 | 333.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1974 | 12 | 4 | 266.449 | 5 | 261.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1974 | 12 | 5 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1974 | 12 | 6 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1974 | 12 | 7 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1974 | 12 | 8 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1974 | 12 | 9 | 1488.9796 | 5 | 1483.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1974 | 12 | 10 | 1008.3265 | 5 | 1003.3265 | 27.9833 | 139.3858 | 0.77441 | 27.2089 | 89.27% | 286.7209 | 269.5177 | 6468.424
1974 | 12 | 11 | 556.4082 | 5 | 551.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1974 | 12 | 12 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1974 | 12 | 13 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1974 | 12 | 14 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1974 | 12 | 15 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1974 | 12 | 16 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1974 | 12 | 17 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1974 | 12 | 18 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1974 | 12 | 19 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1974 | 12 | 20 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1974 | 12 | 21 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1974 | 12 | 22 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1974 | 12 | 23 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1974 | 12 | 24 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1974 | 12 | 25 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1974 | 12 | 26 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1974 | 12 | 27 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1974 | 12 | 28 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1974 | 12 | 29 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1974 | 12 | 30 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1974 | 12 | 31 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1975 | 1 | 1 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1975 | 1 | 2 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1975 | 1 | 3 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1975 | 1 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1975 | 1 | 5 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1975 | 1 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1975 | 1 | 7 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1975 | 1 | 8 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1975 | 1 | 9 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1975 | 1 | 10 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1975 | 1 | 11 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1975 | 1 | 12 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1975 | 1 | 13 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1975 | 1 | 14 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1975 | 1 | 15 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1975 | 1 | 16 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1975 | 1 | 17 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1975 | 1 | 18 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1975 | 1 | 19 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1975 | 1 | 20 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1975 | 1 | 21 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1975 | 1 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1975 | 1 | 23 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1975 | 1 | 24 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1975 | 1 | 25 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1975 | 1 | 26 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1975 | 1 | 27 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1975 | 1 | 28 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1975 | 1 | 29 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1975 | 1 | 30 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1975 | 1 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1975 | 2 | 1 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1975 | 2 | 2 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1975 | 2 | 3 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1975 | 2 | 4 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1975 | 2 | 5 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1975 | 2 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1975 | 2 | 7 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1975 | 2 | 8 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1975 | 2 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1975 | 2 | 10 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1975 | 2 | 11 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1975 | 2 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1975 | 2 | 13 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1975 | 2 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1975 | 2 | 15 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1975 | 2 | 16 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1975 | 2 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1975 | 2 | 18 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1975 | 2 | 19 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1975 | 2 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1975 | 2 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1975 | 2 | 22 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1975 | 2 | 23 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1975 | 2 | 24 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1975 | 2 | 25 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1975 | 2 | 26 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1975 | 2 | 27 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1975 | 2 | 28 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1975 | 3 | 1 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1975 | 3 | 2 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1975 | 3 | 3 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1975 | 3 | 4 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1975 | 3 | 5 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1975 | 3 | 6 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1975 | 3 | 7 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1975 | 3 | 8 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1975 | 3 | 9 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1975 | 3 | 10 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1975 | 3 | 11 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1975 | 3 | 12 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1975 | 3 | 13 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1975 | 3 | 14 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1975 | 3 | 15 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1975 | 3 | 16 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1975 | 3 | 17 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1975 | 3 | 18 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1975 | 3 | 19 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1975 | 3 | 20 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1975 | 3 | 21 | 1502.0408 | 25 | 1477.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1975 | 3 | 22 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1975 | 3 | 23 | 706.6122 | 25 | 681.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
1975 | 3 | 24 | 606.0408 | 25 | 581.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1975 | 3 | 25 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
1975 | 3 | 26 | 671.3469 | 25 | 646.3469 | 28.6573 | 139.3858 | 0.77441 | 27.8829 | 89.27% | 293.8229 | 276.1936 | 6628.6454
1975 | 3 | 27 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1975 | 3 | 28 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1975 | 3 | 29 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1975 | 3 | 30 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1975 | 3 | 31 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1975 | 4 | 1 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1975 | 4 | 2 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1975 | 4 | 3 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1975 | 4 | 4 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1975 | 4 | 5 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1975 | 4 | 6 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1975 | 4 | 7 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1975 | 4 | 8 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1975 | 4 | 9 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1975 | 4 | 10 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1975 | 4 | 11 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1975 | 4 | 12 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1975 | 4 | 13 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1975 | 4 | 14 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1975 | 4 | 15 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1975 | 4 | 16 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1975 | 4 | 17 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1975 | 4 | 18 | 877.7143 | 25 | 852.7143 | 28.2446 | 139.3858 | 0.77441 | 27.4702 | 89.27% | 289.4736 | 272.1052 | 6530.5253
1975 | 4 | 19 | 1155.9184 | 25 | 1130.9184 | 27.6882 | 139.3858 | 0.77441 | 26.9138 | 89.27% | 283.6104 | 266.5937 | 6398.2495
1975 | 4 | 20 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1975 | 4 | 21 | 1142.8571 | 25 | 1117.8571 | 27.7143 | 139.3858 | 0.77441 | 26.9399 | 89.27% | 283.8856 | 266.8525 | 6404.4596
1975 | 4 | 22 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1975 | 4 | 23 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1975 | 4 | 24 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1975 | 4 | 25 | 939.102 | 25 | 914.102 | 28.1218 | 139.3858 | 0.77441 | 27.3474 | 89.27% | 288.1799 | 270.8891 | 6501.3377
1975 | 4 | 26 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1975 | 4 | 27 | 803.2653 | 25 | 778.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
1975 | 4 | 28 | 645.2245 | 25 | 620.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
1975 | 4 | 29 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1975 | 4 | 30 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1975 | 5 | 1 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1975 | 5 | 2 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1975 | 5 | 3 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1975 | 5 | 4 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1975 | 5 | 5 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1975 | 5 | 6 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1975 | 5 | 7 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1975 | 5 | 8 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1975 | 5 | 9 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1975 | 5 | 10 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1975 | 5 | 11 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1975 | 5 | 12 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1975 | 5 | 13 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1975 | 5 | 14 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1975 | 5 | 15 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1975 | 5 | 16 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1975 | 5 | 17 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1975 | 5 | 18 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1975 | 5 | 19 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1975 | 5 | 20 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1975 | 5 | 21 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1975 | 5 | 22 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1975 | 5 | 23 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1975 | 5 | 24 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1975 | 5 | 25 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1975 | 5 | 26 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1975 | 5 | 27 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1975 | 5 | 28 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1975 | 5 | 29 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1975 | 5 | 30 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1975 | 5 | 31 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1975 | 6 | 1 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1975 | 6 | 2 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1975 | 6 | 3 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1975 | 6 | 4 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1975 | 6 | 5 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1975 | 6 | 6 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1975 | 6 | 7 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1975 | 6 | 8 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1975 | 6 | 9 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1975 | 6 | 10 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1975 | 6 | 11 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1975 | 6 | 12 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1975 | 6 | 13 | 425.7959 | 25 | 400.7959 | 29.1484 | 139.3858 | 0.77441 | 28.374 | 89.27% | 298.998 | 281.0582 | 6745.3959
1975 | 6 | 14 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1975 | 6 | 15 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1975 | 6 | 16 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1975 | 6 | 17 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1975 | 6 | 18 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1975 | 6 | 19 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1975 | 6 | 20 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1975 | 6 | 21 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1975 | 6 | 22 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1975 | 6 | 23 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1975 | 6 | 24 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1975 | 6 | 25 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1975 | 6 | 26 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1975 | 6 | 27 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1975 | 6 | 28 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1975 | 6 | 29 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1975 | 6 | 30 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1975 | 7 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1975 | 7 | 2 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1975 | 7 | 3 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1975 | 7 | 4 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1975 | 7 | 5 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 7 | 6 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 7 | 7 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 7 | 8 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 7 | 9 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 7 | 10 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1975 | 7 | 11 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1975 | 7 | 12 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1975 | 7 | 13 | 305.6327 | 5 | 300.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1975 | 7 | 14 | 586.449 | 5 | 581.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1975 | 7 | 15 | 421.8776 | 5 | 416.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1975 | 7 | 16 | 368.3265 | 5 | 363.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1975 | 7 | 17 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1975 | 7 | 18 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1975 | 7 | 19 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1975 | 7 | 20 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1975 | 7 | 21 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1975 | 7 | 22 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1975 | 7 | 23 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1975 | 7 | 24 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1975 | 7 | 25 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1975 | 7 | 26 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1975 | 7 | 27 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1975 | 7 | 28 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1975 | 7 | 29 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1975 | 7 | 30 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1975 | 7 | 31 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1975 | 8 | 1 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1975 | 8 | 2 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1975 | 8 | 3 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1975 | 8 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 8 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 8 | 6 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 8 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 8 | 8 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1975 | 8 | 9 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1975 | 8 | 10 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1975 | 8 | 11 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 8 | 12 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 8 | 13 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 8 | 14 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1975 | 8 | 15 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1975 | 8 | 16 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1975 | 8 | 17 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1975 | 8 | 18 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1975 | 8 | 19 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1975 | 8 | 20 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1975 | 8 | 21 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1975 | 8 | 22 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1975 | 8 | 23 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1975 | 8 | 24 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1975 | 8 | 25 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1975 | 8 | 26 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1975 | 8 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1975 | 8 | 28 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1975 | 8 | 29 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1975 | 8 | 30 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1975 | 8 | 31 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1975 | 9 | 1 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1975 | 9 | 2 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1975 | 9 | 3 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1975 | 9 | 4 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1975 | 9 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1975 | 9 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1975 | 9 | 7 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1975 | 9 | 8 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1975 | 9 | 9 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1975 | 9 | 10 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1975 | 9 | 11 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1975 | 9 | 12 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1975 | 9 | 13 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1975 | 9 | 14 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1975 | 9 | 15 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1975 | 9 | 16 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1975 | 9 | 17 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1975 | 9 | 18 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1975 | 9 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1975 | 9 | 20 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1975 | 9 | 21 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1975 | 9 | 22 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1975 | 9 | 23 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1975 | 9 | 24 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1975 | 9 | 25 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1975 | 9 | 26 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1975 | 9 | 27 | 376.1633 | 15 | 361.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1975 | 9 | 28 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1975 | 9 | 29 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1975 | 9 | 30 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1975 | 10 | 1 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1975 | 10 | 2 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1975 | 10 | 3 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1975 | 10 | 4 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1975 | 10 | 5 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1975 | 10 | 6 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1975 | 10 | 7 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1975 | 10 | 8 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1975 | 10 | 9 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1975 | 10 | 10 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1975 | 10 | 11 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1975 | 10 | 12 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1975 | 10 | 13 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1975 | 10 | 14 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1975 | 10 | 15 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1975 | 10 | 16 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1975 | 10 | 17 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1975 | 10 | 18 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1975 | 10 | 19 | 338.2857 | 15 | 323.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1975 | 10 | 20 | 453.2245 | 15 | 438.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
1975 | 10 | 21 | 630.8571 | 15 | 615.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1975 | 10 | 22 | 370.9388 | 15 | 355.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1975 | 10 | 23 | 269.0612 | 15 | 254.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1975 | 10 | 24 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1975 | 10 | 25 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1975 | 10 | 26 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1975 | 10 | 27 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1975 | 10 | 28 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1975 | 10 | 29 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1975 | 10 | 30 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1975 | 10 | 31 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1975 | 11 | 1 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1975 | 11 | 2 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1975 | 11 | 3 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1975 | 11 | 4 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1975 | 11 | 5 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1975 | 11 | 6 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1975 | 11 | 7 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1975 | 11 | 8 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1975 | 11 | 9 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1975 | 11 | 10 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1975 | 11 | 11 | 253.3878 | 15 | 238.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1975 | 11 | 12 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1975 | 11 | 13 | 483.2653 | 15 | 468.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1975 | 11 | 14 | 845.0612 | 15 | 830.0612 | 28.3099 | 139.3858 | 0.77441 | 27.5355 | 89.27% | 290.1618 | 272.7521 | 6546.0506
1975 | 11 | 15 | 680.4898 | 15 | 665.4898 | 28.639 | 139.3858 | 0.77441 | 27.8646 | 89.27% | 293.6302 | 276.0124 | 6624.2983
1975 | 11 | 16 | 395.7551 | 15 | 380.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1975 | 11 | 17 | 287.3469 | 15 | 272.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1975 | 11 | 18 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1975 | 11 | 19 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1975 | 11 | 20 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1975 | 11 | 21 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1975 | 11 | 22 | 798.0408 | 15 | 783.0408 | 28.4039 | 139.3858 | 0.77441 | 27.6295 | 89.27% | 291.1528 | 273.6836 | 6568.4071
1975 | 11 | 23 | 491.102 | 15 | 476.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1975 | 11 | 24 | 338.2857 | 15 | 323.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1975 | 11 | 25 | 279.5102 | 15 | 264.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1975 | 11 | 26 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1975 | 11 | 27 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1975 | 11 | 28 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1975 | 11 | 29 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1975 | 11 | 30 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1975 | 12 | 1 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1975 | 12 | 2 | 344.8163 | 5 | 339.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1975 | 12 | 3 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1975 | 12 | 4 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1975 | 12 | 5 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1975 | 12 | 6 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1975 | 12 | 7 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1975 | 12 | 8 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1975 | 12 | 9 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1975 | 12 | 10 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1975 | 12 | 11 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1975 | 12 | 12 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1975 | 12 | 13 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1975 | 12 | 14 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1975 | 12 | 15 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1975 | 12 | 16 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1975 | 12 | 17 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1975 | 12 | 18 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1975 | 12 | 19 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1975 | 12 | 20 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1975 | 12 | 21 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1975 | 12 | 22 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1975 | 12 | 23 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1975 | 12 | 24 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1975 | 12 | 25 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1975 | 12 | 26 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1975 | 12 | 27 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1975 | 12 | 28 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1975 | 12 | 29 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1975 | 12 | 30 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1975 | 12 | 31 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1976 | 1 | 1 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1976 | 1 | 2 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1976 | 1 | 3 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1976 | 1 | 4 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1976 | 1 | 5 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1976 | 1 | 6 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1976 | 1 | 7 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1976 | 1 | 8 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1976 | 1 | 9 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1976 | 1 | 10 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1976 | 1 | 11 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1976 | 1 | 12 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1976 | 1 | 13 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1976 | 1 | 14 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1976 | 1 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1976 | 1 | 16 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1976 | 1 | 17 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1976 | 1 | 18 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1976 | 1 | 19 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1976 | 1 | 20 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1976 | 1 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1976 | 1 | 22 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1976 | 1 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1976 | 1 | 24 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1976 | 1 | 25 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1976 | 1 | 26 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1976 | 1 | 27 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1976 | 1 | 28 | 587.7551 | 5 | 582.7551 | 28.8245 | 139.3858 | 0.77441 | 28.0501 | 89.27% | 295.5847 | 277.8496 | 6668.3902
1976 | 1 | 29 | 660.898 | 5 | 655.898 | 28.6782 | 139.3858 | 0.77441 | 27.9038 | 89.27% | 294.0432 | 276.4006 | 6633.6135
1976 | 1 | 30 | 505.4694 | 5 | 500.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1976 | 1 | 31 | 370.9388 | 5 | 365.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1976 | 2 | 1 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1976 | 2 | 2 | 500.2449 | 5 | 495.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1976 | 2 | 3 | 720.9796 | 5 | 715.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
1976 | 2 | 4 | 547.2653 | 5 | 542.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
1976 | 2 | 5 | 414.0408 | 5 | 409.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1976 | 2 | 6 | 344.8163 | 5 | 339.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1976 | 2 | 7 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1976 | 2 | 8 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1976 | 2 | 9 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1976 | 2 | 10 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1976 | 2 | 11 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1976 | 2 | 12 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1976 | 2 | 13 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1976 | 2 | 14 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1976 | 2 | 15 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1976 | 2 | 16 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1976 | 2 | 17 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1976 | 2 | 18 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1976 | 2 | 19 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1976 | 2 | 20 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1976 | 2 | 21 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1976 | 2 | 22 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1976 | 2 | 23 | 233.7959 | 5 | 228.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1976 | 2 | 24 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1976 | 2 | 25 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1976 | 2 | 26 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1976 | 2 | 27 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1976 | 2 | 28 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1976 | 2 | 29 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1976 | 3 | 1 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1976 | 3 | 2 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1976 | 3 | 3 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1976 | 3 | 4 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1976 | 3 | 5 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1976 | 3 | 6 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1976 | 3 | 7 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1976 | 3 | 8 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1976 | 3 | 9 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1976 | 3 | 10 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1976 | 3 | 11 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1976 | 3 | 12 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1976 | 3 | 13 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1976 | 3 | 14 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1976 | 3 | 15 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1976 | 3 | 16 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1976 | 3 | 17 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1976 | 3 | 18 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1976 | 3 | 19 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1976 | 3 | 20 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1976 | 3 | 21 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1976 | 3 | 22 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1976 | 3 | 23 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1976 | 3 | 24 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1976 | 3 | 25 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1976 | 3 | 26 | 521.1429 | 25 | 496.1429 | 28.9577 | 139.3858 | 0.77441 | 28.1833 | 89.27% | 296.9886 | 279.1692 | 6700.0619
1976 | 3 | 27 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1976 | 3 | 28 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
1976 | 3 | 29 | 1632.6531 | 25 | 1607.6531 | 26.7347 | 139.3858 | 0.77441 | 25.9603 | 89.27% | 273.5629 | 257.1492 | 6171.5797
1976 | 3 | 30 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
1976 | 3 | 31 | 1206.8571 | 25 | 1181.8571 | 27.5863 | 139.3858 | 0.77441 | 26.8119 | 89.27% | 282.5368 | 265.5846 | 6374.03
1976 | 4 | 1 | 1266.9388 | 25 | 1241.9388 | 27.4661 | 139.3858 | 0.77441 | 26.6917 | 89.27% | 281.2705 | 264.3943 | 6345.4634
1976 | 4 | 2 | 3239.1837 | 25 | 3214.1837 | 23.5216 | 0 | 0 | 23.5216 | 0% | 0 | 0 | 0
1976 | 4 | 3 | 2037.551 | 25 | 2012.551 | 25.9249 | 139.3858 | 0.77441 | 25.1505 | 89.27% | 265.0295 | 249.1277 | 5979.0656
1976 | 4 | 4 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1976 | 4 | 5 | 1009.6327 | 25 | 984.6327 | 27.9807 | 139.3858 | 0.77441 | 27.2063 | 89.27% | 286.6934 | 269.4918 | 6467.803
1976 | 4 | 6 | 812.4082 | 25 | 787.4082 | 28.3752 | 139.3858 | 0.77441 | 27.6008 | 89.27% | 290.85 | 273.399 | 6561.576
1976 | 4 | 7 | 783.6735 | 25 | 758.6735 | 28.4327 | 139.3858 | 0.77441 | 27.6582 | 89.27% | 291.4556 | 273.9683 | 6575.2383
1976 | 4 | 8 | 679.1837 | 25 | 654.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
1976 | 4 | 9 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1976 | 4 | 10 | 506.7755 | 25 | 481.7755 | 28.9864 | 139.3858 | 0.77441 | 28.212 | 89.27% | 297.2914 | 279.4539 | 6706.893
1976 | 4 | 11 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
1976 | 4 | 12 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1976 | 4 | 13 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1976 | 4 | 14 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1976 | 4 | 15 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1976 | 4 | 16 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1976 | 4 | 17 | 485.8776 | 25 | 460.8776 | 29.0282 | 139.3858 | 0.77441 | 28.2538 | 89.27% | 297.7318 | 279.8679 | 6716.8293
1976 | 4 | 18 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1976 | 4 | 19 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1976 | 4 | 20 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1976 | 4 | 21 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1976 | 4 | 22 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1976 | 4 | 23 | 441.4694 | 25 | 416.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
1976 | 4 | 24 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1976 | 4 | 25 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1976 | 4 | 26 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1976 | 4 | 27 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1976 | 4 | 28 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1976 | 4 | 29 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1976 | 4 | 30 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1976 | 5 | 1 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1976 | 5 | 2 | 676.5714 | 25 | 651.5714 | 28.6469 | 139.3858 | 0.77441 | 27.8724 | 89.27% | 293.7128 | 276.0901 | 6626.1613
1976 | 5 | 3 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1976 | 5 | 4 | 643.9184 | 25 | 618.9184 | 28.7122 | 139.3858 | 0.77441 | 27.9378 | 89.27% | 294.401 | 276.7369 | 6641.6867
1976 | 5 | 5 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1976 | 5 | 6 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
1976 | 5 | 7 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1976 | 5 | 8 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1976 | 5 | 9 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1976 | 5 | 10 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1976 | 5 | 11 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1976 | 5 | 12 | 603.4286 | 25 | 578.4286 | 28.7931 | 139.3858 | 0.77441 | 28.0187 | 89.27% | 295.2543 | 277.5391 | 6660.9381
1976 | 5 | 13 | 933.8776 | 25 | 908.8776 | 28.1322 | 139.3858 | 0.77441 | 27.3578 | 89.27% | 288.29 | 270.9926 | 6503.8217
1976 | 5 | 14 | 506.7755 | 25 | 481.7755 | 28.9864 | 139.3858 | 0.77441 | 28.212 | 89.27% | 297.2914 | 279.4539 | 6706.893
1976 | 5 | 15 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1976 | 5 | 16 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1976 | 5 | 17 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1976 | 5 | 18 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1976 | 5 | 19 | 653.0612 | 25 | 628.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
1976 | 5 | 20 | 975.6735 | 25 | 950.6735 | 28.0487 | 139.3858 | 0.77441 | 27.2742 | 89.27% | 287.4091 | 270.1646 | 6483.9493
1976 | 5 | 21 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1976 | 5 | 22 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1976 | 5 | 23 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1976 | 5 | 24 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1976 | 5 | 25 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1976 | 5 | 26 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1976 | 5 | 27 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1976 | 5 | 28 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1976 | 5 | 29 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1976 | 5 | 30 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1976 | 5 | 31 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1976 | 6 | 1 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1976 | 6 | 2 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1976 | 6 | 3 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1976 | 6 | 4 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1976 | 6 | 5 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1976 | 6 | 6 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1976 | 6 | 7 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1976 | 6 | 8 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1976 | 6 | 9 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1976 | 6 | 10 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1976 | 6 | 11 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1976 | 6 | 12 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1976 | 6 | 13 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1976 | 6 | 14 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1976 | 6 | 15 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1976 | 6 | 16 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1976 | 6 | 17 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1976 | 6 | 18 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1976 | 6 | 19 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1976 | 6 | 20 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1976 | 6 | 21 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1976 | 6 | 22 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1976 | 6 | 23 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1976 | 6 | 24 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1976 | 6 | 25 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1976 | 6 | 26 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1976 | 6 | 27 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1976 | 6 | 28 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1976 | 6 | 29 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1976 | 6 | 30 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1976 | 7 | 1 | 343.5102 | 5 | 338.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1976 | 7 | 2 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1976 | 7 | 3 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1976 | 7 | 4 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1976 | 7 | 5 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1976 | 7 | 6 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1976 | 7 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1976 | 7 | 8 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1976 | 7 | 9 | 305.6327 | 5 | 300.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1976 | 7 | 10 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1976 | 7 | 11 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1976 | 7 | 12 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1976 | 7 | 13 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1976 | 7 | 14 | 259.9184 | 5 | 254.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1976 | 7 | 15 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1976 | 7 | 16 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1976 | 7 | 17 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1976 | 7 | 18 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1976 | 7 | 19 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1976 | 7 | 20 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1976 | 7 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1976 | 7 | 22 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1976 | 7 | 23 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1976 | 7 | 24 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1976 | 7 | 25 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1976 | 7 | 26 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1976 | 7 | 27 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1976 | 7 | 28 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1976 | 7 | 29 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1976 | 7 | 30 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1976 | 7 | 31 | 394.449 | 5 | 389.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1976 | 8 | 1 | 421.8776 | 5 | 416.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1976 | 8 | 2 | 434.9388 | 5 | 429.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1976 | 8 | 3 | 261.2245 | 5 | 256.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1976 | 8 | 4 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1976 | 8 | 5 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1976 | 8 | 6 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1976 | 8 | 7 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1976 | 8 | 8 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1976 | 8 | 9 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1976 | 8 | 10 | 576 | 5 | 571 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
1976 | 8 | 11 | 805.8776 | 5 | 800.8776 | 28.3882 | 139.3858 | 0.77441 | 27.6138 | 89.27% | 290.9876 | 273.5284 | 6564.681
1976 | 8 | 12 | 402.2857 | 5 | 397.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
1976 | 8 | 13 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1976 | 8 | 14 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1976 | 8 | 15 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1976 | 8 | 16 | 885.551 | 5 | 880.551 | 28.2289 | 139.3858 | 0.77441 | 27.4545 | 89.27% | 289.3085 | 271.95 | 6526.7992
1976 | 8 | 17 | 548.5714 | 5 | 543.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
1976 | 8 | 18 | 317.3878 | 5 | 312.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1976 | 8 | 19 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1976 | 8 | 20 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1976 | 8 | 21 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1976 | 8 | 22 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1976 | 8 | 23 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1976 | 8 | 24 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1976 | 8 | 25 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1976 | 8 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1976 | 8 | 27 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1976 | 8 | 28 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1976 | 8 | 29 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1976 | 8 | 30 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1976 | 8 | 31 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1976 | 9 | 1 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1976 | 9 | 2 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
1976 | 9 | 3 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1976 | 9 | 4 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1976 | 9 | 5 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1976 | 9 | 6 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1976 | 9 | 7 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1976 | 9 | 8 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1976 | 9 | 9 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1976 | 9 | 10 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1976 | 9 | 11 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1976 | 9 | 12 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1976 | 9 | 13 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1976 | 9 | 14 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1976 | 9 | 15 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1976 | 9 | 16 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1976 | 9 | 17 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1976 | 9 | 18 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1976 | 9 | 19 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1976 | 9 | 20 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1976 | 9 | 21 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1976 | 9 | 22 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1976 | 9 | 23 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1976 | 9 | 24 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1976 | 9 | 25 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1976 | 9 | 26 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1976 | 9 | 27 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1976 | 9 | 28 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1976 | 9 | 29 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1976 | 9 | 30 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1976 | 10 | 1 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1976 | 10 | 2 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1976 | 10 | 3 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1976 | 10 | 4 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1976 | 10 | 5 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1976 | 10 | 6 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1976 | 10 | 7 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1976 | 10 | 8 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1976 | 10 | 9 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1976 | 10 | 10 | 515.9184 | 15 | 500.9184 | 28.9682 | 139.3858 | 0.77441 | 28.1938 | 89.27% | 297.0987 | 279.2727 | 6702.5459
1976 | 10 | 11 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1976 | 10 | 12 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1976 | 10 | 13 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1976 | 10 | 14 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1976 | 10 | 15 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1976 | 10 | 16 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1976 | 10 | 17 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1976 | 10 | 18 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1976 | 10 | 19 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1976 | 10 | 20 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1976 | 10 | 21 | 1116.7347 | 15 | 1101.7347 | 27.7665 | 139.3858 | 0.77441 | 26.9921 | 89.27% | 284.4362 | 267.37 | 6416.8799
1976 | 10 | 22 | 1121.9592 | 15 | 1106.9592 | 27.7561 | 139.3858 | 0.77441 | 26.9817 | 89.27% | 284.3261 | 267.2665 | 6414.3958
1976 | 10 | 23 | 530.2857 | 15 | 515.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
1976 | 10 | 24 | 339.5918 | 15 | 324.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1976 | 10 | 25 | 308.2449 | 15 | 293.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1976 | 10 | 26 | 322.6122 | 15 | 307.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1976 | 10 | 27 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1976 | 10 | 28 | 231.1837 | 15 | 216.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1976 | 10 | 29 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1976 | 10 | 30 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1976 | 10 | 31 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1976 | 11 | 1 | 286.0408 | 15 | 271.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1976 | 11 | 2 | 225.9592 | 15 | 210.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1976 | 11 | 3 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1976 | 11 | 4 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1976 | 11 | 5 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1976 | 11 | 6 | 436.2449 | 15 | 421.2449 | 29.1275 | 139.3858 | 0.77441 | 28.3531 | 89.27% | 298.7778 | 280.8512 | 6740.4278
1976 | 11 | 7 | 394.449 | 15 | 379.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1976 | 11 | 8 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1976 | 11 | 9 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1976 | 11 | 10 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1976 | 11 | 11 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1976 | 11 | 12 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1976 | 11 | 13 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1976 | 11 | 14 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1976 | 11 | 15 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1976 | 11 | 16 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1976 | 11 | 17 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1976 | 11 | 18 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1976 | 11 | 19 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1976 | 11 | 20 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1976 | 11 | 21 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1976 | 11 | 22 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1976 | 11 | 23 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1976 | 11 | 24 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1976 | 11 | 25 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1976 | 11 | 26 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1976 | 11 | 27 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1976 | 11 | 28 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1976 | 11 | 29 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1976 | 11 | 30 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1976 | 12 | 1 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1976 | 12 | 2 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1976 | 12 | 3 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1976 | 12 | 4 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1976 | 12 | 5 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1976 | 12 | 6 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1976 | 12 | 7 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1976 | 12 | 8 | 851.5918 | 5 | 846.5918 | 28.2968 | 139.3858 | 0.77441 | 27.5224 | 89.27% | 290.0242 | 272.6227 | 6542.9456
1976 | 12 | 9 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1976 | 12 | 10 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1976 | 12 | 11 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1976 | 12 | 12 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1976 | 12 | 13 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1976 | 12 | 14 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1976 | 12 | 15 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1976 | 12 | 16 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1976 | 12 | 17 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1976 | 12 | 18 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1976 | 12 | 19 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1976 | 12 | 20 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1976 | 12 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1976 | 12 | 22 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1976 | 12 | 23 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1976 | 12 | 24 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1976 | 12 | 25 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1976 | 12 | 26 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1976 | 12 | 27 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1976 | 12 | 28 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1976 | 12 | 29 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1976 | 12 | 30 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1976 | 12 | 31 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1977 | 1 | 1 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1977 | 1 | 2 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1977 | 1 | 3 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1977 | 1 | 4 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1977 | 1 | 5 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1977 | 1 | 6 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1977 | 1 | 7 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1977 | 1 | 8 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1977 | 1 | 9 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1977 | 1 | 10 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1977 | 1 | 11 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1977 | 1 | 12 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1977 | 1 | 13 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1977 | 1 | 14 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1977 | 1 | 15 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1977 | 1 | 16 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1977 | 1 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1977 | 1 | 18 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1977 | 1 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1977 | 1 | 20 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1977 | 1 | 21 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1977 | 1 | 22 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1977 | 1 | 23 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1977 | 1 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1977 | 1 | 25 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1977 | 1 | 26 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1977 | 1 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1977 | 1 | 28 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1977 | 1 | 29 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1977 | 1 | 30 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1977 | 1 | 31 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1977 | 2 | 1 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1977 | 2 | 2 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1977 | 2 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1977 | 2 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1977 | 2 | 5 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1977 | 2 | 6 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1977 | 2 | 7 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1977 | 2 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1977 | 2 | 9 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1977 | 2 | 10 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1977 | 2 | 11 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1977 | 2 | 12 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1977 | 2 | 13 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1977 | 2 | 14 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1977 | 2 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1977 | 2 | 16 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1977 | 2 | 17 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1977 | 2 | 18 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1977 | 2 | 19 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1977 | 2 | 20 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1977 | 2 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1977 | 2 | 22 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1977 | 2 | 23 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1977 | 2 | 24 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1977 | 2 | 25 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1977 | 2 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1977 | 2 | 27 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1977 | 2 | 28 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1977 | 3 | 1 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1977 | 3 | 2 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1977 | 3 | 3 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1977 | 3 | 4 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1977 | 3 | 5 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1977 | 3 | 6 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1977 | 3 | 7 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1977 | 3 | 8 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1977 | 3 | 9 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1977 | 3 | 10 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1977 | 3 | 11 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1977 | 3 | 12 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1977 | 3 | 13 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1977 | 3 | 14 | 2063.6735 | 25 | 2038.6735 | 25.8727 | 139.3858 | 0.77441 | 25.0982 | 89.27% | 264.479 | 248.6102 | 5966.6454
1977 | 3 | 15 | 2977.9592 | 25 | 2952.9592 | 24.0441 | 0 | 0 | 24.0441 | 0% | 0 | 0 | 0
1977 | 3 | 16 | 1711.0204 | 25 | 1686.0204 | 26.578 | 139.3858 | 0.77441 | 25.8035 | 89.27% | 271.9113 | 255.5966 | 6134.3189
1977 | 3 | 17 | 1167.6735 | 25 | 1142.6735 | 27.6647 | 139.3858 | 0.77441 | 26.8902 | 89.27% | 283.3626 | 266.3608 | 6392.6604
1977 | 3 | 18 | 824.1633 | 25 | 799.1633 | 28.3517 | 139.3858 | 0.77441 | 27.5773 | 89.27% | 290.6023 | 273.1661 | 6555.9868
1977 | 3 | 19 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1977 | 3 | 20 | 504.1633 | 25 | 479.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
1977 | 3 | 21 | 420.5714 | 25 | 395.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1977 | 3 | 22 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1977 | 3 | 23 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1977 | 3 | 24 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1977 | 3 | 25 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1977 | 3 | 26 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1977 | 3 | 27 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1977 | 3 | 28 | 380.0816 | 25 | 355.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1977 | 3 | 29 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1977 | 3 | 30 | 970.449 | 25 | 945.449 | 28.0591 | 139.3858 | 0.77441 | 27.2847 | 89.27% | 287.5192 | 270.2681 | 6486.4334
1977 | 3 | 31 | 1619.5918 | 25 | 1594.5918 | 26.7608 | 139.3858 | 0.77441 | 25.9864 | 89.27% | 273.8382 | 257.4079 | 6177.7898
1977 | 4 | 1 | 1488.9796 | 25 | 1463.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1977 | 4 | 2 | 879.0204 | 25 | 854.0204 | 28.242 | 139.3858 | 0.77441 | 27.4675 | 89.27% | 289.4461 | 272.0793 | 6529.9043
1977 | 4 | 3 | 1060.5714 | 25 | 1035.5714 | 27.8789 | 139.3858 | 0.77441 | 27.1044 | 89.27% | 285.6198 | 268.4826 | 6443.5835
1977 | 4 | 4 | 1107.5918 | 25 | 1082.5918 | 27.7848 | 139.3858 | 0.77441 | 27.0104 | 89.27% | 284.6289 | 267.5511 | 6421.227
1977 | 4 | 5 | 768 | 25 | 743 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
1977 | 4 | 6 | 662.2041 | 25 | 637.2041 | 28.6756 | 139.3858 | 0.77441 | 27.9012 | 89.27% | 294.0156 | 276.3747 | 6632.9925
1977 | 4 | 7 | 573.3878 | 25 | 548.3878 | 28.8532 | 139.3858 | 0.77441 | 28.0788 | 89.27% | 295.8875 | 278.1342 | 6675.2214
1977 | 4 | 8 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1977 | 4 | 9 | 361.7959 | 25 | 336.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1977 | 4 | 10 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1977 | 4 | 11 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1977 | 4 | 12 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1977 | 4 | 13 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1977 | 4 | 14 | 828.0816 | 25 | 803.0816 | 28.3438 | 139.3858 | 0.77441 | 27.5694 | 89.27% | 290.5197 | 273.0885 | 6554.1238
1977 | 4 | 15 | 679.1837 | 25 | 654.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
1977 | 4 | 16 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1977 | 4 | 17 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1977 | 4 | 18 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1977 | 4 | 19 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1977 | 4 | 20 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1977 | 4 | 21 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1977 | 4 | 22 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1977 | 4 | 23 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1977 | 4 | 24 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1977 | 4 | 25 | 843.7551 | 25 | 818.7551 | 28.3125 | 139.3858 | 0.77441 | 27.5381 | 89.27% | 290.1893 | 272.778 | 6546.6716
1977 | 4 | 26 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
1977 | 4 | 27 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
1977 | 4 | 28 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1977 | 4 | 29 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1977 | 4 | 30 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1977 | 5 | 1 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1977 | 5 | 2 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1977 | 5 | 3 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1977 | 5 | 4 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1977 | 5 | 5 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1977 | 5 | 6 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1977 | 5 | 7 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1977 | 5 | 8 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1977 | 5 | 9 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1977 | 5 | 10 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1977 | 5 | 11 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1977 | 5 | 12 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1977 | 5 | 13 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1977 | 5 | 14 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1977 | 5 | 15 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1977 | 5 | 16 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1977 | 5 | 17 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1977 | 5 | 18 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1977 | 5 | 19 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1977 | 5 | 20 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1977 | 5 | 21 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1977 | 5 | 22 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1977 | 5 | 23 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1977 | 5 | 24 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1977 | 5 | 25 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1977 | 5 | 26 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1977 | 5 | 27 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1977 | 5 | 28 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1977 | 5 | 29 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1977 | 5 | 30 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1977 | 5 | 31 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1977 | 6 | 1 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1977 | 6 | 2 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1977 | 6 | 3 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1977 | 6 | 4 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1977 | 6 | 5 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1977 | 6 | 6 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1977 | 6 | 7 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1977 | 6 | 8 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1977 | 6 | 9 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1977 | 6 | 10 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1977 | 6 | 11 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1977 | 6 | 12 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1977 | 6 | 13 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1977 | 6 | 14 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1977 | 6 | 15 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1977 | 6 | 16 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1977 | 6 | 17 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1977 | 6 | 18 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1977 | 6 | 19 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1977 | 6 | 20 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1977 | 6 | 21 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1977 | 6 | 22 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1977 | 6 | 23 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1977 | 6 | 24 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1977 | 6 | 25 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1977 | 6 | 26 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1977 | 6 | 27 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1977 | 6 | 28 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1977 | 6 | 29 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1977 | 6 | 30 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1977 | 7 | 1 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1977 | 7 | 2 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1977 | 7 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1977 | 7 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1977 | 7 | 5 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1977 | 7 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1977 | 7 | 7 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1977 | 7 | 8 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1977 | 7 | 9 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1977 | 7 | 10 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1977 | 7 | 11 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1977 | 7 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1977 | 7 | 13 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1977 | 7 | 14 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1977 | 7 | 15 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1977 | 7 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1977 | 7 | 17 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1977 | 7 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1977 | 7 | 19 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1977 | 7 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1977 | 7 | 21 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1977 | 7 | 22 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1977 | 7 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1977 | 7 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1977 | 7 | 25 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1977 | 7 | 26 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1977 | 7 | 27 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1977 | 7 | 28 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1977 | 7 | 29 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1977 | 7 | 30 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1977 | 7 | 31 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1977 | 8 | 1 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1977 | 8 | 2 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1977 | 8 | 3 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1977 | 8 | 4 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1977 | 8 | 5 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1977 | 8 | 6 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1977 | 8 | 7 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1977 | 8 | 8 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1977 | 8 | 9 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1977 | 8 | 10 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1977 | 8 | 11 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1977 | 8 | 12 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1977 | 8 | 13 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1977 | 8 | 14 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1977 | 8 | 15 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1977 | 8 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1977 | 8 | 17 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1977 | 8 | 18 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1977 | 8 | 19 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1977 | 8 | 20 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1977 | 8 | 21 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1977 | 8 | 22 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1977 | 8 | 23 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1977 | 8 | 24 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1977 | 8 | 25 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1977 | 8 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1977 | 8 | 27 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1977 | 8 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1977 | 8 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1977 | 8 | 30 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1977 | 8 | 31 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1977 | 9 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1977 | 9 | 2 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1977 | 9 | 3 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1977 | 9 | 4 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1977 | 9 | 5 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1977 | 9 | 6 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1977 | 9 | 7 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1977 | 9 | 8 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1977 | 9 | 9 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1977 | 9 | 10 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1977 | 9 | 11 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1977 | 9 | 12 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1977 | 9 | 13 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1977 | 9 | 14 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1977 | 9 | 15 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1977 | 9 | 16 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1977 | 9 | 17 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1977 | 9 | 18 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1977 | 9 | 19 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1977 | 9 | 20 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1977 | 9 | 21 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1977 | 9 | 22 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1977 | 9 | 23 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1977 | 9 | 24 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1977 | 9 | 25 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1977 | 9 | 26 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1977 | 9 | 27 | 1010.9388 | 15 | 995.9388 | 27.9781 | 139.3858 | 0.77441 | 27.2037 | 89.27% | 286.6659 | 269.4659 | 6467.182
1977 | 9 | 28 | 489.7959 | 15 | 474.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
1977 | 9 | 29 | 336.9796 | 15 | 321.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1977 | 9 | 30 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1977 | 10 | 1 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1977 | 10 | 2 | 1697.9592 | 15 | 1682.9592 | 26.6041 | 139.3858 | 0.77441 | 25.8297 | 89.27% | 272.1866 | 255.8554 | 6140.529
1977 | 10 | 3 | 884.2449 | 15 | 869.2449 | 28.2315 | 139.3858 | 0.77441 | 27.4571 | 89.27% | 289.336 | 271.9758 | 6527.4202
1977 | 10 | 4 | 489.7959 | 15 | 474.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
1977 | 10 | 5 | 329.1429 | 15 | 314.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1977 | 10 | 6 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1977 | 10 | 7 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1977 | 10 | 8 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1977 | 10 | 9 | 668.7347 | 15 | 653.7347 | 28.6625 | 139.3858 | 0.77441 | 27.8881 | 89.27% | 293.878 | 276.2453 | 6629.8874
1977 | 10 | 10 | 2246.5306 | 15 | 2231.5306 | 25.5069 | 139.3858 | 0.77441 | 24.7325 | 89.27% | 260.6252 | 244.9876 | 5879.7035
1977 | 10 | 11 | 882.9388 | 15 | 867.9388 | 28.2341 | 139.3858 | 0.77441 | 27.4597 | 89.27% | 289.3635 | 272.0017 | 6528.0413
1977 | 10 | 12 | 536.8163 | 15 | 521.8163 | 28.9264 | 139.3858 | 0.77441 | 28.152 | 89.27% | 296.6582 | 278.8587 | 6692.6097
1977 | 10 | 13 | 382.6939 | 15 | 367.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
1977 | 10 | 14 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1977 | 10 | 15 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1977 | 10 | 16 | 322.6122 | 15 | 307.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1977 | 10 | 17 | 1345.3061 | 15 | 1330.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
1977 | 10 | 18 | 1502.0408 | 15 | 1487.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1977 | 10 | 19 | 726.2041 | 15 | 711.2041 | 28.5476 | 139.3858 | 0.77441 | 27.7732 | 89.27% | 292.6668 | 275.1068 | 6602.5628
1977 | 10 | 20 | 1004.4082 | 15 | 989.4082 | 27.9912 | 139.3858 | 0.77441 | 27.2168 | 89.27% | 286.8035 | 269.5953 | 6470.287
1977 | 10 | 21 | 975.6735 | 15 | 960.6735 | 28.0487 | 139.3858 | 0.77441 | 27.2742 | 89.27% | 287.4091 | 270.1646 | 6483.9493
1977 | 10 | 22 | 632.1633 | 15 | 617.1633 | 28.7357 | 139.3858 | 0.77441 | 27.9613 | 89.27% | 294.6487 | 276.9698 | 6647.2758
1977 | 10 | 23 | 457.1429 | 15 | 442.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1977 | 10 | 24 | 360.4898 | 15 | 345.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1977 | 10 | 25 | 303.0204 | 15 | 288.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1977 | 10 | 26 | 270.3673 | 15 | 255.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1977 | 10 | 27 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1977 | 10 | 28 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1977 | 10 | 29 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1977 | 10 | 30 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1977 | 10 | 31 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1977 | 11 | 1 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1977 | 11 | 2 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1977 | 11 | 3 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1977 | 11 | 4 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1977 | 11 | 5 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1977 | 11 | 6 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1977 | 11 | 7 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1977 | 11 | 8 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1977 | 11 | 9 | 508.0816 | 15 | 493.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
1977 | 11 | 10 | 479.3469 | 15 | 464.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1977 | 11 | 11 | 476.7347 | 15 | 461.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
1977 | 11 | 12 | 408.8163 | 15 | 393.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
1977 | 11 | 13 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1977 | 11 | 14 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1977 | 11 | 15 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1977 | 11 | 16 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1977 | 11 | 17 | 194.6122 | 15 | 179.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1977 | 11 | 18 | 297.7959 | 15 | 282.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1977 | 11 | 19 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1977 | 11 | 20 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1977 | 11 | 21 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1977 | 11 | 22 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1977 | 11 | 23 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1977 | 11 | 24 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1977 | 11 | 25 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1977 | 11 | 26 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1977 | 11 | 27 | 254.6939 | 15 | 239.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1977 | 11 | 28 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1977 | 11 | 29 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1977 | 11 | 30 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1977 | 12 | 1 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1977 | 12 | 2 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1977 | 12 | 3 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1977 | 12 | 4 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1977 | 12 | 5 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1977 | 12 | 6 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1977 | 12 | 7 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1977 | 12 | 8 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1977 | 12 | 9 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1977 | 12 | 10 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1977 | 12 | 11 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1977 | 12 | 12 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1977 | 12 | 13 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1977 | 12 | 14 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1977 | 12 | 15 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1977 | 12 | 16 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1977 | 12 | 17 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1977 | 12 | 18 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1977 | 12 | 19 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1977 | 12 | 20 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1977 | 12 | 21 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1977 | 12 | 22 | 330.449 | 5 | 325.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1977 | 12 | 23 | 316.0816 | 5 | 311.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1977 | 12 | 24 | 259.9184 | 5 | 254.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1977 | 12 | 25 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1977 | 12 | 26 | 455.8367 | 5 | 450.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1977 | 12 | 27 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1977 | 12 | 28 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1977 | 12 | 29 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1977 | 12 | 30 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1977 | 12 | 31 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1978 | 1 | 1 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1978 | 1 | 2 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1978 | 1 | 3 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1978 | 1 | 4 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1978 | 1 | 5 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1978 | 1 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1978 | 1 | 7 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1978 | 1 | 8 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1978 | 1 | 9 | 1055.3469 | 5 | 1050.3469 | 27.8893 | 139.3858 | 0.77441 | 27.1149 | 89.27% | 285.7299 | 268.5861 | 6446.0675
1978 | 1 | 10 | 2377.1429 | 5 | 2372.1429 | 25.2457 | 139.3858 | 0.77441 | 24.4713 | 89.27% | 257.8724 | 242.4001 | 5817.6022
1978 | 1 | 11 | 1116.7347 | 5 | 1111.7347 | 27.7665 | 139.3858 | 0.77441 | 26.9921 | 89.27% | 284.4362 | 267.37 | 6416.8799
1978 | 1 | 12 | 690.9388 | 5 | 685.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
1978 | 1 | 13 | 509.3878 | 5 | 504.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1978 | 1 | 14 | 378.7755 | 5 | 373.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1978 | 1 | 15 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1978 | 1 | 16 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1978 | 1 | 17 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1978 | 1 | 18 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1978 | 1 | 19 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1978 | 1 | 20 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1978 | 1 | 21 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1978 | 1 | 22 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1978 | 1 | 23 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1978 | 1 | 24 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1978 | 1 | 25 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1978 | 1 | 26 | 399.6735 | 5 | 394.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1978 | 1 | 27 | 790.2041 | 5 | 785.2041 | 28.4196 | 139.3858 | 0.77441 | 27.6452 | 89.27% | 291.318 | 273.8389 | 6572.1332
1978 | 1 | 28 | 592.9796 | 5 | 587.9796 | 28.814 | 139.3858 | 0.77441 | 28.0396 | 89.27% | 295.4746 | 277.7461 | 6665.9062
1978 | 1 | 29 | 412.7347 | 5 | 407.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1978 | 1 | 30 | 342.2041 | 5 | 337.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1978 | 1 | 31 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1978 | 2 | 1 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1978 | 2 | 2 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1978 | 2 | 3 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1978 | 2 | 4 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1978 | 2 | 5 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1978 | 2 | 6 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1978 | 2 | 7 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1978 | 2 | 8 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1978 | 2 | 9 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1978 | 2 | 10 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1978 | 2 | 11 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1978 | 2 | 12 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1978 | 2 | 13 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1978 | 2 | 14 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1978 | 2 | 15 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1978 | 2 | 16 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1978 | 2 | 17 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1978 | 2 | 18 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1978 | 2 | 19 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1978 | 2 | 20 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1978 | 2 | 21 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1978 | 2 | 22 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1978 | 2 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1978 | 2 | 24 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1978 | 2 | 25 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1978 | 2 | 26 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1978 | 2 | 27 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1978 | 2 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1978 | 3 | 1 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1978 | 3 | 2 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1978 | 3 | 3 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1978 | 3 | 4 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1978 | 3 | 5 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1978 | 3 | 6 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1978 | 3 | 7 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1978 | 3 | 8 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1978 | 3 | 9 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1978 | 3 | 10 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1978 | 3 | 11 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1978 | 3 | 12 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1978 | 3 | 13 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1978 | 3 | 14 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1978 | 3 | 15 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1978 | 3 | 16 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1978 | 3 | 17 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1978 | 3 | 18 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1978 | 3 | 19 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1978 | 3 | 20 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1978 | 3 | 21 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1978 | 3 | 22 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1978 | 3 | 23 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1978 | 3 | 24 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
1978 | 3 | 25 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1978 | 3 | 26 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1978 | 3 | 27 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1978 | 3 | 28 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1978 | 3 | 29 | 467.5918 | 25 | 442.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1978 | 3 | 30 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1978 | 3 | 31 | 361.7959 | 25 | 336.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1978 | 4 | 1 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1978 | 4 | 2 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1978 | 4 | 3 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1978 | 4 | 4 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1978 | 4 | 5 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1978 | 4 | 6 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1978 | 4 | 7 | 348.7347 | 25 | 323.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1978 | 4 | 8 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1978 | 4 | 9 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1978 | 4 | 10 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1978 | 4 | 11 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1978 | 4 | 12 | 809.7959 | 25 | 784.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
1978 | 4 | 13 | 796.7347 | 25 | 771.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1978 | 4 | 14 | 724.898 | 25 | 699.898 | 28.5502 | 139.3858 | 0.77441 | 27.7758 | 89.27% | 292.6943 | 275.1327 | 6603.1838
1978 | 4 | 15 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
1978 | 4 | 16 | 783.6735 | 25 | 758.6735 | 28.4327 | 139.3858 | 0.77441 | 27.6582 | 89.27% | 291.4556 | 273.9683 | 6575.2383
1978 | 4 | 17 | 698.7755 | 25 | 673.7755 | 28.6024 | 139.3858 | 0.77441 | 27.828 | 89.27% | 293.2449 | 275.6502 | 6615.6041
1978 | 4 | 18 | 744.4898 | 25 | 719.4898 | 28.511 | 139.3858 | 0.77441 | 27.7366 | 89.27% | 292.2814 | 274.7445 | 6593.8686
1978 | 4 | 19 | 880.3265 | 25 | 855.3265 | 28.2393 | 139.3858 | 0.77441 | 27.4649 | 89.27% | 289.4186 | 272.0535 | 6529.2833
1978 | 4 | 20 | 1072.3265 | 25 | 1047.3265 | 27.8553 | 139.3858 | 0.77441 | 27.0809 | 89.27% | 285.3721 | 268.2498 | 6437.9943
1978 | 4 | 21 | 1632.6531 | 25 | 1607.6531 | 26.7347 | 139.3858 | 0.77441 | 25.9603 | 89.27% | 273.5629 | 257.1492 | 6171.5797
1978 | 4 | 22 | 1475.9184 | 25 | 1450.9184 | 27.0482 | 139.3858 | 0.77441 | 26.2738 | 89.27% | 276.8662 | 260.2542 | 6246.1013
1978 | 4 | 23 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
1978 | 4 | 24 | 1102.3673 | 25 | 1077.3673 | 27.7953 | 139.3858 | 0.77441 | 27.0209 | 89.27% | 284.739 | 267.6546 | 6423.711
1978 | 4 | 25 | 953.4694 | 25 | 928.4694 | 28.0931 | 139.3858 | 0.77441 | 27.3187 | 89.27% | 287.8771 | 270.6044 | 6494.5065
1978 | 4 | 26 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1978 | 4 | 27 | 1022.6939 | 25 | 997.6939 | 27.9546 | 139.3858 | 0.77441 | 27.1802 | 89.27% | 286.4181 | 269.233 | 6461.5928
1978 | 4 | 28 | 976.9796 | 25 | 951.9796 | 28.046 | 139.3858 | 0.77441 | 27.2716 | 89.27% | 287.3816 | 270.1387 | 6483.3283
1978 | 4 | 29 | 876.4082 | 25 | 851.4082 | 28.2472 | 139.3858 | 0.77441 | 27.4728 | 89.27% | 289.5012 | 272.1311 | 6531.1463
1978 | 4 | 30 | 796.7347 | 25 | 771.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1978 | 5 | 1 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1978 | 5 | 2 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1978 | 5 | 3 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
1978 | 5 | 4 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1978 | 5 | 5 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1978 | 5 | 6 | 356.5714 | 25 | 331.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1978 | 5 | 7 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1978 | 5 | 8 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1978 | 5 | 9 | 384 | 25 | 359 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
1978 | 5 | 10 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1978 | 5 | 11 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1978 | 5 | 12 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1978 | 5 | 13 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1978 | 5 | 14 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1978 | 5 | 15 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1978 | 5 | 16 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1978 | 5 | 17 | 783.6735 | 25 | 758.6735 | 28.4327 | 139.3858 | 0.77441 | 27.6582 | 89.27% | 291.4556 | 273.9683 | 6575.2383
1978 | 5 | 18 | 688.3265 | 25 | 663.3265 | 28.6233 | 139.3858 | 0.77441 | 27.8489 | 89.27% | 293.4651 | 275.8572 | 6620.5722
1978 | 5 | 19 | 462.3673 | 25 | 437.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
1978 | 5 | 20 | 356.5714 | 25 | 331.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1978 | 5 | 21 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1978 | 5 | 22 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1978 | 5 | 23 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1978 | 5 | 24 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1978 | 5 | 25 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1978 | 5 | 26 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1978 | 5 | 27 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1978 | 5 | 28 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1978 | 5 | 29 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1978 | 5 | 30 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1978 | 5 | 31 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1978 | 6 | 1 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1978 | 6 | 2 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1978 | 6 | 3 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1978 | 6 | 4 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1978 | 6 | 5 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1978 | 6 | 6 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1978 | 6 | 7 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1978 | 6 | 8 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1978 | 6 | 9 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1978 | 6 | 10 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1978 | 6 | 11 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1978 | 6 | 12 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1978 | 6 | 13 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1978 | 6 | 14 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1978 | 6 | 15 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1978 | 6 | 16 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1978 | 6 | 17 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1978 | 6 | 18 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1978 | 6 | 19 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1978 | 6 | 20 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1978 | 6 | 21 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1978 | 6 | 22 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1978 | 6 | 23 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1978 | 6 | 24 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1978 | 6 | 25 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1978 | 6 | 26 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1978 | 6 | 27 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1978 | 6 | 28 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1978 | 6 | 29 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1978 | 6 | 30 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1978 | 7 | 1 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1978 | 7 | 2 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1978 | 7 | 3 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1978 | 7 | 4 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1978 | 7 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1978 | 7 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1978 | 7 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 7 | 8 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 7 | 9 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 7 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 7 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 7 | 12 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 7 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1978 | 7 | 14 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1978 | 7 | 15 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1978 | 7 | 16 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 7 | 17 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1978 | 7 | 18 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 7 | 19 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 7 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1978 | 7 | 21 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1978 | 7 | 22 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1978 | 7 | 23 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1978 | 7 | 24 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1978 | 7 | 25 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1978 | 7 | 26 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1978 | 7 | 27 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1978 | 7 | 28 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1978 | 7 | 29 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1978 | 7 | 30 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1978 | 7 | 31 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1978 | 8 | 1 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1978 | 8 | 2 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1978 | 8 | 3 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1978 | 8 | 4 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1978 | 8 | 5 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1978 | 8 | 6 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1978 | 8 | 7 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1978 | 8 | 8 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1978 | 8 | 9 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1978 | 8 | 10 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1978 | 8 | 11 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
1978 | 8 | 12 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1978 | 8 | 13 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1978 | 8 | 14 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1978 | 8 | 15 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1978 | 8 | 16 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1978 | 8 | 17 | 6.1388 | 5 | 1.1388 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1978 | 8 | 18 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1978 | 8 | 19 | 4.8327 | 5 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1978 | 8 | 20 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1978 | 8 | 21 | 3.6571 | 5 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
1978 | 8 | 22 | 3.2653 | 5 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1978 | 8 | 23 | 2.8735 | 5 | 0 | 29.9943 | 0 | 0 | 29.9943 | 0% | 0 | 0 | 0
1978 | 8 | 24 | 3.0041 | 5 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1978 | 8 | 25 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1978 | 8 | 26 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1978 | 8 | 27 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1978 | 8 | 28 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1978 | 8 | 29 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1978 | 8 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1978 | 8 | 31 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1978 | 9 | 1 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1978 | 9 | 2 | 5.0939 | 15 | 0 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1978 | 9 | 3 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1978 | 9 | 4 | 3.7878 | 15 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1978 | 9 | 5 | 3.3959 | 15 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
1978 | 9 | 6 | 3.1347 | 15 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
1978 | 9 | 7 | 3.0041 | 15 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1978 | 9 | 8 | 3.5265 | 15 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1978 | 9 | 9 | 4.5714 | 15 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1978 | 9 | 10 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1978 | 9 | 11 | 3.5265 | 15 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1978 | 9 | 12 | 3.2653 | 15 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1978 | 9 | 13 | 3.6571 | 15 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
1978 | 9 | 14 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1978 | 9 | 15 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1978 | 9 | 16 | 4.5714 | 15 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1978 | 9 | 17 | 3.9184 | 15 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
1978 | 9 | 18 | 3.5265 | 15 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1978 | 9 | 19 | 3.2653 | 15 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
1978 | 9 | 20 | 3.0041 | 15 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1978 | 9 | 21 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
1978 | 9 | 22 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
1978 | 9 | 23 | 2.4816 | 15 | 0 | 29.995 | 0 | 0 | 29.995 | 0% | 0 | 0 | 0
1978 | 9 | 24 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
1978 | 9 | 25 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
1978 | 9 | 26 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
1978 | 9 | 27 | 2.2204 | 15 | 0 | 29.9956 | 0 | 0 | 29.9956 | 0% | 0 | 0 | 0
1978 | 9 | 28 | 1.9592 | 15 | 0 | 29.9961 | 0 | 0 | 29.9961 | 0% | 0 | 0 | 0
1978 | 9 | 29 | 1.9592 | 15 | 0 | 29.9961 | 0 | 0 | 29.9961 | 0% | 0 | 0 | 0
1978 | 9 | 30 | 1.8286 | 15 | 0 | 29.9963 | 0 | 0 | 29.9963 | 0% | 0 | 0 | 0
1978 | 10 | 1 | 1.9592 | 15 | 0 | 29.9961 | 0 | 0 | 29.9961 | 0% | 0 | 0 | 0
1978 | 10 | 2 | 5.8776 | 15 | 0 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1978 | 10 | 3 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1978 | 10 | 4 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1978 | 10 | 5 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1978 | 10 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1978 | 10 | 7 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1978 | 10 | 8 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 10 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1978 | 10 | 10 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1978 | 10 | 11 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1978 | 10 | 12 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1978 | 10 | 13 | 9.7959 | 15 | 0 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1978 | 10 | 14 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1978 | 10 | 15 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1978 | 10 | 16 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1978 | 10 | 17 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1978 | 10 | 18 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1978 | 10 | 19 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1978 | 10 | 20 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1978 | 10 | 21 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1978 | 10 | 22 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1978 | 10 | 23 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 10 | 24 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1978 | 10 | 25 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1978 | 10 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1978 | 10 | 27 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1978 | 10 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1978 | 10 | 29 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 10 | 30 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1978 | 10 | 31 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1978 | 11 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1978 | 11 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1978 | 11 | 3 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1978 | 11 | 4 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 5 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 6 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1978 | 11 | 7 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1978 | 11 | 8 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 10 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 11 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 12 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1978 | 11 | 13 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1978 | 11 | 14 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1978 | 11 | 15 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1978 | 11 | 16 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1978 | 11 | 17 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1978 | 11 | 18 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1978 | 11 | 19 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1978 | 11 | 20 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1978 | 11 | 21 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1978 | 11 | 22 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1978 | 11 | 23 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1978 | 11 | 24 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1978 | 11 | 25 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 11 | 26 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 11 | 27 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1978 | 11 | 28 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 11 | 29 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1978 | 11 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1978 | 12 | 1 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 2 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 3 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 4 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 5 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 12 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 12 | 7 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 12 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1978 | 12 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1978 | 12 | 11 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1978 | 12 | 12 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1978 | 12 | 13 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1978 | 12 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 12 | 15 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 12 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 12 | 18 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 12 | 19 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1978 | 12 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1978 | 12 | 21 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 22 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1978 | 12 | 23 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1978 | 12 | 24 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1978 | 12 | 25 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1978 | 12 | 26 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1978 | 12 | 27 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1978 | 12 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1978 | 12 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1978 | 12 | 31 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1979 | 1 | 1 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 1 | 2 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1979 | 1 | 3 | 417.9592 | 5 | 412.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1979 | 1 | 4 | 342.2041 | 5 | 337.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1979 | 1 | 5 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1979 | 1 | 6 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1979 | 1 | 7 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1979 | 1 | 8 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1979 | 1 | 9 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1979 | 1 | 10 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1979 | 1 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1979 | 1 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1979 | 1 | 13 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1979 | 1 | 14 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1979 | 1 | 15 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1979 | 1 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1979 | 1 | 17 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1979 | 1 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1979 | 1 | 19 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1979 | 1 | 20 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1979 | 1 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1979 | 1 | 22 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1979 | 1 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1979 | 1 | 24 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1979 | 1 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1979 | 1 | 26 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1979 | 1 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1979 | 1 | 28 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1979 | 1 | 29 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1979 | 1 | 30 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1979 | 1 | 31 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1979 | 2 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1979 | 2 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1979 | 2 | 3 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1979 | 2 | 4 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1979 | 2 | 5 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1979 | 2 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1979 | 2 | 7 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1979 | 2 | 8 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1979 | 2 | 9 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1979 | 2 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1979 | 2 | 11 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1979 | 2 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1979 | 2 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1979 | 2 | 14 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1979 | 2 | 15 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1979 | 2 | 16 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1979 | 2 | 17 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1979 | 2 | 18 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1979 | 2 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1979 | 2 | 20 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1979 | 2 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1979 | 2 | 22 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1979 | 2 | 23 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1979 | 2 | 24 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1979 | 2 | 25 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1979 | 2 | 26 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1979 | 2 | 27 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1979 | 2 | 28 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1979 | 3 | 1 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1979 | 3 | 2 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1979 | 3 | 3 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1979 | 3 | 4 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1979 | 3 | 5 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1979 | 3 | 6 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1979 | 3 | 7 | 946.9388 | 25 | 921.9388 | 28.1061 | 139.3858 | 0.77441 | 27.3317 | 89.27% | 288.0147 | 270.7338 | 6497.6116
1979 | 3 | 8 | 1208.1633 | 25 | 1183.1633 | 27.5837 | 139.3858 | 0.77441 | 26.8093 | 89.27% | 282.5093 | 265.5587 | 6373.409
1979 | 3 | 9 | 944.3265 | 25 | 919.3265 | 28.1113 | 139.3858 | 0.77441 | 27.3369 | 89.27% | 288.0698 | 270.7856 | 6498.8536
1979 | 3 | 10 | 698.7755 | 25 | 673.7755 | 28.6024 | 139.3858 | 0.77441 | 27.828 | 89.27% | 293.2449 | 275.6502 | 6615.6041
1979 | 3 | 11 | 598.2041 | 25 | 573.2041 | 28.8036 | 139.3858 | 0.77441 | 28.0292 | 89.27% | 295.3645 | 277.6426 | 6663.4221
1979 | 3 | 12 | 528.9796 | 25 | 503.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1979 | 3 | 13 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1979 | 3 | 14 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1979 | 3 | 15 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1979 | 3 | 16 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1979 | 3 | 17 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1979 | 3 | 18 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1979 | 3 | 19 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1979 | 3 | 20 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1979 | 3 | 21 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1979 | 3 | 22 | 616.4898 | 25 | 591.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
1979 | 3 | 23 | 966.5306 | 25 | 941.5306 | 28.0669 | 139.3858 | 0.77441 | 27.2925 | 89.27% | 287.6018 | 270.3457 | 6488.2964
1979 | 3 | 24 | 1253.8776 | 25 | 1228.8776 | 27.4922 | 139.3858 | 0.77441 | 26.7178 | 89.27% | 281.5458 | 264.6531 | 6351.6735
1979 | 3 | 25 | 2390.2041 | 25 | 2365.2041 | 25.2196 | 139.3858 | 0.77441 | 24.4452 | 89.27% | 257.5972 | 242.1413 | 5811.3921
1979 | 3 | 26 | 2390.2041 | 25 | 2365.2041 | 25.2196 | 139.3858 | 0.77441 | 24.4452 | 89.27% | 257.5972 | 242.1413 | 5811.3921
1979 | 3 | 27 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
1979 | 3 | 28 | 799.3469 | 25 | 774.3469 | 28.4013 | 139.3858 | 0.77441 | 27.6269 | 89.27% | 291.1253 | 273.6578 | 6567.7861
1979 | 3 | 29 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
1979 | 3 | 30 | 485.8776 | 25 | 460.8776 | 29.0282 | 139.3858 | 0.77441 | 28.2538 | 89.27% | 297.7318 | 279.8679 | 6716.8293
1979 | 3 | 31 | 654.3673 | 25 | 629.3673 | 28.6913 | 139.3858 | 0.77441 | 27.9169 | 89.27% | 294.1808 | 276.5299 | 6636.7186
1979 | 4 | 1 | 683.102 | 25 | 658.102 | 28.6338 | 139.3858 | 0.77441 | 27.8594 | 89.27% | 293.5752 | 275.9607 | 6623.0563
1979 | 4 | 2 | 687.0204 | 25 | 662.0204 | 28.626 | 139.3858 | 0.77441 | 27.8515 | 89.27% | 293.4926 | 275.8831 | 6621.1932
1979 | 4 | 3 | 603.4286 | 25 | 578.4286 | 28.7931 | 139.3858 | 0.77441 | 28.0187 | 89.27% | 295.2543 | 277.5391 | 6660.9381
1979 | 4 | 4 | 594.2857 | 25 | 569.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
1979 | 4 | 5 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
1979 | 4 | 6 | 531.5918 | 25 | 506.5918 | 28.9368 | 139.3858 | 0.77441 | 28.1624 | 89.27% | 296.7683 | 278.9622 | 6695.0938
1979 | 4 | 7 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1979 | 4 | 8 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1979 | 4 | 9 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1979 | 4 | 10 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
1979 | 4 | 11 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
1979 | 4 | 12 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1979 | 4 | 13 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
1979 | 4 | 14 | 594.2857 | 25 | 569.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
1979 | 4 | 15 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
1979 | 4 | 16 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1979 | 4 | 17 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1979 | 4 | 18 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
1979 | 4 | 19 | 535.5102 | 25 | 510.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1979 | 4 | 20 | 544.6531 | 25 | 519.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
1979 | 4 | 21 | 589.0612 | 25 | 564.0612 | 28.8219 | 139.3858 | 0.77441 | 28.0475 | 89.27% | 295.5571 | 277.8237 | 6667.7692
1979 | 4 | 22 | 608.6531 | 25 | 583.6531 | 28.7827 | 139.3858 | 0.77441 | 28.0083 | 89.27% | 295.1442 | 277.4356 | 6658.454
1979 | 4 | 23 | 540.7347 | 25 | 515.7347 | 28.9185 | 139.3858 | 0.77441 | 28.1441 | 89.27% | 296.5757 | 278.7811 | 6690.7467
1979 | 4 | 24 | 629.551 | 25 | 604.551 | 28.7409 | 139.3858 | 0.77441 | 27.9665 | 89.27% | 294.7038 | 277.0216 | 6648.5178
1979 | 4 | 25 | 559.0204 | 25 | 534.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
1979 | 4 | 26 | 508.0816 | 25 | 483.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
1979 | 4 | 27 | 1345.3061 | 25 | 1320.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
1979 | 4 | 28 | 3278.3673 | 25 | 3253.3673 | 23.4433 | 0 | 0 | 23.4433 | 0% | 0 | 0 | 0
1979 | 4 | 29 | 1488.9796 | 25 | 1463.9796 | 27.022 | 139.3858 | 0.77441 | 26.2476 | 89.27% | 276.5909 | 259.9955 | 6239.8911
1979 | 4 | 30 | 859.4286 | 25 | 834.4286 | 28.2811 | 139.3858 | 0.77441 | 27.5067 | 89.27% | 289.859 | 272.4675 | 6539.2195
1979 | 5 | 1 | 654.3673 | 25 | 629.3673 | 28.6913 | 139.3858 | 0.77441 | 27.9169 | 89.27% | 294.1808 | 276.5299 | 6636.7186
1979 | 5 | 2 | 654.3673 | 25 | 629.3673 | 28.6913 | 139.3858 | 0.77441 | 27.9169 | 89.27% | 294.1808 | 276.5299 | 6636.7186
1979 | 5 | 3 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1979 | 5 | 4 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1979 | 5 | 5 | 608.6531 | 25 | 583.6531 | 28.7827 | 139.3858 | 0.77441 | 28.0083 | 89.27% | 295.1442 | 277.4356 | 6658.454
1979 | 5 | 6 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1979 | 5 | 7 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1979 | 5 | 8 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1979 | 5 | 9 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1979 | 5 | 10 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1979 | 5 | 11 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1979 | 5 | 12 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1979 | 5 | 13 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1979 | 5 | 14 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1979 | 5 | 15 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1979 | 5 | 16 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1979 | 5 | 17 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1979 | 5 | 18 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1979 | 5 | 19 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1979 | 5 | 20 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1979 | 5 | 21 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1979 | 5 | 22 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1979 | 5 | 23 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1979 | 5 | 24 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1979 | 5 | 25 | 722.2857 | 25 | 697.2857 | 28.5554 | 139.3858 | 0.77441 | 27.781 | 89.27% | 292.7494 | 275.1844 | 6604.4259
1979 | 5 | 26 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1979 | 5 | 27 | 815.0204 | 25 | 790.0204 | 28.37 | 139.3858 | 0.77441 | 27.5955 | 89.27% | 290.7949 | 273.3472 | 6560.3339
1979 | 5 | 28 | 542.0408 | 25 | 517.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
1979 | 5 | 29 | 830.6939 | 25 | 805.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
1979 | 5 | 30 | 830.6939 | 25 | 805.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
1979 | 5 | 31 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1979 | 6 | 1 | 555.102 | 25 | 530.102 | 28.8898 | 139.3858 | 0.77441 | 28.1154 | 89.27% | 296.2729 | 278.4965 | 6683.9156
1979 | 6 | 2 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
1979 | 6 | 3 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1979 | 6 | 4 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1979 | 6 | 5 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1979 | 6 | 6 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1979 | 6 | 7 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1979 | 6 | 8 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1979 | 6 | 9 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1979 | 6 | 10 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1979 | 6 | 11 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1979 | 6 | 12 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1979 | 6 | 13 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1979 | 6 | 14 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1979 | 6 | 15 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1979 | 6 | 16 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1979 | 6 | 17 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1979 | 6 | 18 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1979 | 6 | 19 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1979 | 6 | 20 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1979 | 6 | 21 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1979 | 6 | 22 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1979 | 6 | 23 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1979 | 6 | 24 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1979 | 6 | 25 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1979 | 6 | 26 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1979 | 6 | 27 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1979 | 6 | 28 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1979 | 6 | 29 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1979 | 6 | 30 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1979 | 7 | 1 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1979 | 7 | 2 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1979 | 7 | 3 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1979 | 7 | 4 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1979 | 7 | 5 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1979 | 7 | 6 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1979 | 7 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1979 | 7 | 8 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1979 | 7 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1979 | 7 | 10 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1979 | 7 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 7 | 12 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1979 | 7 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1979 | 7 | 14 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1979 | 7 | 15 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1979 | 7 | 16 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1979 | 7 | 17 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1979 | 7 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1979 | 7 | 19 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1979 | 7 | 20 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1979 | 7 | 21 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1979 | 7 | 22 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 7 | 23 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1979 | 7 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1979 | 7 | 25 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1979 | 7 | 26 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1979 | 7 | 27 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1979 | 7 | 28 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1979 | 7 | 29 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1979 | 7 | 30 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1979 | 7 | 31 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1979 | 8 | 1 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1979 | 8 | 2 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1979 | 8 | 3 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1979 | 8 | 4 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 8 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1979 | 8 | 6 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
1979 | 8 | 7 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1979 | 8 | 8 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1979 | 8 | 9 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1979 | 8 | 10 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1979 | 8 | 11 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1979 | 8 | 12 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1979 | 8 | 13 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1979 | 8 | 14 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1979 | 8 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1979 | 8 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1979 | 8 | 17 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1979 | 8 | 18 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 8 | 19 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1979 | 8 | 20 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1979 | 8 | 21 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1979 | 8 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1979 | 8 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1979 | 8 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1979 | 8 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1979 | 8 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1979 | 8 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1979 | 8 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1979 | 8 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1979 | 8 | 31 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1979 | 9 | 1 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1979 | 9 | 2 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1979 | 9 | 3 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1979 | 9 | 4 | 12.4082 | 15 | 0 | 29.9752 | 0 | 0 | 29.9752 | 0% | 0 | 0 | 0
1979 | 9 | 5 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1979 | 9 | 6 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1979 | 9 | 7 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1979 | 9 | 8 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1979 | 9 | 9 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1979 | 9 | 10 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1979 | 9 | 11 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1979 | 9 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1979 | 9 | 13 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1979 | 9 | 14 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1979 | 9 | 15 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1979 | 9 | 16 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1979 | 9 | 17 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1979 | 9 | 18 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1979 | 9 | 19 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1979 | 9 | 20 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1979 | 9 | 21 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1979 | 9 | 22 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1979 | 9 | 23 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1979 | 9 | 24 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1979 | 9 | 25 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1979 | 9 | 26 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1979 | 9 | 27 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1979 | 9 | 28 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1979 | 9 | 29 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1979 | 9 | 30 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1979 | 10 | 1 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1979 | 10 | 2 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1979 | 10 | 3 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1979 | 10 | 4 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1979 | 10 | 5 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1979 | 10 | 6 | 244.2449 | 15 | 229.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1979 | 10 | 7 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1979 | 10 | 8 | 269.0612 | 15 | 254.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1979 | 10 | 9 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1979 | 10 | 10 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1979 | 10 | 11 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1979 | 10 | 12 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1979 | 10 | 13 | 259.9184 | 15 | 244.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1979 | 10 | 14 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1979 | 10 | 15 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1979 | 10 | 16 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1979 | 10 | 17 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1979 | 10 | 18 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1979 | 10 | 19 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1979 | 10 | 20 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1979 | 10 | 21 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1979 | 10 | 22 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1979 | 10 | 23 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1979 | 10 | 24 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1979 | 10 | 25 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1979 | 10 | 26 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1979 | 10 | 27 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1979 | 10 | 28 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1979 | 10 | 29 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1979 | 10 | 30 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1979 | 10 | 31 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1979 | 11 | 1 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1979 | 11 | 2 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1979 | 11 | 3 | 308.2449 | 15 | 293.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1979 | 11 | 4 | 448 | 15 | 433 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1979 | 11 | 5 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1979 | 11 | 6 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1979 | 11 | 7 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1979 | 11 | 8 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1979 | 11 | 9 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1979 | 11 | 10 | 203.7551 | 15 | 188.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1979 | 11 | 11 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1979 | 11 | 12 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1979 | 11 | 13 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1979 | 11 | 14 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1979 | 11 | 15 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1979 | 11 | 16 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1979 | 11 | 17 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1979 | 11 | 18 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1979 | 11 | 19 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1979 | 11 | 20 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1979 | 11 | 21 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1979 | 11 | 22 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1979 | 11 | 23 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1979 | 11 | 24 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1979 | 11 | 25 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1979 | 11 | 26 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1979 | 11 | 27 | 586.449 | 15 | 571.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1979 | 11 | 28 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1979 | 11 | 29 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1979 | 11 | 30 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1979 | 12 | 1 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1979 | 12 | 2 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1979 | 12 | 3 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1979 | 12 | 4 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1979 | 12 | 5 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1979 | 12 | 6 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1979 | 12 | 7 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1979 | 12 | 8 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1979 | 12 | 9 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1979 | 12 | 10 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1979 | 12 | 11 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1979 | 12 | 12 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1979 | 12 | 13 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1979 | 12 | 14 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1979 | 12 | 15 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1979 | 12 | 16 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1979 | 12 | 17 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1979 | 12 | 18 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1979 | 12 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1979 | 12 | 20 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1979 | 12 | 21 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1979 | 12 | 22 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1979 | 12 | 23 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1979 | 12 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1979 | 12 | 25 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1979 | 12 | 26 | 363.102 | 5 | 358.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1979 | 12 | 27 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1979 | 12 | 28 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1979 | 12 | 29 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1979 | 12 | 30 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1979 | 12 | 31 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1980 | 1 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1980 | 1 | 2 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1980 | 1 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1980 | 1 | 4 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1980 | 1 | 5 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1980 | 1 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1980 | 1 | 7 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1980 | 1 | 8 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1980 | 1 | 9 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1980 | 1 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1980 | 1 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1980 | 1 | 12 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1980 | 1 | 13 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1980 | 1 | 14 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1980 | 1 | 15 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1980 | 1 | 16 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1980 | 1 | 17 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1980 | 1 | 18 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1980 | 1 | 19 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1980 | 1 | 20 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1980 | 1 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1980 | 1 | 22 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1980 | 1 | 23 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1980 | 1 | 24 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1980 | 1 | 25 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1980 | 1 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1980 | 1 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1980 | 1 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1980 | 1 | 29 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1980 | 1 | 30 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1980 | 1 | 31 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1980 | 2 | 1 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1980 | 2 | 2 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1980 | 2 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1980 | 2 | 4 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1980 | 2 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 2 | 6 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 8 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 9 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 10 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1980 | 2 | 11 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1980 | 2 | 12 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1980 | 2 | 13 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1980 | 2 | 14 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1980 | 2 | 15 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1980 | 2 | 16 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1980 | 2 | 17 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1980 | 2 | 18 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1980 | 2 | 19 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1980 | 2 | 20 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1980 | 2 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 23 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 2 | 24 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 2 | 25 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 2 | 26 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 2 | 27 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 2 | 28 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 2 | 29 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 3 | 1 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1980 | 3 | 2 | 11.7551 | 25 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1980 | 3 | 3 | 10.8408 | 25 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1980 | 3 | 4 | 10.5796 | 25 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1980 | 3 | 5 | 10.449 | 25 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1980 | 3 | 6 | 11.4939 | 25 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1980 | 3 | 7 | 12.2776 | 25 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1980 | 3 | 8 | 12.8 | 25 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1980 | 3 | 9 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1980 | 3 | 10 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1980 | 3 | 11 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1980 | 3 | 12 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1980 | 3 | 13 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1980 | 3 | 14 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1980 | 3 | 15 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1980 | 3 | 16 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1980 | 3 | 17 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1980 | 3 | 18 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1980 | 3 | 19 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1980 | 3 | 20 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1980 | 3 | 21 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1980 | 3 | 22 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1980 | 3 | 23 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1980 | 3 | 24 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1980 | 3 | 25 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1980 | 3 | 26 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1980 | 3 | 27 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1980 | 3 | 28 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1980 | 3 | 29 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1980 | 3 | 30 | 535.5102 | 25 | 510.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1980 | 3 | 31 | 420.5714 | 25 | 395.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1980 | 4 | 1 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1980 | 4 | 2 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1980 | 4 | 3 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1980 | 4 | 4 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1980 | 4 | 5 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1980 | 4 | 6 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1980 | 4 | 7 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1980 | 4 | 8 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1980 | 4 | 9 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1980 | 4 | 10 | 2089.7959 | 25 | 2064.7959 | 25.8204 | 139.3858 | 0.77441 | 25.046 | 89.27% | 263.9284 | 248.0927 | 5954.2251
1980 | 4 | 11 | 2690.6122 | 25 | 2665.6122 | 24.6188 | 0 | 0 | 24.6188 | 0% | 0 | 0 | 0
1980 | 4 | 12 | 941.7143 | 25 | 916.7143 | 28.1166 | 139.3858 | 0.77441 | 27.3422 | 89.27% | 288.1248 | 270.8373 | 6500.0957
1980 | 4 | 13 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
1980 | 4 | 14 | 445.3878 | 25 | 420.3878 | 29.1092 | 139.3858 | 0.77441 | 28.3348 | 89.27% | 298.5851 | 280.67 | 6736.0807
1980 | 4 | 15 | 557.7143 | 25 | 532.7143 | 28.8846 | 139.3858 | 0.77441 | 28.1102 | 89.27% | 296.2178 | 278.4447 | 6682.6735
1980 | 4 | 16 | 641.3061 | 25 | 616.3061 | 28.7174 | 139.3858 | 0.77441 | 27.943 | 89.27% | 294.4561 | 276.7887 | 6642.9287
1980 | 4 | 17 | 419.2653 | 25 | 394.2653 | 29.1615 | 139.3858 | 0.77441 | 28.3871 | 89.27% | 299.1357 | 281.1875 | 6748.5009
1980 | 4 | 18 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1980 | 4 | 19 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1980 | 4 | 20 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1980 | 4 | 21 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1980 | 4 | 22 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1980 | 4 | 23 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1980 | 4 | 24 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1980 | 4 | 25 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1980 | 4 | 26 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1980 | 4 | 27 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1980 | 4 | 28 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1980 | 4 | 29 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1980 | 4 | 30 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1980 | 5 | 1 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1980 | 5 | 2 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1980 | 5 | 3 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1980 | 5 | 4 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1980 | 5 | 5 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1980 | 5 | 6 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1980 | 5 | 7 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1980 | 5 | 8 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1980 | 5 | 9 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1980 | 5 | 10 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1980 | 5 | 11 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1980 | 5 | 12 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1980 | 5 | 13 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1980 | 5 | 14 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1980 | 5 | 15 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1980 | 5 | 16 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1980 | 5 | 17 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1980 | 5 | 18 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1980 | 5 | 19 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1980 | 5 | 20 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1980 | 5 | 21 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1980 | 5 | 22 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1980 | 5 | 23 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1980 | 5 | 24 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1980 | 5 | 25 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1980 | 5 | 26 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1980 | 5 | 27 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1980 | 5 | 28 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1980 | 5 | 29 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1980 | 5 | 30 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1980 | 5 | 31 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1980 | 6 | 1 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1980 | 6 | 2 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1980 | 6 | 3 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1980 | 6 | 4 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1980 | 6 | 5 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1980 | 6 | 6 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1980 | 6 | 7 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1980 | 6 | 8 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1980 | 6 | 9 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1980 | 6 | 10 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1980 | 6 | 11 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1980 | 6 | 12 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1980 | 6 | 13 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1980 | 6 | 14 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1980 | 6 | 15 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1980 | 6 | 16 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1980 | 6 | 17 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1980 | 6 | 18 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1980 | 6 | 19 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1980 | 6 | 20 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1980 | 6 | 21 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1980 | 6 | 22 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1980 | 6 | 23 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1980 | 6 | 24 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1980 | 6 | 25 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1980 | 6 | 26 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1980 | 6 | 27 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1980 | 6 | 28 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1980 | 6 | 29 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1980 | 6 | 30 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1980 | 7 | 1 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1980 | 7 | 2 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1980 | 7 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1980 | 7 | 4 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1980 | 7 | 5 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1980 | 7 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1980 | 7 | 7 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1980 | 7 | 8 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1980 | 7 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1980 | 7 | 10 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1980 | 7 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1980 | 7 | 12 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1980 | 7 | 13 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1980 | 7 | 14 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1980 | 7 | 15 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1980 | 7 | 16 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1980 | 7 | 17 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1980 | 7 | 18 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1980 | 7 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1980 | 7 | 20 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1980 | 7 | 21 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1980 | 7 | 22 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1980 | 7 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1980 | 7 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1980 | 7 | 25 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1980 | 7 | 26 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1980 | 7 | 27 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1980 | 7 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1980 | 7 | 29 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1980 | 7 | 30 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1980 | 7 | 31 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1980 | 8 | 1 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1980 | 8 | 2 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1980 | 8 | 3 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1980 | 8 | 4 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1980 | 8 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1980 | 8 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1980 | 8 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1980 | 8 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1980 | 8 | 9 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1980 | 8 | 10 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1980 | 8 | 11 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1980 | 8 | 12 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1980 | 8 | 13 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1980 | 8 | 14 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1980 | 8 | 15 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1980 | 8 | 16 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1980 | 8 | 17 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1980 | 8 | 18 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1980 | 8 | 19 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1980 | 8 | 20 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1980 | 8 | 21 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 8 | 22 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1980 | 8 | 23 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1980 | 8 | 24 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1980 | 8 | 25 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1980 | 8 | 26 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1980 | 8 | 27 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1980 | 8 | 28 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1980 | 8 | 29 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1980 | 8 | 30 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1980 | 8 | 31 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1980 | 9 | 1 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1980 | 9 | 2 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1980 | 9 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1980 | 9 | 4 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1980 | 9 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1980 | 9 | 6 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1980 | 9 | 7 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1980 | 9 | 8 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1980 | 9 | 9 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1980 | 9 | 10 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1980 | 9 | 11 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1980 | 9 | 12 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1980 | 9 | 13 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1980 | 9 | 14 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1980 | 9 | 15 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1980 | 9 | 16 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1980 | 9 | 17 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1980 | 9 | 18 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1980 | 9 | 19 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1980 | 9 | 20 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1980 | 9 | 21 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1980 | 9 | 22 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1980 | 9 | 23 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1980 | 9 | 24 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1980 | 9 | 25 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1980 | 9 | 26 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1980 | 9 | 27 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1980 | 9 | 28 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1980 | 9 | 29 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1980 | 9 | 30 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1980 | 10 | 1 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1980 | 10 | 2 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1980 | 10 | 3 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1980 | 10 | 4 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1980 | 10 | 5 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1980 | 10 | 6 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1980 | 10 | 7 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1980 | 10 | 8 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1980 | 10 | 9 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1980 | 10 | 10 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1980 | 10 | 11 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1980 | 10 | 12 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1980 | 10 | 13 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1980 | 10 | 14 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1980 | 10 | 15 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1980 | 10 | 16 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1980 | 10 | 17 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1980 | 10 | 18 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1980 | 10 | 19 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1980 | 10 | 20 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1980 | 10 | 21 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1980 | 10 | 22 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1980 | 10 | 23 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1980 | 10 | 24 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1980 | 10 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1980 | 10 | 26 | 519.8367 | 15 | 504.8367 | 28.9603 | 139.3858 | 0.77441 | 28.1859 | 89.27% | 297.0161 | 279.1951 | 6700.6829
1980 | 10 | 27 | 351.3469 | 15 | 336.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1980 | 10 | 28 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1980 | 10 | 29 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1980 | 10 | 30 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1980 | 10 | 31 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1980 | 11 | 1 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1980 | 11 | 2 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1980 | 11 | 3 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1980 | 11 | 4 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1980 | 11 | 5 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1980 | 11 | 6 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1980 | 11 | 7 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1980 | 11 | 8 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1980 | 11 | 9 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1980 | 11 | 10 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1980 | 11 | 11 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1980 | 11 | 12 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1980 | 11 | 13 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1980 | 11 | 14 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1980 | 11 | 15 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1980 | 11 | 16 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1980 | 11 | 17 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1980 | 11 | 18 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1980 | 11 | 19 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1980 | 11 | 20 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1980 | 11 | 21 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1980 | 11 | 22 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1980 | 11 | 23 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1980 | 11 | 24 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1980 | 11 | 25 | 293.8776 | 15 | 278.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1980 | 11 | 26 | 340.898 | 15 | 325.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
1980 | 11 | 27 | 225.9592 | 15 | 210.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1980 | 11 | 28 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1980 | 11 | 29 | 534.2041 | 15 | 519.2041 | 28.9316 | 139.3858 | 0.77441 | 28.1572 | 89.27% | 296.7133 | 278.9105 | 6693.8518
1980 | 11 | 30 | 438.8571 | 15 | 423.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1980 | 12 | 1 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1980 | 12 | 2 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1980 | 12 | 3 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1980 | 12 | 4 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1980 | 12 | 5 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1980 | 12 | 6 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1980 | 12 | 7 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1980 | 12 | 8 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1980 | 12 | 9 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1980 | 12 | 10 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1980 | 12 | 11 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1980 | 12 | 12 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1980 | 12 | 13 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1980 | 12 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1980 | 12 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1980 | 12 | 16 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1980 | 12 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1980 | 12 | 18 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1980 | 12 | 19 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1980 | 12 | 20 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1980 | 12 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1980 | 12 | 22 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1980 | 12 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1980 | 12 | 24 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1980 | 12 | 25 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1980 | 12 | 26 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1980 | 12 | 27 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1980 | 12 | 28 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1980 | 12 | 29 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1980 | 12 | 30 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1980 | 12 | 31 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1981 | 1 | 1 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 2 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1981 | 1 | 3 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 4 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1981 | 1 | 6 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1981 | 1 | 7 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1981 | 1 | 8 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1981 | 1 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1981 | 1 | 10 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1981 | 1 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 12 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 13 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 14 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 15 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 16 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 17 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 18 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 19 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 20 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 21 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 22 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1981 | 1 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 24 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1981 | 1 | 26 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 27 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 1 | 29 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 1 | 30 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1981 | 1 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1981 | 2 | 1 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1981 | 2 | 2 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1981 | 2 | 3 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1981 | 2 | 4 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1981 | 2 | 5 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1981 | 2 | 6 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1981 | 2 | 7 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1981 | 2 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1981 | 2 | 9 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1981 | 2 | 10 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1981 | 2 | 11 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1981 | 2 | 12 | 555.102 | 5 | 550.102 | 28.8898 | 139.3858 | 0.77441 | 28.1154 | 89.27% | 296.2729 | 278.4965 | 6683.9156
1981 | 2 | 13 | 509.3878 | 5 | 504.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1981 | 2 | 14 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1981 | 2 | 15 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1981 | 2 | 16 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1981 | 2 | 17 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1981 | 2 | 18 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1981 | 2 | 19 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1981 | 2 | 20 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1981 | 2 | 21 | 1098.449 | 5 | 1093.449 | 27.8031 | 139.3858 | 0.77441 | 27.0287 | 89.27% | 284.8215 | 267.7323 | 6425.5741
1981 | 2 | 22 | 960 | 5 | 955 | 28.08 | 139.3858 | 0.77441 | 27.3056 | 89.27% | 287.7394 | 270.4751 | 6491.4015
1981 | 2 | 23 | 581.2245 | 5 | 576.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
1981 | 2 | 24 | 535.5102 | 5 | 530.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
1981 | 2 | 25 | 1071.0204 | 5 | 1066.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
1981 | 2 | 26 | 768 | 5 | 763 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
1981 | 2 | 27 | 701.3878 | 5 | 696.3878 | 28.5972 | 139.3858 | 0.77441 | 27.8228 | 89.27% | 293.1898 | 275.5984 | 6614.3621
1981 | 2 | 28 | 468.898 | 5 | 463.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
1981 | 3 | 1 | 361.7959 | 25 | 336.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1981 | 3 | 2 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1981 | 3 | 3 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1981 | 3 | 4 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1981 | 3 | 5 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1981 | 3 | 6 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1981 | 3 | 7 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1981 | 3 | 8 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1981 | 3 | 9 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1981 | 3 | 10 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1981 | 3 | 11 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1981 | 3 | 12 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1981 | 3 | 13 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1981 | 3 | 14 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1981 | 3 | 15 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1981 | 3 | 16 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1981 | 3 | 17 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1981 | 3 | 18 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1981 | 3 | 19 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1981 | 3 | 20 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1981 | 3 | 21 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1981 | 3 | 22 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1981 | 3 | 23 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1981 | 3 | 24 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1981 | 3 | 25 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1981 | 3 | 26 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1981 | 3 | 27 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1981 | 3 | 28 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1981 | 3 | 29 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1981 | 3 | 30 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1981 | 3 | 31 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1981 | 4 | 1 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1981 | 4 | 2 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1981 | 4 | 3 | 445.3878 | 25 | 420.3878 | 29.1092 | 139.3858 | 0.77441 | 28.3348 | 89.27% | 298.5851 | 280.67 | 6736.0807
1981 | 4 | 4 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1981 | 4 | 5 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1981 | 4 | 6 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1981 | 4 | 7 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1981 | 4 | 8 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1981 | 4 | 9 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1981 | 4 | 10 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1981 | 4 | 11 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1981 | 4 | 12 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1981 | 4 | 13 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1981 | 4 | 14 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1981 | 4 | 15 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1981 | 4 | 16 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1981 | 4 | 17 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1981 | 4 | 18 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1981 | 4 | 19 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1981 | 4 | 20 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1981 | 4 | 21 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1981 | 4 | 22 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1981 | 4 | 23 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1981 | 4 | 24 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1981 | 4 | 25 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1981 | 4 | 26 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1981 | 4 | 27 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1981 | 4 | 28 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1981 | 4 | 29 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1981 | 4 | 30 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1981 | 5 | 1 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1981 | 5 | 2 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1981 | 5 | 3 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1981 | 5 | 4 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1981 | 5 | 5 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1981 | 5 | 6 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1981 | 5 | 7 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1981 | 5 | 8 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1981 | 5 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1981 | 5 | 10 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1981 | 5 | 11 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1981 | 5 | 12 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1981 | 5 | 13 | 327.8367 | 25 | 302.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1981 | 5 | 14 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1981 | 5 | 15 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1981 | 5 | 16 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1981 | 5 | 17 | 327.8367 | 25 | 302.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1981 | 5 | 18 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1981 | 5 | 19 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1981 | 5 | 20 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1981 | 5 | 21 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1981 | 5 | 22 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1981 | 5 | 23 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1981 | 5 | 24 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1981 | 5 | 25 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1981 | 5 | 26 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1981 | 5 | 27 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1981 | 5 | 28 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1981 | 5 | 29 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1981 | 5 | 30 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1981 | 5 | 31 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1981 | 6 | 1 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1981 | 6 | 2 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1981 | 6 | 3 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1981 | 6 | 4 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1981 | 6 | 5 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1981 | 6 | 6 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1981 | 6 | 7 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1981 | 6 | 8 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1981 | 6 | 9 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1981 | 6 | 10 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1981 | 6 | 11 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1981 | 6 | 12 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1981 | 6 | 13 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1981 | 6 | 14 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1981 | 6 | 15 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1981 | 6 | 16 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1981 | 6 | 17 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1981 | 6 | 18 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1981 | 6 | 19 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1981 | 6 | 20 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1981 | 6 | 21 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1981 | 6 | 22 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1981 | 6 | 23 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1981 | 6 | 24 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1981 | 6 | 25 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1981 | 6 | 26 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1981 | 6 | 27 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1981 | 6 | 28 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1981 | 6 | 29 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1981 | 6 | 30 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1981 | 7 | 1 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1981 | 7 | 2 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1981 | 7 | 3 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 7 | 4 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1981 | 7 | 5 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1981 | 7 | 6 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1981 | 7 | 7 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1981 | 7 | 8 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1981 | 7 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1981 | 7 | 10 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1981 | 7 | 11 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1981 | 7 | 12 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1981 | 7 | 13 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1981 | 7 | 14 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1981 | 7 | 15 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1981 | 7 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1981 | 7 | 17 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1981 | 7 | 18 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1981 | 7 | 19 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1981 | 7 | 20 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1981 | 7 | 21 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1981 | 7 | 22 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1981 | 7 | 23 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1981 | 7 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1981 | 7 | 25 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1981 | 7 | 26 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1981 | 7 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1981 | 7 | 28 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1981 | 7 | 29 | 190.6939 | 5 | 185.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1981 | 7 | 30 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1981 | 7 | 31 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1981 | 8 | 1 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1981 | 8 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1981 | 8 | 3 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1981 | 8 | 4 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1981 | 8 | 5 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1981 | 8 | 6 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1981 | 8 | 7 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1981 | 8 | 8 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1981 | 8 | 9 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1981 | 8 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1981 | 8 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1981 | 8 | 12 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1981 | 8 | 13 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1981 | 8 | 14 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1981 | 8 | 15 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1981 | 8 | 16 | 1154.6122 | 5 | 1149.6122 | 27.6908 | 139.3858 | 0.77441 | 26.9164 | 89.27% | 283.6379 | 266.6196 | 6398.8705
1981 | 8 | 17 | 871.1837 | 5 | 866.1837 | 28.2576 | 139.3858 | 0.77441 | 27.4832 | 89.27% | 289.6113 | 272.2346 | 6533.6304
1981 | 8 | 18 | 414.0408 | 5 | 409.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1981 | 8 | 19 | 257.3061 | 5 | 252.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1981 | 8 | 20 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1981 | 8 | 21 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1981 | 8 | 22 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1981 | 8 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1981 | 8 | 24 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1981 | 8 | 25 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1981 | 8 | 26 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1981 | 8 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1981 | 8 | 28 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1981 | 8 | 29 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1981 | 8 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1981 | 8 | 31 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1981 | 9 | 1 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1981 | 9 | 2 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1981 | 9 | 3 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1981 | 9 | 4 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1981 | 9 | 5 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1981 | 9 | 6 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1981 | 9 | 7 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1981 | 9 | 8 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1981 | 9 | 9 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1981 | 9 | 10 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1981 | 9 | 11 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1981 | 9 | 12 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1981 | 9 | 13 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1981 | 9 | 14 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1981 | 9 | 15 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1981 | 9 | 16 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1981 | 9 | 17 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1981 | 9 | 18 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1981 | 9 | 19 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1981 | 9 | 20 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1981 | 9 | 21 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1981 | 9 | 22 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1981 | 9 | 23 | 561.6327 | 15 | 546.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
1981 | 9 | 24 | 920.8163 | 15 | 905.8163 | 28.1584 | 139.3858 | 0.77441 | 27.384 | 89.27% | 288.5652 | 271.2513 | 6510.0319
1981 | 9 | 25 | 679.1837 | 15 | 664.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
1981 | 9 | 26 | 400.9796 | 15 | 385.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1981 | 9 | 27 | 284.7347 | 15 | 269.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1981 | 9 | 28 | 455.8367 | 15 | 440.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1981 | 9 | 29 | 368.3265 | 15 | 353.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1981 | 9 | 30 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1981 | 10 | 1 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1981 | 10 | 2 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1981 | 10 | 3 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1981 | 10 | 4 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1981 | 10 | 5 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1981 | 10 | 6 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1981 | 10 | 7 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1981 | 10 | 8 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1981 | 10 | 9 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1981 | 10 | 10 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1981 | 10 | 11 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1981 | 10 | 12 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1981 | 10 | 13 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1981 | 10 | 14 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1981 | 10 | 15 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1981 | 10 | 16 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1981 | 10 | 17 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1981 | 10 | 18 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1981 | 10 | 19 | 336.9796 | 15 | 321.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1981 | 10 | 20 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1981 | 10 | 21 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1981 | 10 | 22 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1981 | 10 | 23 | 246.8571 | 15 | 231.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
1981 | 10 | 24 | 1371.4286 | 15 | 1356.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1981 | 10 | 25 | 915.5918 | 15 | 900.5918 | 28.1688 | 139.3858 | 0.77441 | 27.3944 | 89.27% | 288.6754 | 271.3548 | 6512.5159
1981 | 10 | 26 | 617.7959 | 15 | 602.7959 | 28.7644 | 139.3858 | 0.77441 | 27.99 | 89.27% | 294.9515 | 277.2545 | 6654.1069
1981 | 10 | 27 | 1039.6735 | 15 | 1024.6735 | 27.9207 | 139.3858 | 0.77441 | 27.1462 | 89.27% | 286.0603 | 268.8967 | 6453.5197
1981 | 10 | 28 | 1201.6327 | 15 | 1186.6327 | 27.5967 | 139.3858 | 0.77441 | 26.8223 | 89.27% | 282.6469 | 265.6881 | 6376.514
1981 | 10 | 29 | 800.6531 | 15 | 785.6531 | 28.3987 | 139.3858 | 0.77441 | 27.6243 | 89.27% | 291.0977 | 273.6319 | 6567.1651
1981 | 10 | 30 | 574.6939 | 15 | 559.6939 | 28.8506 | 139.3858 | 0.77441 | 28.0762 | 89.27% | 295.8599 | 278.1083 | 6674.6004
1981 | 10 | 31 | 448 | 15 | 433 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
1981 | 11 | 1 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1981 | 11 | 2 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1981 | 11 | 3 | 284.7347 | 15 | 269.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1981 | 11 | 4 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1981 | 11 | 5 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1981 | 11 | 6 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1981 | 11 | 7 | 350.0408 | 15 | 335.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1981 | 11 | 8 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1981 | 11 | 9 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1981 | 11 | 10 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1981 | 11 | 11 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1981 | 11 | 12 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1981 | 11 | 13 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1981 | 11 | 14 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1981 | 11 | 15 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1981 | 11 | 16 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1981 | 11 | 17 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1981 | 11 | 18 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1981 | 11 | 19 | 320 | 15 | 305 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1981 | 11 | 20 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1981 | 11 | 21 | 519.8367 | 15 | 504.8367 | 28.9603 | 139.3858 | 0.77441 | 28.1859 | 89.27% | 297.0161 | 279.1951 | 6700.6829
1981 | 11 | 22 | 543.3469 | 15 | 528.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1981 | 11 | 23 | 378.7755 | 15 | 363.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1981 | 11 | 24 | 295.1837 | 15 | 280.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1981 | 11 | 25 | 244.2449 | 15 | 229.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1981 | 11 | 26 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1981 | 11 | 27 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1981 | 11 | 28 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1981 | 11 | 29 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1981 | 11 | 30 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1981 | 12 | 1 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1981 | 12 | 2 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1981 | 12 | 3 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1981 | 12 | 4 | 249.4694 | 5 | 244.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1981 | 12 | 5 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1981 | 12 | 6 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1981 | 12 | 7 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1981 | 12 | 8 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1981 | 12 | 9 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1981 | 12 | 10 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1981 | 12 | 11 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1981 | 12 | 12 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1981 | 12 | 13 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1981 | 12 | 14 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1981 | 12 | 15 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1981 | 12 | 16 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1981 | 12 | 17 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1981 | 12 | 18 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1981 | 12 | 19 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1981 | 12 | 20 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1981 | 12 | 21 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1981 | 12 | 22 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1981 | 12 | 23 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1981 | 12 | 24 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1981 | 12 | 25 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1981 | 12 | 26 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1981 | 12 | 27 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1981 | 12 | 28 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1981 | 12 | 29 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1981 | 12 | 30 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1981 | 12 | 31 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1982 | 1 | 1 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1982 | 1 | 2 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1982 | 1 | 3 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1982 | 1 | 4 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1982 | 1 | 5 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1982 | 1 | 6 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1982 | 1 | 7 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1982 | 1 | 8 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1982 | 1 | 9 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1982 | 1 | 10 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1982 | 1 | 11 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1982 | 1 | 12 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1982 | 1 | 13 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1982 | 1 | 14 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1982 | 1 | 15 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1982 | 1 | 16 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1982 | 1 | 17 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1982 | 1 | 18 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1982 | 1 | 19 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1982 | 1 | 20 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1982 | 1 | 21 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1982 | 1 | 22 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1982 | 1 | 23 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1982 | 1 | 24 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1982 | 1 | 25 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1982 | 1 | 26 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1982 | 1 | 27 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1982 | 1 | 28 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1982 | 1 | 29 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1982 | 1 | 30 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1982 | 1 | 31 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1982 | 2 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1982 | 2 | 2 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1982 | 2 | 3 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1982 | 2 | 4 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1982 | 2 | 5 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1982 | 2 | 6 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1982 | 2 | 7 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1982 | 2 | 8 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1982 | 2 | 9 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1982 | 2 | 10 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1982 | 2 | 11 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1982 | 2 | 12 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1982 | 2 | 13 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1982 | 2 | 14 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1982 | 2 | 15 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1982 | 2 | 16 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1982 | 2 | 17 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1982 | 2 | 18 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1982 | 2 | 19 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1982 | 2 | 20 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1982 | 2 | 21 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1982 | 2 | 22 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1982 | 2 | 23 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1982 | 2 | 24 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1982 | 2 | 25 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1982 | 2 | 26 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1982 | 2 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1982 | 2 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1982 | 3 | 1 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1982 | 3 | 2 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1982 | 3 | 3 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1982 | 3 | 4 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1982 | 3 | 5 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1982 | 3 | 6 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1982 | 3 | 7 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1982 | 3 | 8 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1982 | 3 | 9 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1982 | 3 | 10 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1982 | 3 | 11 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1982 | 3 | 12 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1982 | 3 | 13 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1982 | 3 | 14 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1982 | 3 | 15 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1982 | 3 | 16 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1982 | 3 | 17 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1982 | 3 | 18 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1982 | 3 | 19 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1982 | 3 | 20 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1982 | 3 | 21 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1982 | 3 | 22 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1982 | 3 | 23 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1982 | 3 | 24 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1982 | 3 | 25 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1982 | 3 | 26 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1982 | 3 | 27 | 564.2449 | 25 | 539.2449 | 28.8715 | 139.3858 | 0.77441 | 28.0971 | 89.27% | 296.0802 | 278.3154 | 6679.5685
1982 | 3 | 28 | 496.3265 | 25 | 471.3265 | 29.0073 | 139.3858 | 0.77441 | 28.2329 | 89.27% | 297.5116 | 279.6609 | 6711.8611
1982 | 3 | 29 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1982 | 3 | 30 | 327.8367 | 25 | 302.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1982 | 3 | 31 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1982 | 4 | 1 | 506.7755 | 25 | 481.7755 | 28.9864 | 139.3858 | 0.77441 | 28.212 | 89.27% | 297.2914 | 279.4539 | 6706.893
1982 | 4 | 2 | 594.2857 | 25 | 569.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
1982 | 4 | 3 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1982 | 4 | 4 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
1982 | 4 | 5 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1982 | 4 | 6 | 393.1429 | 25 | 368.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1982 | 4 | 7 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1982 | 4 | 8 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1982 | 4 | 9 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1982 | 4 | 10 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1982 | 4 | 11 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1982 | 4 | 12 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1982 | 4 | 13 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1982 | 4 | 14 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1982 | 4 | 15 | 484.5714 | 25 | 459.5714 | 29.0309 | 139.3858 | 0.77441 | 28.2564 | 89.27% | 297.7593 | 279.8938 | 6717.4503
1982 | 4 | 16 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1982 | 4 | 17 | 976.9796 | 25 | 951.9796 | 28.046 | 139.3858 | 0.77441 | 27.2716 | 89.27% | 287.3816 | 270.1387 | 6483.3283
1982 | 4 | 18 | 1619.5918 | 25 | 1594.5918 | 26.7608 | 139.3858 | 0.77441 | 25.9864 | 89.27% | 273.8382 | 257.4079 | 6177.7898
1982 | 4 | 19 | 1593.4694 | 25 | 1568.4694 | 26.8131 | 139.3858 | 0.77441 | 26.0387 | 89.27% | 274.3887 | 257.9254 | 6190.2101
1982 | 4 | 20 | 1270.8571 | 25 | 1245.8571 | 27.4583 | 139.3858 | 0.77441 | 26.6839 | 89.27% | 281.188 | 264.3167 | 6343.6003
1982 | 4 | 21 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1982 | 4 | 22 | 1046.2041 | 25 | 1021.2041 | 27.9076 | 139.3858 | 0.77441 | 27.1332 | 89.27% | 285.9226 | 268.7673 | 6450.4146
1982 | 4 | 23 | 732.7347 | 25 | 707.7347 | 28.5345 | 139.3858 | 0.77441 | 27.7601 | 89.27% | 292.5292 | 274.9774 | 6599.4578
1982 | 4 | 24 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1982 | 4 | 25 | 877.7143 | 25 | 852.7143 | 28.2446 | 139.3858 | 0.77441 | 27.4702 | 89.27% | 289.4736 | 272.1052 | 6530.5253
1982 | 4 | 26 | 914.2857 | 25 | 889.2857 | 28.1714 | 139.3858 | 0.77441 | 27.397 | 89.27% | 288.7029 | 271.3807 | 6513.1369
1982 | 4 | 27 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1982 | 4 | 28 | 1056.6531 | 25 | 1031.6531 | 27.8867 | 139.3858 | 0.77441 | 27.1123 | 89.27% | 285.7024 | 268.5603 | 6445.4465
1982 | 4 | 29 | 629.551 | 25 | 604.551 | 28.7409 | 139.3858 | 0.77441 | 27.9665 | 89.27% | 294.7038 | 277.0216 | 6648.5178
1982 | 4 | 30 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1982 | 5 | 1 | 393.1429 | 25 | 368.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1982 | 5 | 2 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1982 | 5 | 3 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1982 | 5 | 4 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1982 | 5 | 5 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1982 | 5 | 6 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1982 | 5 | 7 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1982 | 5 | 8 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1982 | 5 | 9 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1982 | 5 | 10 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1982 | 5 | 11 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1982 | 5 | 12 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1982 | 5 | 13 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1982 | 5 | 14 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1982 | 5 | 15 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1982 | 5 | 16 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1982 | 5 | 17 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1982 | 5 | 18 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1982 | 5 | 19 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1982 | 5 | 20 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1982 | 5 | 21 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1982 | 5 | 22 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1982 | 5 | 23 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1982 | 5 | 24 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1982 | 5 | 25 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1982 | 5 | 26 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1982 | 5 | 27 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1982 | 5 | 28 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1982 | 5 | 29 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1982 | 5 | 30 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1982 | 5 | 31 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1982 | 6 | 1 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1982 | 6 | 2 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1982 | 6 | 3 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1982 | 6 | 4 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1982 | 6 | 5 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1982 | 6 | 6 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1982 | 6 | 7 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1982 | 6 | 8 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1982 | 6 | 9 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1982 | 6 | 10 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1982 | 6 | 11 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1982 | 6 | 12 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1982 | 6 | 13 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1982 | 6 | 14 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1982 | 6 | 15 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1982 | 6 | 16 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1982 | 6 | 17 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1982 | 6 | 18 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1982 | 6 | 19 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1982 | 6 | 20 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1982 | 6 | 21 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1982 | 6 | 22 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1982 | 6 | 23 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1982 | 6 | 24 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1982 | 6 | 25 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1982 | 6 | 26 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1982 | 6 | 27 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1982 | 6 | 28 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1982 | 6 | 29 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1982 | 6 | 30 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1982 | 7 | 1 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1982 | 7 | 2 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1982 | 7 | 3 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1982 | 7 | 4 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1982 | 7 | 5 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1982 | 7 | 6 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1982 | 7 | 7 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1982 | 7 | 8 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1982 | 7 | 9 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1982 | 7 | 10 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1982 | 7 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1982 | 7 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1982 | 7 | 13 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1982 | 7 | 14 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1982 | 7 | 15 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1982 | 7 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1982 | 7 | 17 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1982 | 7 | 18 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1982 | 7 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1982 | 7 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1982 | 7 | 21 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1982 | 7 | 22 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1982 | 7 | 23 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1982 | 7 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1982 | 7 | 25 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1982 | 7 | 26 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1982 | 7 | 27 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1982 | 7 | 28 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1982 | 7 | 29 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1982 | 7 | 30 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1982 | 7 | 31 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1982 | 8 | 1 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1982 | 8 | 2 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1982 | 8 | 3 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1982 | 8 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1982 | 8 | 5 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1982 | 8 | 6 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1982 | 8 | 7 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1982 | 8 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1982 | 8 | 9 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1982 | 8 | 10 | 487.1837 | 5 | 482.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1982 | 8 | 11 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1982 | 8 | 12 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1982 | 8 | 13 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1982 | 8 | 14 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1982 | 8 | 15 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1982 | 8 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1982 | 8 | 17 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1982 | 8 | 18 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1982 | 8 | 19 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1982 | 8 | 20 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1982 | 8 | 21 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1982 | 8 | 22 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1982 | 8 | 23 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1982 | 8 | 24 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1982 | 8 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1982 | 8 | 26 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1982 | 8 | 27 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1982 | 8 | 28 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1982 | 8 | 29 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1982 | 8 | 30 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1982 | 8 | 31 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1982 | 9 | 1 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1982 | 9 | 2 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1982 | 9 | 3 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1982 | 9 | 4 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1982 | 9 | 5 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1982 | 9 | 6 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1982 | 9 | 7 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1982 | 9 | 8 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1982 | 9 | 9 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1982 | 9 | 10 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1982 | 9 | 11 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1982 | 9 | 12 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1982 | 9 | 13 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1982 | 9 | 14 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1982 | 9 | 15 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1982 | 9 | 16 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1982 | 9 | 17 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1982 | 9 | 18 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1982 | 9 | 19 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1982 | 9 | 20 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1982 | 9 | 21 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 9 | 22 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1982 | 9 | 23 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1982 | 9 | 24 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1982 | 9 | 25 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1982 | 9 | 26 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1982 | 9 | 27 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1982 | 9 | 28 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1982 | 9 | 29 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1982 | 9 | 30 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1982 | 10 | 1 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1982 | 10 | 2 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1982 | 10 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1982 | 10 | 4 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1982 | 10 | 5 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1982 | 10 | 6 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1982 | 10 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1982 | 10 | 8 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1982 | 10 | 9 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1982 | 10 | 10 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1982 | 10 | 11 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1982 | 10 | 12 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1982 | 10 | 13 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1982 | 10 | 14 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1982 | 10 | 15 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1982 | 10 | 16 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1982 | 10 | 17 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1982 | 10 | 18 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1982 | 10 | 19 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1982 | 10 | 20 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1982 | 10 | 21 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1982 | 10 | 22 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1982 | 10 | 23 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1982 | 10 | 24 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1982 | 10 | 25 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 10 | 26 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 10 | 27 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 10 | 28 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 10 | 29 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 10 | 30 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 10 | 31 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1982 | 11 | 1 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1982 | 11 | 2 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1982 | 11 | 3 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1982 | 11 | 4 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1982 | 11 | 5 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1982 | 11 | 6 | 235.102 | 15 | 220.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1982 | 11 | 7 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1982 | 11 | 8 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1982 | 11 | 9 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1982 | 11 | 10 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1982 | 11 | 11 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1982 | 11 | 12 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1982 | 11 | 13 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1982 | 11 | 14 | 381.3878 | 15 | 366.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1982 | 11 | 15 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1982 | 11 | 16 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1982 | 11 | 17 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1982 | 11 | 18 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1982 | 11 | 19 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1982 | 11 | 20 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1982 | 11 | 21 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1982 | 11 | 22 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1982 | 11 | 23 | 233.7959 | 15 | 218.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1982 | 11 | 24 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1982 | 11 | 25 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1982 | 11 | 26 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1982 | 11 | 27 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1982 | 11 | 28 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1982 | 11 | 29 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1982 | 11 | 30 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1982 | 12 | 1 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1982 | 12 | 2 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1982 | 12 | 3 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1982 | 12 | 4 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1982 | 12 | 5 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1982 | 12 | 6 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1982 | 12 | 7 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1982 | 12 | 8 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1982 | 12 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1982 | 12 | 10 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1982 | 12 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1982 | 12 | 12 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1982 | 12 | 13 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1982 | 12 | 14 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1982 | 12 | 15 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1982 | 12 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1982 | 12 | 17 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1982 | 12 | 18 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1982 | 12 | 19 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1982 | 12 | 20 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1982 | 12 | 21 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1982 | 12 | 22 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1982 | 12 | 23 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1982 | 12 | 24 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1982 | 12 | 25 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1982 | 12 | 26 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1982 | 12 | 27 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1982 | 12 | 28 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1982 | 12 | 29 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1982 | 12 | 30 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1982 | 12 | 31 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1983 | 1 | 1 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1983 | 1 | 2 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1983 | 1 | 3 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1983 | 1 | 4 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1983 | 1 | 5 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1983 | 1 | 6 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1983 | 1 | 7 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1983 | 1 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1983 | 1 | 9 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1983 | 1 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1983 | 1 | 11 | 705.3061 | 5 | 700.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1983 | 1 | 12 | 777.1429 | 5 | 772.1429 | 28.4457 | 139.3858 | 0.77441 | 27.6713 | 89.27% | 291.5932 | 274.0976 | 6578.3433
1983 | 1 | 13 | 359.1837 | 5 | 354.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1983 | 1 | 14 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1983 | 1 | 15 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1983 | 1 | 16 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1983 | 1 | 17 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1983 | 1 | 18 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1983 | 1 | 19 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1983 | 1 | 20 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1983 | 1 | 21 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1983 | 1 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1983 | 1 | 23 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1983 | 1 | 24 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1983 | 1 | 25 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1983 | 1 | 26 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1983 | 1 | 27 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1983 | 1 | 28 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1983 | 1 | 29 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1983 | 1 | 30 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1983 | 1 | 31 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1983 | 2 | 1 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1983 | 2 | 2 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1983 | 2 | 3 | 569.4694 | 5 | 564.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
1983 | 2 | 4 | 1502.0408 | 5 | 1497.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1983 | 2 | 5 | 796.7347 | 5 | 791.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1983 | 2 | 6 | 391.8367 | 5 | 386.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1983 | 2 | 7 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1983 | 2 | 8 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1983 | 2 | 9 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1983 | 2 | 10 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1983 | 2 | 11 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1983 | 2 | 12 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1983 | 2 | 13 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1983 | 2 | 14 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1983 | 2 | 15 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1983 | 2 | 16 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1983 | 2 | 17 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1983 | 2 | 18 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1983 | 2 | 19 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1983 | 2 | 20 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1983 | 2 | 21 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1983 | 2 | 22 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1983 | 2 | 23 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1983 | 2 | 24 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1983 | 2 | 25 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1983 | 2 | 26 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1983 | 2 | 27 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1983 | 2 | 28 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1983 | 3 | 1 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1983 | 3 | 2 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1983 | 3 | 3 | 724.898 | 25 | 699.898 | 28.5502 | 139.3858 | 0.77441 | 27.7758 | 89.27% | 292.6943 | 275.1327 | 6603.1838
1983 | 3 | 4 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1983 | 3 | 5 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1983 | 3 | 6 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1983 | 3 | 7 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1983 | 3 | 8 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1983 | 3 | 9 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1983 | 3 | 10 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1983 | 3 | 11 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1983 | 3 | 12 | 1029.2245 | 25 | 1004.2245 | 27.9416 | 139.3858 | 0.77441 | 27.1671 | 89.27% | 286.2805 | 269.1037 | 6458.4878
1983 | 3 | 13 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
1983 | 3 | 14 | 736.6531 | 25 | 711.6531 | 28.5267 | 139.3858 | 0.77441 | 27.7523 | 89.27% | 292.4466 | 274.8998 | 6597.5947
1983 | 3 | 15 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1983 | 3 | 16 | 549.8776 | 25 | 524.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
1983 | 3 | 17 | 466.2857 | 25 | 441.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
1983 | 3 | 18 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1983 | 3 | 19 | 894.6939 | 25 | 869.6939 | 28.2106 | 139.3858 | 0.77441 | 27.4362 | 89.27% | 289.1158 | 271.7688 | 6522.4521
1983 | 3 | 20 | 2703.6735 | 25 | 2678.6735 | 24.5927 | 0 | 0 | 24.5927 | 0% | 0 | 0 | 0
1983 | 3 | 21 | 1287.8367 | 25 | 1262.8367 | 27.4243 | 139.3858 | 0.77441 | 26.6499 | 89.27% | 280.8301 | 263.9803 | 6335.5272
1983 | 3 | 22 | 1711.0204 | 25 | 1686.0204 | 26.578 | 139.3858 | 0.77441 | 25.8035 | 89.27% | 271.9113 | 255.5966 | 6134.3189
1983 | 3 | 23 | 884.2449 | 25 | 859.2449 | 28.2315 | 139.3858 | 0.77441 | 27.4571 | 89.27% | 289.336 | 271.9758 | 6527.4202
1983 | 3 | 24 | 549.8776 | 25 | 524.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
1983 | 3 | 25 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1983 | 3 | 26 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1983 | 3 | 27 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1983 | 3 | 28 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1983 | 3 | 29 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1983 | 3 | 30 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1983 | 3 | 31 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1983 | 4 | 1 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1983 | 4 | 2 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1983 | 4 | 3 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1983 | 4 | 4 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1983 | 4 | 5 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1983 | 4 | 6 | 501.551 | 25 | 476.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
1983 | 4 | 7 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1983 | 4 | 8 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
1983 | 4 | 9 | 419.2653 | 25 | 394.2653 | 29.1615 | 139.3858 | 0.77441 | 28.3871 | 89.27% | 299.1357 | 281.1875 | 6748.5009
1983 | 4 | 10 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1983 | 4 | 11 | 583.8367 | 25 | 558.8367 | 28.8323 | 139.3858 | 0.77441 | 28.0579 | 89.27% | 295.6673 | 277.9272 | 6670.2533
1983 | 4 | 12 | 899.9184 | 25 | 874.9184 | 28.2002 | 139.3858 | 0.77441 | 27.4258 | 89.27% | 289.0057 | 271.6653 | 6519.9681
1983 | 4 | 13 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1983 | 4 | 14 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1983 | 4 | 15 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1983 | 4 | 16 | 411.4286 | 25 | 386.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1983 | 4 | 17 | 512 | 25 | 487 | 28.976 | 139.3858 | 0.77441 | 28.2016 | 89.27% | 297.1812 | 279.3504 | 6704.409
1983 | 4 | 18 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1983 | 4 | 19 | 512 | 25 | 487 | 28.976 | 139.3858 | 0.77441 | 28.2016 | 89.27% | 297.1812 | 279.3504 | 6704.409
1983 | 4 | 20 | 508.0816 | 25 | 483.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
1983 | 4 | 21 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1983 | 4 | 22 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1983 | 4 | 23 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1983 | 4 | 24 | 378.7755 | 25 | 353.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1983 | 4 | 25 | 2089.7959 | 25 | 2064.7959 | 25.8204 | 139.3858 | 0.77441 | 25.046 | 89.27% | 263.9284 | 248.0927 | 5954.2251
1983 | 4 | 26 | 1515.102 | 25 | 1490.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
1983 | 4 | 27 | 879.0204 | 25 | 854.0204 | 28.242 | 139.3858 | 0.77441 | 27.4675 | 89.27% | 289.4461 | 272.0793 | 6529.9043
1983 | 4 | 28 | 616.4898 | 25 | 591.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
1983 | 4 | 29 | 484.5714 | 25 | 459.5714 | 29.0309 | 139.3858 | 0.77441 | 28.2564 | 89.27% | 297.7593 | 279.8938 | 6717.4503
1983 | 4 | 30 | 505.4694 | 25 | 480.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
1983 | 5 | 1 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1983 | 5 | 2 | 552.4898 | 25 | 527.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
1983 | 5 | 3 | 779.7551 | 25 | 754.7551 | 28.4405 | 139.3858 | 0.77441 | 27.6661 | 89.27% | 291.5382 | 274.0459 | 6577.1013
1983 | 5 | 4 | 670.0408 | 25 | 645.0408 | 28.6599 | 139.3858 | 0.77441 | 27.8855 | 89.27% | 293.8505 | 276.2194 | 6629.2664
1983 | 5 | 5 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1983 | 5 | 6 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1983 | 5 | 7 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
1983 | 5 | 8 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1983 | 5 | 9 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1983 | 5 | 10 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1983 | 5 | 11 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1983 | 5 | 12 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1983 | 5 | 13 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1983 | 5 | 14 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1983 | 5 | 15 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1983 | 5 | 16 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1983 | 5 | 17 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1983 | 5 | 18 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1983 | 5 | 19 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1983 | 5 | 20 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1983 | 5 | 21 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1983 | 5 | 22 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1983 | 5 | 23 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1983 | 5 | 24 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1983 | 5 | 25 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1983 | 5 | 26 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1983 | 5 | 27 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1983 | 5 | 28 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1983 | 5 | 29 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1983 | 5 | 30 | 474.1224 | 25 | 449.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
1983 | 5 | 31 | 799.3469 | 25 | 774.3469 | 28.4013 | 139.3858 | 0.77441 | 27.6269 | 89.27% | 291.1253 | 273.6578 | 6567.7861
1983 | 6 | 1 | 560.3265 | 25 | 535.3265 | 28.8793 | 139.3858 | 0.77441 | 28.1049 | 89.27% | 296.1627 | 278.393 | 6681.4315
1983 | 6 | 2 | 382.6939 | 25 | 357.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
1983 | 6 | 3 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1983 | 6 | 4 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1983 | 6 | 5 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1983 | 6 | 6 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1983 | 6 | 7 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1983 | 6 | 8 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1983 | 6 | 9 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1983 | 6 | 10 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1983 | 6 | 11 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1983 | 6 | 12 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1983 | 6 | 13 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1983 | 6 | 14 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1983 | 6 | 15 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1983 | 6 | 16 | 628.2449 | 25 | 603.2449 | 28.7435 | 139.3858 | 0.77441 | 27.9691 | 89.27% | 294.7313 | 277.0475 | 6649.1388
1983 | 6 | 17 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1983 | 6 | 18 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1983 | 6 | 19 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1983 | 6 | 20 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1983 | 6 | 21 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1983 | 6 | 22 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1983 | 6 | 23 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1983 | 6 | 24 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1983 | 6 | 25 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1983 | 6 | 26 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1983 | 6 | 27 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1983 | 6 | 28 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1983 | 6 | 29 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1983 | 6 | 30 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1983 | 7 | 1 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1983 | 7 | 2 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1983 | 7 | 3 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1983 | 7 | 4 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1983 | 7 | 5 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1983 | 7 | 6 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1983 | 7 | 7 | 218.1224 | 5 | 213.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1983 | 7 | 8 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1983 | 7 | 9 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1983 | 7 | 10 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1983 | 7 | 11 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1983 | 7 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1983 | 7 | 13 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1983 | 7 | 14 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1983 | 7 | 15 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1983 | 7 | 16 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1983 | 7 | 17 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1983 | 7 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1983 | 7 | 19 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1983 | 7 | 20 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1983 | 7 | 21 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 7 | 22 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1983 | 7 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1983 | 7 | 24 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1983 | 7 | 25 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1983 | 7 | 26 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1983 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1983 | 7 | 28 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1983 | 7 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 7 | 30 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 7 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1983 | 8 | 1 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1983 | 8 | 2 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 8 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 8 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 8 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1983 | 8 | 6 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1983 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1983 | 8 | 8 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 8 | 9 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1983 | 8 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1983 | 8 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1983 | 8 | 12 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1983 | 8 | 13 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1983 | 8 | 14 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1983 | 8 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1983 | 8 | 16 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1983 | 8 | 17 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1983 | 8 | 18 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1983 | 8 | 19 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1983 | 8 | 20 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1983 | 8 | 21 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1983 | 8 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1983 | 8 | 23 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1983 | 8 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1983 | 8 | 25 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1983 | 8 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1983 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1983 | 8 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1983 | 8 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1983 | 8 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1983 | 8 | 31 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1983 | 9 | 1 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1983 | 9 | 2 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1983 | 9 | 3 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1983 | 9 | 4 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1983 | 9 | 5 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1983 | 9 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1983 | 9 | 7 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1983 | 9 | 8 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1983 | 9 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1983 | 9 | 10 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1983 | 9 | 11 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1983 | 9 | 12 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1983 | 9 | 13 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1983 | 9 | 14 | 10.7102 | 15 | 0 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1983 | 9 | 15 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1983 | 9 | 16 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1983 | 9 | 17 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1983 | 9 | 18 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1983 | 9 | 19 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1983 | 9 | 20 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1983 | 9 | 21 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1983 | 9 | 22 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1983 | 9 | 23 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1983 | 9 | 24 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1983 | 9 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1983 | 9 | 26 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1983 | 9 | 27 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1983 | 9 | 28 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1983 | 9 | 29 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1983 | 9 | 30 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1983 | 10 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1983 | 10 | 2 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1983 | 10 | 3 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1983 | 10 | 4 | 12.4082 | 15 | 0 | 29.9752 | 0 | 0 | 29.9752 | 0% | 0 | 0 | 0
1983 | 10 | 5 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1983 | 10 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1983 | 10 | 7 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1983 | 10 | 8 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1983 | 10 | 9 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1983 | 10 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1983 | 10 | 11 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1983 | 10 | 12 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1983 | 10 | 13 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1983 | 10 | 14 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1983 | 10 | 15 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1983 | 10 | 16 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1983 | 10 | 17 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1983 | 10 | 18 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1983 | 10 | 19 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1983 | 10 | 20 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1983 | 10 | 21 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1983 | 10 | 22 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1983 | 10 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1983 | 10 | 24 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1983 | 10 | 25 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1983 | 10 | 26 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1983 | 10 | 27 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1983 | 10 | 28 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1983 | 10 | 29 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1983 | 10 | 30 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1983 | 10 | 31 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1983 | 11 | 1 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1983 | 11 | 2 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1983 | 11 | 3 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1983 | 11 | 4 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1983 | 11 | 5 | 545.9592 | 15 | 530.9592 | 28.9081 | 139.3858 | 0.77441 | 28.1337 | 89.27% | 296.4655 | 278.6776 | 6688.2626
1983 | 11 | 6 | 1039.6735 | 15 | 1024.6735 | 27.9207 | 139.3858 | 0.77441 | 27.1462 | 89.27% | 286.0603 | 268.8967 | 6453.5197
1983 | 11 | 7 | 519.8367 | 15 | 504.8367 | 28.9603 | 139.3858 | 0.77441 | 28.1859 | 89.27% | 297.0161 | 279.1951 | 6700.6829
1983 | 11 | 8 | 327.8367 | 15 | 312.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
1983 | 11 | 9 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1983 | 11 | 10 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1983 | 11 | 11 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1983 | 11 | 12 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1983 | 11 | 13 | 275.5918 | 15 | 260.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1983 | 11 | 14 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1983 | 11 | 15 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1983 | 11 | 16 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1983 | 11 | 17 | 602.1224 | 15 | 587.1224 | 28.7958 | 139.3858 | 0.77441 | 28.0213 | 89.27% | 295.2819 | 277.565 | 6661.5591
1983 | 11 | 18 | 450.6122 | 15 | 435.6122 | 29.0988 | 139.3858 | 0.77441 | 28.3244 | 89.27% | 298.475 | 280.5665 | 6733.5966
1983 | 11 | 19 | 316.0816 | 15 | 301.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1983 | 11 | 20 | 241.6327 | 15 | 226.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1983 | 11 | 21 | 370.9388 | 15 | 355.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1983 | 11 | 22 | 634.7755 | 15 | 619.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
1983 | 11 | 23 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1983 | 11 | 24 | 318.6939 | 15 | 303.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1983 | 11 | 25 | 1065.7959 | 15 | 1050.7959 | 27.8684 | 139.3858 | 0.77441 | 27.094 | 89.27% | 285.5097 | 268.3791 | 6441.0994
1983 | 11 | 26 | 1593.4694 | 15 | 1578.4694 | 26.8131 | 139.3858 | 0.77441 | 26.0387 | 89.27% | 274.3887 | 257.9254 | 6190.2101
1983 | 11 | 27 | 730.1224 | 15 | 715.1224 | 28.5398 | 139.3858 | 0.77441 | 27.7653 | 89.27% | 292.5842 | 275.0292 | 6600.6998
1983 | 11 | 28 | 454.5306 | 15 | 439.5306 | 29.0909 | 139.3858 | 0.77441 | 28.3165 | 89.27% | 298.3924 | 280.4889 | 6731.7336
1983 | 11 | 29 | 436.2449 | 15 | 421.2449 | 29.1275 | 139.3858 | 0.77441 | 28.3531 | 89.27% | 298.7778 | 280.8512 | 6740.4278
1983 | 11 | 30 | 501.551 | 15 | 486.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
1983 | 12 | 1 | 384 | 5 | 379 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
1983 | 12 | 2 | 320 | 5 | 315 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1983 | 12 | 3 | 271.6735 | 5 | 266.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1983 | 12 | 4 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1983 | 12 | 5 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1983 | 12 | 6 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1983 | 12 | 7 | 787.5918 | 5 | 782.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
1983 | 12 | 8 | 630.8571 | 5 | 625.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
1983 | 12 | 9 | 385.3061 | 5 | 380.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1983 | 12 | 10 | 318.6939 | 5 | 313.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1983 | 12 | 11 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1983 | 12 | 12 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1983 | 12 | 13 | 623.0204 | 5 | 618.0204 | 28.754 | 139.3858 | 0.77441 | 27.9795 | 89.27% | 294.8414 | 277.151 | 6651.6229
1983 | 12 | 14 | 2285.7143 | 5 | 2280.7143 | 25.4286 | 139.3858 | 0.77441 | 24.6542 | 89.27% | 259.7993 | 244.2114 | 5861.0731
1983 | 12 | 15 | 1593.4694 | 5 | 1588.4694 | 26.8131 | 139.3858 | 0.77441 | 26.0387 | 89.27% | 274.3887 | 257.9254 | 6190.2101
1983 | 12 | 16 | 982.2041 | 5 | 977.2041 | 28.0356 | 139.3858 | 0.77441 | 27.2612 | 89.27% | 287.2715 | 270.0352 | 6480.8443
1983 | 12 | 17 | 655.6735 | 5 | 650.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1983 | 12 | 18 | 461.0612 | 5 | 456.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
1983 | 12 | 19 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1983 | 12 | 20 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1983 | 12 | 21 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1983 | 12 | 22 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1983 | 12 | 23 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1983 | 12 | 24 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1983 | 12 | 25 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1983 | 12 | 26 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1983 | 12 | 27 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1983 | 12 | 28 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1983 | 12 | 29 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1983 | 12 | 30 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1983 | 12 | 31 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1984 | 1 | 1 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1984 | 1 | 2 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1984 | 1 | 3 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1984 | 1 | 4 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1984 | 1 | 5 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1984 | 1 | 6 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1984 | 1 | 7 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1984 | 1 | 8 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1984 | 1 | 9 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1984 | 1 | 10 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1984 | 1 | 11 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1984 | 1 | 12 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1984 | 1 | 13 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1984 | 1 | 14 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1984 | 1 | 15 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1984 | 1 | 16 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1984 | 1 | 17 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1984 | 1 | 18 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1984 | 1 | 19 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1984 | 1 | 20 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1984 | 1 | 21 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1984 | 1 | 22 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1984 | 1 | 23 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1984 | 1 | 24 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1984 | 1 | 25 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1984 | 1 | 26 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1984 | 1 | 27 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1984 | 1 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1984 | 1 | 29 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1984 | 1 | 30 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1984 | 1 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1984 | 2 | 1 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1984 | 2 | 2 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1984 | 2 | 3 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1984 | 2 | 4 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1984 | 2 | 5 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1984 | 2 | 6 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1984 | 2 | 7 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1984 | 2 | 8 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1984 | 2 | 9 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1984 | 2 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1984 | 2 | 11 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1984 | 2 | 12 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1984 | 2 | 13 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1984 | 2 | 14 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1984 | 2 | 15 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1984 | 2 | 16 | 504.1633 | 5 | 499.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
1984 | 2 | 17 | 455.8367 | 5 | 450.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1984 | 2 | 18 | 382.6939 | 5 | 377.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
1984 | 2 | 19 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1984 | 2 | 20 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1984 | 2 | 21 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1984 | 2 | 22 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1984 | 2 | 23 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1984 | 2 | 24 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1984 | 2 | 25 | 391.8367 | 5 | 386.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1984 | 2 | 26 | 907.7551 | 5 | 902.7551 | 28.1845 | 139.3858 | 0.77441 | 27.4101 | 89.27% | 288.8405 | 271.5101 | 6516.242
1984 | 2 | 27 | 688.3265 | 5 | 683.3265 | 28.6233 | 139.3858 | 0.77441 | 27.8489 | 89.27% | 293.4651 | 275.8572 | 6620.5722
1984 | 2 | 28 | 370.9388 | 5 | 365.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1984 | 2 | 29 | 347.4286 | 5 | 342.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1984 | 3 | 1 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1984 | 3 | 2 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1984 | 3 | 3 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1984 | 3 | 4 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1984 | 3 | 5 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1984 | 3 | 6 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1984 | 3 | 7 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1984 | 3 | 8 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1984 | 3 | 9 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1984 | 3 | 10 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1984 | 3 | 11 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1984 | 3 | 12 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1984 | 3 | 13 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1984 | 3 | 14 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1984 | 3 | 15 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1984 | 3 | 16 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1984 | 3 | 17 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1984 | 3 | 18 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1984 | 3 | 19 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1984 | 3 | 20 | 689.6327 | 25 | 664.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
1984 | 3 | 21 | 741.8776 | 25 | 716.8776 | 28.5162 | 139.3858 | 0.77441 | 27.7418 | 89.27% | 292.3365 | 274.7963 | 6595.1107
1984 | 3 | 22 | 860.7347 | 25 | 835.7347 | 28.2785 | 139.3858 | 0.77441 | 27.5041 | 89.27% | 289.8315 | 272.4416 | 6538.5985
1984 | 3 | 23 | 817.6327 | 25 | 792.6327 | 28.3647 | 139.3858 | 0.77441 | 27.5903 | 89.27% | 290.7399 | 273.2955 | 6559.0919
1984 | 3 | 24 | 585.1429 | 25 | 560.1429 | 28.8297 | 139.3858 | 0.77441 | 28.0553 | 89.27% | 295.6397 | 277.9013 | 6669.6323
1984 | 3 | 25 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1984 | 3 | 26 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1984 | 3 | 27 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1984 | 3 | 28 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1984 | 3 | 29 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1984 | 3 | 30 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1984 | 3 | 31 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1984 | 4 | 1 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1984 | 4 | 2 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1984 | 4 | 3 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1984 | 4 | 4 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1984 | 4 | 5 | 812.4082 | 25 | 787.4082 | 28.3752 | 139.3858 | 0.77441 | 27.6008 | 89.27% | 290.85 | 273.399 | 6561.576
1984 | 4 | 6 | 5511.8367 | 25 | 5486.8367 | 18.9763 | 0 | 0 | 18.9763 | 0% | 0 | 0 | 0
1984 | 4 | 7 | 2377.1429 | 25 | 2352.1429 | 25.2457 | 139.3858 | 0.77441 | 24.4713 | 89.27% | 257.8724 | 242.4001 | 5817.6022
1984 | 4 | 8 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1984 | 4 | 9 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
1984 | 4 | 10 | 683.102 | 25 | 658.102 | 28.6338 | 139.3858 | 0.77441 | 27.8594 | 89.27% | 293.5752 | 275.9607 | 6623.0563
1984 | 4 | 11 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1984 | 4 | 12 | 624.3265 | 25 | 599.3265 | 28.7513 | 139.3858 | 0.77441 | 27.9769 | 89.27% | 294.8139 | 277.1251 | 6651.0019
1984 | 4 | 13 | 731.4286 | 25 | 706.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1984 | 4 | 14 | 730.1224 | 25 | 705.1224 | 28.5398 | 139.3858 | 0.77441 | 27.7653 | 89.27% | 292.5842 | 275.0292 | 6600.6998
1984 | 4 | 15 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
1984 | 4 | 16 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1984 | 4 | 17 | 1099.7551 | 25 | 1074.7551 | 27.8005 | 139.3858 | 0.77441 | 27.0261 | 89.27% | 284.794 | 267.7064 | 6424.9531
1984 | 4 | 18 | 927.3469 | 25 | 902.3469 | 28.1453 | 139.3858 | 0.77441 | 27.3709 | 89.27% | 288.4276 | 271.122 | 6506.9268
1984 | 4 | 19 | 728.8163 | 25 | 703.8163 | 28.5424 | 139.3858 | 0.77441 | 27.768 | 89.27% | 292.6117 | 275.055 | 6601.3208
1984 | 4 | 20 | 612.5714 | 25 | 587.5714 | 28.7749 | 139.3858 | 0.77441 | 28.0004 | 89.27% | 295.0617 | 277.358 | 6656.591
1984 | 4 | 21 | 508.0816 | 25 | 483.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
1984 | 4 | 22 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1984 | 4 | 23 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1984 | 4 | 24 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1984 | 4 | 25 | 664.8163 | 25 | 639.8163 | 28.6704 | 139.3858 | 0.77441 | 27.896 | 89.27% | 293.9606 | 276.3229 | 6631.7504
1984 | 4 | 26 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
1984 | 4 | 27 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1984 | 4 | 28 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1984 | 4 | 29 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1984 | 4 | 30 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1984 | 5 | 1 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1984 | 5 | 2 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1984 | 5 | 3 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1984 | 5 | 4 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1984 | 5 | 5 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1984 | 5 | 6 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1984 | 5 | 7 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1984 | 5 | 8 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1984 | 5 | 9 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
1984 | 5 | 10 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1984 | 5 | 11 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1984 | 5 | 12 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1984 | 5 | 13 | 551.1837 | 25 | 526.1837 | 28.8976 | 139.3858 | 0.77441 | 28.1232 | 89.27% | 296.3554 | 278.5741 | 6685.7786
1984 | 5 | 14 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1984 | 5 | 15 | 436.2449 | 25 | 411.2449 | 29.1275 | 139.3858 | 0.77441 | 28.3531 | 89.27% | 298.7778 | 280.8512 | 6740.4278
1984 | 5 | 16 | 348.7347 | 25 | 323.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1984 | 5 | 17 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1984 | 5 | 18 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1984 | 5 | 19 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1984 | 5 | 20 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1984 | 5 | 21 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1984 | 5 | 22 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1984 | 5 | 23 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1984 | 5 | 24 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1984 | 5 | 25 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1984 | 5 | 26 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1984 | 5 | 27 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1984 | 5 | 28 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1984 | 5 | 29 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1984 | 5 | 30 | 1502.0408 | 25 | 1477.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
1984 | 5 | 31 | 2403.2653 | 25 | 2378.2653 | 25.1935 | 139.3858 | 0.77441 | 24.4191 | 89.27% | 257.3219 | 241.8826 | 5805.1819
1984 | 6 | 1 | 2246.5306 | 25 | 2221.5306 | 25.5069 | 139.3858 | 0.77441 | 24.7325 | 89.27% | 260.6252 | 244.9876 | 5879.7035
1984 | 6 | 2 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
1984 | 6 | 3 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1984 | 6 | 4 | 817.6327 | 25 | 792.6327 | 28.3647 | 139.3858 | 0.77441 | 27.5903 | 89.27% | 290.7399 | 273.2955 | 6559.0919
1984 | 6 | 5 | 598.2041 | 25 | 573.2041 | 28.8036 | 139.3858 | 0.77441 | 28.0292 | 89.27% | 295.3645 | 277.6426 | 6663.4221
1984 | 6 | 6 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
1984 | 6 | 7 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
1984 | 6 | 8 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1984 | 6 | 9 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1984 | 6 | 10 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1984 | 6 | 11 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1984 | 6 | 12 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1984 | 6 | 13 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1984 | 6 | 14 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1984 | 6 | 15 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1984 | 6 | 16 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1984 | 6 | 17 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1984 | 6 | 18 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1984 | 6 | 19 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1984 | 6 | 20 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1984 | 6 | 21 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1984 | 6 | 22 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1984 | 6 | 23 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1984 | 6 | 24 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1984 | 6 | 25 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1984 | 6 | 26 | 809.7959 | 25 | 784.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
1984 | 6 | 27 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1984 | 6 | 28 | 356.5714 | 25 | 331.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1984 | 6 | 29 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1984 | 6 | 30 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1984 | 7 | 1 | 262.5306 | 5 | 257.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1984 | 7 | 2 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1984 | 7 | 3 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1984 | 7 | 4 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1984 | 7 | 5 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1984 | 7 | 6 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1984 | 7 | 7 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1984 | 7 | 8 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1984 | 7 | 9 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1984 | 7 | 10 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1984 | 7 | 11 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1984 | 7 | 12 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1984 | 7 | 13 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1984 | 7 | 14 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1984 | 7 | 15 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1984 | 7 | 16 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1984 | 7 | 17 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1984 | 7 | 18 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1984 | 7 | 19 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1984 | 7 | 20 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1984 | 7 | 21 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1984 | 7 | 22 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1984 | 7 | 23 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1984 | 7 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1984 | 7 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1984 | 7 | 26 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1984 | 7 | 27 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1984 | 7 | 28 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1984 | 7 | 29 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1984 | 7 | 30 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1984 | 7 | 31 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1984 | 8 | 1 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1984 | 8 | 2 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1984 | 8 | 3 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1984 | 8 | 4 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1984 | 8 | 5 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1984 | 8 | 6 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1984 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1984 | 8 | 8 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1984 | 8 | 9 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1984 | 8 | 10 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1984 | 8 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1984 | 8 | 12 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1984 | 8 | 13 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1984 | 8 | 14 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1984 | 8 | 15 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1984 | 8 | 16 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1984 | 8 | 17 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1984 | 8 | 18 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1984 | 8 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1984 | 8 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1984 | 8 | 21 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1984 | 8 | 22 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1984 | 8 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1984 | 8 | 24 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1984 | 8 | 25 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1984 | 8 | 26 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1984 | 8 | 27 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1984 | 8 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1984 | 8 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1984 | 8 | 30 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1984 | 8 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1984 | 9 | 1 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1984 | 9 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1984 | 9 | 3 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1984 | 9 | 4 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1984 | 9 | 5 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1984 | 9 | 6 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1984 | 9 | 7 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1984 | 9 | 8 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1984 | 9 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1984 | 9 | 10 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1984 | 9 | 11 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1984 | 9 | 12 | 12.4082 | 15 | 0 | 29.9752 | 0 | 0 | 29.9752 | 0% | 0 | 0 | 0
1984 | 9 | 13 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1984 | 9 | 14 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1984 | 9 | 15 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1984 | 9 | 16 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1984 | 9 | 17 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
1984 | 9 | 18 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1984 | 9 | 19 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1984 | 9 | 20 | 9.7959 | 15 | 0 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1984 | 9 | 21 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1984 | 9 | 22 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1984 | 9 | 23 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1984 | 9 | 24 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1984 | 9 | 25 | 10.7102 | 15 | 0 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1984 | 9 | 26 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1984 | 9 | 27 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1984 | 9 | 28 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1984 | 9 | 29 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1984 | 9 | 30 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1984 | 10 | 1 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1984 | 10 | 2 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1984 | 10 | 3 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1984 | 10 | 4 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1984 | 10 | 5 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1984 | 10 | 6 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1984 | 10 | 7 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1984 | 10 | 8 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1984 | 10 | 9 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1984 | 10 | 10 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1984 | 10 | 11 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1984 | 10 | 12 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1984 | 10 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1984 | 10 | 14 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1984 | 10 | 15 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1984 | 10 | 16 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1984 | 10 | 17 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1984 | 10 | 18 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1984 | 10 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1984 | 10 | 20 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1984 | 10 | 21 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1984 | 10 | 22 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1984 | 10 | 23 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1984 | 10 | 24 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1984 | 10 | 25 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1984 | 10 | 26 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1984 | 10 | 27 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1984 | 10 | 28 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1984 | 10 | 29 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1984 | 10 | 30 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1984 | 10 | 31 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1984 | 11 | 1 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1984 | 11 | 2 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1984 | 11 | 3 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1984 | 11 | 4 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1984 | 11 | 5 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1984 | 11 | 6 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1984 | 11 | 7 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1984 | 11 | 8 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1984 | 11 | 9 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1984 | 11 | 10 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1984 | 11 | 11 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1984 | 11 | 12 | 334.3673 | 15 | 319.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1984 | 11 | 13 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1984 | 11 | 14 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1984 | 11 | 15 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1984 | 11 | 16 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1984 | 11 | 17 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1984 | 11 | 18 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1984 | 11 | 19 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1984 | 11 | 20 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1984 | 11 | 21 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1984 | 11 | 22 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1984 | 11 | 23 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1984 | 11 | 24 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1984 | 11 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1984 | 11 | 26 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1984 | 11 | 27 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1984 | 11 | 28 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1984 | 11 | 29 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1984 | 11 | 30 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1984 | 12 | 1 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1984 | 12 | 2 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1984 | 12 | 3 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1984 | 12 | 4 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1984 | 12 | 5 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1984 | 12 | 6 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1984 | 12 | 7 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1984 | 12 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1984 | 12 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1984 | 12 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1984 | 12 | 11 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1984 | 12 | 12 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1984 | 12 | 13 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1984 | 12 | 14 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1984 | 12 | 15 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1984 | 12 | 16 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1984 | 12 | 17 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1984 | 12 | 18 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1984 | 12 | 19 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1984 | 12 | 20 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1984 | 12 | 21 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1984 | 12 | 22 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1984 | 12 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1984 | 12 | 24 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1984 | 12 | 25 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1984 | 12 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1984 | 12 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1984 | 12 | 28 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1984 | 12 | 29 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1984 | 12 | 30 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1984 | 12 | 31 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1985 | 1 | 1 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1985 | 1 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1985 | 1 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1985 | 1 | 4 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1985 | 1 | 5 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1985 | 1 | 6 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1985 | 1 | 7 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1985 | 1 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1985 | 1 | 9 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1985 | 1 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1985 | 1 | 11 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1985 | 1 | 12 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1985 | 1 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1985 | 1 | 14 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1985 | 1 | 15 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1985 | 1 | 16 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1985 | 1 | 17 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1985 | 1 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1985 | 1 | 19 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1985 | 1 | 20 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1985 | 1 | 21 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1985 | 1 | 22 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1985 | 1 | 23 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1985 | 1 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1985 | 1 | 25 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1985 | 1 | 26 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 1 | 27 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 1 | 28 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 1 | 29 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 1 | 30 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 1 | 31 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 2 | 1 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 2 | 2 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1985 | 2 | 3 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1985 | 2 | 4 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 6 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 7 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 8 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 9 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 10 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 12 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 2 | 13 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1985 | 2 | 14 | 502.8571 | 5 | 497.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
1985 | 2 | 15 | 357.8776 | 5 | 352.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1985 | 2 | 16 | 299.102 | 5 | 294.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
1985 | 2 | 17 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1985 | 2 | 18 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1985 | 2 | 19 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1985 | 2 | 20 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1985 | 2 | 21 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1985 | 2 | 22 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1985 | 2 | 23 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1985 | 2 | 24 | 292.5714 | 5 | 287.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1985 | 2 | 25 | 348.7347 | 5 | 343.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1985 | 2 | 26 | 317.3878 | 5 | 312.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1985 | 2 | 27 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1985 | 2 | 28 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1985 | 3 | 1 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1985 | 3 | 2 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1985 | 3 | 3 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1985 | 3 | 4 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1985 | 3 | 5 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1985 | 3 | 6 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1985 | 3 | 7 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1985 | 3 | 8 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1985 | 3 | 9 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1985 | 3 | 10 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1985 | 3 | 11 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1985 | 3 | 12 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
1985 | 3 | 13 | 1144.1633 | 25 | 1119.1633 | 27.7117 | 139.3858 | 0.77441 | 26.9373 | 89.27% | 283.8581 | 266.8266 | 6403.8386
1985 | 3 | 14 | 799.3469 | 25 | 774.3469 | 28.4013 | 139.3858 | 0.77441 | 27.6269 | 89.27% | 291.1253 | 273.6578 | 6567.7861
1985 | 3 | 15 | 539.4286 | 25 | 514.4286 | 28.9211 | 139.3858 | 0.77441 | 28.1467 | 89.27% | 296.6032 | 278.807 | 6691.3677
1985 | 3 | 16 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
1985 | 3 | 17 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1985 | 3 | 18 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1985 | 3 | 19 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1985 | 3 | 20 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1985 | 3 | 21 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1985 | 3 | 22 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1985 | 3 | 23 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1985 | 3 | 24 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1985 | 3 | 25 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1985 | 3 | 26 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1985 | 3 | 27 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1985 | 3 | 28 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1985 | 3 | 29 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1985 | 3 | 30 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1985 | 3 | 31 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1985 | 4 | 1 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1985 | 4 | 2 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1985 | 4 | 3 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1985 | 4 | 4 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1985 | 4 | 5 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1985 | 4 | 6 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1985 | 4 | 7 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1985 | 4 | 8 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1985 | 4 | 9 | 411.4286 | 25 | 386.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1985 | 4 | 10 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1985 | 4 | 11 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1985 | 4 | 12 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1985 | 4 | 13 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1985 | 4 | 14 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1985 | 4 | 15 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1985 | 4 | 16 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1985 | 4 | 17 | 407.5102 | 25 | 382.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1985 | 4 | 18 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1985 | 4 | 19 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1985 | 4 | 20 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1985 | 4 | 21 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1985 | 4 | 22 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1985 | 4 | 23 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1985 | 4 | 24 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1985 | 4 | 25 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1985 | 4 | 26 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1985 | 4 | 27 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1985 | 4 | 28 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1985 | 4 | 29 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1985 | 4 | 30 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1985 | 5 | 1 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1985 | 5 | 2 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1985 | 5 | 3 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1985 | 5 | 4 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1985 | 5 | 5 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1985 | 5 | 6 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1985 | 5 | 7 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1985 | 5 | 8 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1985 | 5 | 9 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1985 | 5 | 10 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1985 | 5 | 11 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1985 | 5 | 12 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1985 | 5 | 13 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1985 | 5 | 14 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1985 | 5 | 15 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1985 | 5 | 16 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1985 | 5 | 17 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1985 | 5 | 18 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1985 | 5 | 19 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1985 | 5 | 20 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1985 | 5 | 21 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1985 | 5 | 22 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1985 | 5 | 23 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1985 | 5 | 24 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1985 | 5 | 25 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1985 | 5 | 26 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1985 | 5 | 27 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1985 | 5 | 28 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1985 | 5 | 29 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1985 | 5 | 30 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1985 | 5 | 31 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1985 | 6 | 1 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1985 | 6 | 2 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1985 | 6 | 3 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1985 | 6 | 4 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1985 | 6 | 5 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1985 | 6 | 6 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1985 | 6 | 7 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1985 | 6 | 8 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1985 | 6 | 9 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1985 | 6 | 10 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1985 | 6 | 11 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1985 | 6 | 12 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1985 | 6 | 13 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1985 | 6 | 14 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1985 | 6 | 15 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1985 | 6 | 16 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1985 | 6 | 17 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1985 | 6 | 18 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1985 | 6 | 19 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1985 | 6 | 20 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1985 | 6 | 21 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1985 | 6 | 22 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1985 | 6 | 23 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1985 | 6 | 24 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1985 | 6 | 25 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1985 | 6 | 26 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1985 | 6 | 27 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1985 | 6 | 28 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1985 | 6 | 29 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1985 | 6 | 30 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1985 | 7 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1985 | 7 | 2 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1985 | 7 | 3 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1985 | 7 | 4 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1985 | 7 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1985 | 7 | 6 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1985 | 7 | 7 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1985 | 7 | 8 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1985 | 7 | 9 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1985 | 7 | 10 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1985 | 7 | 11 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1985 | 7 | 12 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1985 | 7 | 13 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1985 | 7 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1985 | 7 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1985 | 7 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1985 | 7 | 17 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1985 | 7 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1985 | 7 | 19 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1985 | 7 | 20 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1985 | 7 | 21 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1985 | 7 | 22 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1985 | 7 | 23 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1985 | 7 | 24 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1985 | 7 | 25 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1985 | 7 | 26 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1985 | 7 | 27 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1985 | 7 | 28 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1985 | 7 | 29 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1985 | 7 | 30 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1985 | 7 | 31 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1985 | 8 | 1 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1985 | 8 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1985 | 8 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1985 | 8 | 4 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1985 | 8 | 5 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1985 | 8 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1985 | 8 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1985 | 8 | 8 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1985 | 8 | 9 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1985 | 8 | 10 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1985 | 8 | 11 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1985 | 8 | 12 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1985 | 8 | 13 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1985 | 8 | 14 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1985 | 8 | 15 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1985 | 8 | 16 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1985 | 8 | 17 | 6.1388 | 5 | 1.1388 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1985 | 8 | 18 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1985 | 8 | 19 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1985 | 8 | 20 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1985 | 8 | 21 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1985 | 8 | 22 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1985 | 8 | 23 | 4.8327 | 5 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1985 | 8 | 24 | 4.8327 | 5 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1985 | 8 | 25 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1985 | 8 | 26 | 6.1388 | 5 | 1.1388 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1985 | 8 | 27 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1985 | 8 | 28 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1985 | 8 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1985 | 8 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1985 | 8 | 31 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1985 | 9 | 1 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1985 | 9 | 2 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1985 | 9 | 3 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1985 | 9 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1985 | 9 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1985 | 9 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1985 | 9 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1985 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1985 | 9 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1985 | 9 | 10 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1985 | 9 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1985 | 9 | 12 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1985 | 9 | 13 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1985 | 9 | 14 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1985 | 9 | 15 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1985 | 9 | 16 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1985 | 9 | 17 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1985 | 9 | 18 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1985 | 9 | 19 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1985 | 9 | 20 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1985 | 9 | 21 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1985 | 9 | 22 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1985 | 9 | 23 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1985 | 9 | 24 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1985 | 9 | 25 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1985 | 9 | 26 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1985 | 9 | 27 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1985 | 9 | 28 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1985 | 9 | 29 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1985 | 9 | 30 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1985 | 10 | 1 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1985 | 10 | 2 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1985 | 10 | 3 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1985 | 10 | 4 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1985 | 10 | 5 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1985 | 10 | 6 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1985 | 10 | 7 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1985 | 10 | 8 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1985 | 10 | 9 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1985 | 10 | 10 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1985 | 10 | 11 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1985 | 10 | 12 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1985 | 10 | 13 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1985 | 10 | 14 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1985 | 10 | 15 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1985 | 10 | 16 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1985 | 10 | 17 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1985 | 10 | 18 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1985 | 10 | 19 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1985 | 10 | 20 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1985 | 10 | 21 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1985 | 10 | 22 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1985 | 10 | 23 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1985 | 10 | 24 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1985 | 10 | 25 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1985 | 10 | 26 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1985 | 10 | 27 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1985 | 10 | 28 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1985 | 10 | 29 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1985 | 10 | 30 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1985 | 10 | 31 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1985 | 11 | 1 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1985 | 11 | 2 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1985 | 11 | 3 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1985 | 11 | 4 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1985 | 11 | 5 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1985 | 11 | 6 | 673.9592 | 15 | 658.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1985 | 11 | 7 | 663.5102 | 15 | 648.5102 | 28.673 | 139.3858 | 0.77441 | 27.8986 | 89.27% | 293.9881 | 276.3488 | 6632.3715
1985 | 11 | 8 | 389.2245 | 15 | 374.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1985 | 11 | 9 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1985 | 11 | 10 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1985 | 11 | 11 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1985 | 11 | 12 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1985 | 11 | 13 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1985 | 11 | 14 | 197.2245 | 15 | 182.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1985 | 11 | 15 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1985 | 11 | 16 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1985 | 11 | 17 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1985 | 11 | 18 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1985 | 11 | 19 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1985 | 11 | 20 | 288.6531 | 15 | 273.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1985 | 11 | 21 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1985 | 11 | 22 | 225.9592 | 15 | 210.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1985 | 11 | 23 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1985 | 11 | 24 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1985 | 11 | 25 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1985 | 11 | 26 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1985 | 11 | 27 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1985 | 11 | 28 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1985 | 11 | 29 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1985 | 11 | 30 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1985 | 12 | 1 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1985 | 12 | 2 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1985 | 12 | 3 | 356.5714 | 5 | 351.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1985 | 12 | 4 | 381.3878 | 5 | 376.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1985 | 12 | 5 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1985 | 12 | 6 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1985 | 12 | 7 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1985 | 12 | 8 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1985 | 12 | 9 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1985 | 12 | 10 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1985 | 12 | 11 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1985 | 12 | 12 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1985 | 12 | 13 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1985 | 12 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1985 | 12 | 15 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1985 | 12 | 16 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1985 | 12 | 17 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1985 | 12 | 18 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1985 | 12 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1985 | 12 | 20 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1985 | 12 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1985 | 12 | 22 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1985 | 12 | 23 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1985 | 12 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1985 | 12 | 25 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1985 | 12 | 26 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1985 | 12 | 27 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1985 | 12 | 28 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1985 | 12 | 29 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1985 | 12 | 30 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1985 | 12 | 31 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 1 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 2 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 3 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 5 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 6 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 7 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 10 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 11 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 12 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1986 | 1 | 13 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1986 | 1 | 14 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1986 | 1 | 15 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1986 | 1 | 16 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1986 | 1 | 17 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1986 | 1 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 1 | 19 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1986 | 1 | 20 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1986 | 1 | 21 | 438.8571 | 5 | 433.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1986 | 1 | 22 | 368.3265 | 5 | 363.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1986 | 1 | 23 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1986 | 1 | 24 | 214.2041 | 5 | 209.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1986 | 1 | 25 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1986 | 1 | 26 | 348.7347 | 5 | 343.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1986 | 1 | 27 | 4101.2245 | 5 | 4096.2245 | 21.7976 | 0 | 0 | 21.7976 | 0% | 0 | 0 | 0
1986 | 1 | 28 | 2625.3061 | 5 | 2620.3061 | 24.7494 | 0 | 0 | 24.7494 | 0% | 0 | 0 | 0
1986 | 1 | 29 | 1086.6939 | 5 | 1081.6939 | 27.8266 | 139.3858 | 0.77441 | 27.0522 | 89.27% | 285.0693 | 267.9651 | 6431.1632
1986 | 1 | 30 | 632.1633 | 5 | 627.1633 | 28.7357 | 139.3858 | 0.77441 | 27.9613 | 89.27% | 294.6487 | 276.9698 | 6647.2758
1986 | 1 | 31 | 438.8571 | 5 | 433.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
1986 | 2 | 1 | 338.2857 | 5 | 333.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1986 | 2 | 2 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1986 | 2 | 3 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1986 | 2 | 4 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1986 | 2 | 5 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1986 | 2 | 6 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1986 | 2 | 7 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1986 | 2 | 8 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1986 | 2 | 9 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1986 | 2 | 10 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1986 | 2 | 11 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1986 | 2 | 12 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1986 | 2 | 13 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1986 | 2 | 14 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1986 | 2 | 15 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1986 | 2 | 16 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1986 | 2 | 17 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1986 | 2 | 18 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1986 | 2 | 19 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1986 | 2 | 20 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1986 | 2 | 21 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 2 | 22 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1986 | 2 | 23 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1986 | 2 | 24 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1986 | 2 | 25 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1986 | 2 | 26 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1986 | 2 | 27 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1986 | 2 | 28 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1986 | 3 | 1 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1986 | 3 | 2 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1986 | 3 | 3 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1986 | 3 | 4 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1986 | 3 | 5 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1986 | 3 | 6 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1986 | 3 | 7 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1986 | 3 | 8 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1986 | 3 | 9 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1986 | 3 | 10 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1986 | 3 | 11 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1986 | 3 | 12 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1986 | 3 | 13 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1986 | 3 | 14 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1986 | 3 | 15 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1986 | 3 | 16 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1986 | 3 | 17 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1986 | 3 | 18 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1986 | 3 | 19 | 402.2857 | 25 | 377.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
1986 | 3 | 20 | 616.4898 | 25 | 591.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
1986 | 3 | 21 | 474.1224 | 25 | 449.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
1986 | 3 | 22 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1986 | 3 | 23 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1986 | 3 | 24 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1986 | 3 | 25 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1986 | 3 | 26 | 275.5918 | 25 | 250.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1986 | 3 | 27 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1986 | 3 | 28 | 1017.4694 | 25 | 992.4694 | 27.9651 | 139.3858 | 0.77441 | 27.1907 | 89.27% | 286.5282 | 269.3365 | 6464.0769
1986 | 3 | 29 | 1012.2449 | 25 | 987.2449 | 27.9755 | 139.3858 | 0.77441 | 27.2011 | 89.27% | 286.6383 | 269.44 | 6466.5609
1986 | 3 | 30 | 1227.7551 | 25 | 1202.7551 | 27.5445 | 139.3858 | 0.77441 | 26.7701 | 89.27% | 282.0964 | 265.1706 | 6364.0938
1986 | 3 | 31 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1986 | 4 | 1 | 1136.3265 | 25 | 1111.3265 | 27.7273 | 139.3858 | 0.77441 | 26.9529 | 89.27% | 284.0233 | 266.9819 | 6407.5647
1986 | 4 | 2 | 937.7959 | 25 | 912.7959 | 28.1244 | 139.3858 | 0.77441 | 27.35 | 89.27% | 288.2074 | 270.9149 | 6501.9587
1986 | 4 | 3 | 713.1429 | 25 | 688.1429 | 28.5737 | 139.3858 | 0.77441 | 27.7993 | 89.27% | 292.9421 | 275.3655 | 6608.773
1986 | 4 | 4 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1986 | 4 | 5 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1986 | 4 | 6 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1986 | 4 | 7 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1986 | 4 | 8 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1986 | 4 | 9 | 525.0612 | 25 | 500.0612 | 28.9499 | 139.3858 | 0.77441 | 28.1755 | 89.27% | 296.906 | 279.0916 | 6698.1989
1986 | 4 | 10 | 449.3061 | 25 | 424.3061 | 29.1014 | 139.3858 | 0.77441 | 28.327 | 89.27% | 298.5026 | 280.5924 | 6734.2176
1986 | 4 | 11 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1986 | 4 | 12 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1986 | 4 | 13 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1986 | 4 | 14 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1986 | 4 | 15 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1986 | 4 | 16 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1986 | 4 | 17 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1986 | 4 | 18 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1986 | 4 | 19 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1986 | 4 | 20 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1986 | 4 | 21 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1986 | 4 | 22 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1986 | 4 | 23 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1986 | 4 | 24 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1986 | 4 | 25 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1986 | 4 | 26 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1986 | 4 | 27 | 545.9592 | 25 | 520.9592 | 28.9081 | 139.3858 | 0.77441 | 28.1337 | 89.27% | 296.4655 | 278.6776 | 6688.2626
1986 | 4 | 28 | 407.5102 | 25 | 382.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1986 | 4 | 29 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1986 | 4 | 30 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1986 | 5 | 1 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1986 | 5 | 2 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1986 | 5 | 3 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1986 | 5 | 4 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1986 | 5 | 5 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1986 | 5 | 6 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1986 | 5 | 7 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1986 | 5 | 8 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1986 | 5 | 9 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1986 | 5 | 10 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1986 | 5 | 11 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1986 | 5 | 12 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1986 | 5 | 13 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1986 | 5 | 14 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1986 | 5 | 15 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1986 | 5 | 16 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1986 | 5 | 17 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1986 | 5 | 18 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1986 | 5 | 19 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1986 | 5 | 20 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1986 | 5 | 21 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1986 | 5 | 22 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1986 | 5 | 23 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1986 | 5 | 24 | 411.4286 | 25 | 386.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
1986 | 5 | 25 | 999.1837 | 25 | 974.1837 | 28.0016 | 139.3858 | 0.77441 | 27.2272 | 89.27% | 286.9136 | 269.6988 | 6472.7711
1986 | 5 | 26 | 506.7755 | 25 | 481.7755 | 28.9864 | 139.3858 | 0.77441 | 28.212 | 89.27% | 297.2914 | 279.4539 | 6706.893
1986 | 5 | 27 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1986 | 5 | 28 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1986 | 5 | 29 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1986 | 5 | 30 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1986 | 5 | 31 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1986 | 6 | 1 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1986 | 6 | 2 | 445.3878 | 25 | 420.3878 | 29.1092 | 139.3858 | 0.77441 | 28.3348 | 89.27% | 298.5851 | 280.67 | 6736.0807
1986 | 6 | 3 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1986 | 6 | 4 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1986 | 6 | 5 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1986 | 6 | 6 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1986 | 6 | 7 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1986 | 6 | 8 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1986 | 6 | 9 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1986 | 6 | 10 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1986 | 6 | 11 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1986 | 6 | 12 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1986 | 6 | 13 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1986 | 6 | 14 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1986 | 6 | 15 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1986 | 6 | 16 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1986 | 6 | 17 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1986 | 6 | 18 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1986 | 6 | 19 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1986 | 6 | 20 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1986 | 6 | 21 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1986 | 6 | 22 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1986 | 6 | 23 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1986 | 6 | 24 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1986 | 6 | 25 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1986 | 6 | 26 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1986 | 6 | 27 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1986 | 6 | 28 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1986 | 6 | 29 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1986 | 6 | 30 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1986 | 7 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1986 | 7 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1986 | 7 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1986 | 7 | 4 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1986 | 7 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1986 | 7 | 6 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1986 | 7 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1986 | 7 | 8 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1986 | 7 | 9 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1986 | 7 | 10 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1986 | 7 | 11 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1986 | 7 | 12 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1986 | 7 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1986 | 7 | 14 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1986 | 7 | 15 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1986 | 7 | 16 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1986 | 7 | 17 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1986 | 7 | 18 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1986 | 7 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1986 | 7 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1986 | 7 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1986 | 7 | 22 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1986 | 7 | 23 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1986 | 7 | 24 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1986 | 7 | 25 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1986 | 7 | 26 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1986 | 7 | 27 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 7 | 28 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1986 | 7 | 29 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1986 | 7 | 30 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1986 | 7 | 31 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1986 | 8 | 1 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1986 | 8 | 2 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1986 | 8 | 3 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1986 | 8 | 4 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1986 | 8 | 5 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1986 | 8 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1986 | 8 | 7 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1986 | 8 | 8 | 791.5102 | 5 | 786.5102 | 28.417 | 139.3858 | 0.77441 | 27.6426 | 89.27% | 291.2904 | 273.813 | 6571.5122
1986 | 8 | 9 | 1039.6735 | 5 | 1034.6735 | 27.9207 | 139.3858 | 0.77441 | 27.1462 | 89.27% | 286.0603 | 268.8967 | 6453.5197
1986 | 8 | 10 | 559.0204 | 5 | 554.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
1986 | 8 | 11 | 353.9592 | 5 | 348.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
1986 | 8 | 12 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1986 | 8 | 13 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1986 | 8 | 14 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1986 | 8 | 15 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 8 | 16 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1986 | 8 | 17 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1986 | 8 | 18 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1986 | 8 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1986 | 8 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1986 | 8 | 21 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1986 | 8 | 22 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1986 | 8 | 23 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1986 | 8 | 24 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1986 | 8 | 25 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1986 | 8 | 26 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1986 | 8 | 27 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 8 | 28 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1986 | 8 | 29 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1986 | 8 | 30 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1986 | 8 | 31 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1986 | 9 | 1 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1986 | 9 | 2 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1986 | 9 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1986 | 9 | 4 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1986 | 9 | 5 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1986 | 9 | 6 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1986 | 9 | 7 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1986 | 9 | 8 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1986 | 9 | 9 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1986 | 9 | 10 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1986 | 9 | 11 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1986 | 9 | 12 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1986 | 9 | 13 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1986 | 9 | 14 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1986 | 9 | 15 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1986 | 9 | 16 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1986 | 9 | 17 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1986 | 9 | 18 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1986 | 9 | 19 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1986 | 9 | 20 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1986 | 9 | 21 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1986 | 9 | 22 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1986 | 9 | 23 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1986 | 9 | 24 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1986 | 9 | 25 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1986 | 9 | 26 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1986 | 9 | 27 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1986 | 9 | 28 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1986 | 9 | 29 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1986 | 9 | 30 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1986 | 10 | 1 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1986 | 10 | 2 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1986 | 10 | 3 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1986 | 10 | 4 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1986 | 10 | 5 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1986 | 10 | 6 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1986 | 10 | 7 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1986 | 10 | 8 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1986 | 10 | 9 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1986 | 10 | 10 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1986 | 10 | 11 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1986 | 10 | 12 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1986 | 10 | 13 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1986 | 10 | 14 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1986 | 10 | 15 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1986 | 10 | 16 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1986 | 10 | 17 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1986 | 10 | 18 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1986 | 10 | 19 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1986 | 10 | 20 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1986 | 10 | 21 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1986 | 10 | 22 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1986 | 10 | 23 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1986 | 10 | 24 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1986 | 10 | 25 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1986 | 10 | 26 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1986 | 10 | 27 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1986 | 10 | 28 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1986 | 10 | 29 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1986 | 10 | 30 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1986 | 10 | 31 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1986 | 11 | 1 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1986 | 11 | 2 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1986 | 11 | 3 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1986 | 11 | 4 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1986 | 11 | 5 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1986 | 11 | 6 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1986 | 11 | 7 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1986 | 11 | 8 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1986 | 11 | 9 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1986 | 11 | 10 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1986 | 11 | 11 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1986 | 11 | 12 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1986 | 11 | 13 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1986 | 11 | 14 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1986 | 11 | 15 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1986 | 11 | 16 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1986 | 11 | 17 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1986 | 11 | 18 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1986 | 11 | 19 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1986 | 11 | 20 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1986 | 11 | 21 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1986 | 11 | 22 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1986 | 11 | 23 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1986 | 11 | 24 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1986 | 11 | 25 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1986 | 11 | 26 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1986 | 11 | 27 | 434.9388 | 15 | 419.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1986 | 11 | 28 | 359.1837 | 15 | 344.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1986 | 11 | 29 | 269.0612 | 15 | 254.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1986 | 11 | 30 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1986 | 12 | 1 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1986 | 12 | 2 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1986 | 12 | 3 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1986 | 12 | 4 | 715.7551 | 5 | 710.7551 | 28.5685 | 139.3858 | 0.77441 | 27.7941 | 89.27% | 292.887 | 275.3138 | 6607.5309
1986 | 12 | 5 | 420.5714 | 5 | 415.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1986 | 12 | 6 | 322.6122 | 5 | 317.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1986 | 12 | 7 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1986 | 12 | 8 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1986 | 12 | 9 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1986 | 12 | 10 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1986 | 12 | 11 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1986 | 12 | 12 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1986 | 12 | 13 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1986 | 12 | 14 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 12 | 15 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 12 | 16 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1986 | 12 | 17 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1986 | 12 | 18 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1986 | 12 | 19 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1986 | 12 | 20 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1986 | 12 | 21 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1986 | 12 | 22 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1986 | 12 | 23 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1986 | 12 | 24 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1986 | 12 | 25 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1986 | 12 | 26 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1986 | 12 | 27 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1986 | 12 | 28 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1986 | 12 | 29 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1986 | 12 | 30 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1986 | 12 | 31 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1987 | 1 | 1 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1987 | 1 | 2 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1987 | 1 | 3 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1987 | 1 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1987 | 1 | 5 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1987 | 1 | 6 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1987 | 1 | 7 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1987 | 1 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1987 | 1 | 9 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1987 | 1 | 10 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1987 | 1 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1987 | 1 | 12 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1987 | 1 | 13 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1987 | 1 | 14 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1987 | 1 | 15 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1987 | 1 | 16 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1987 | 1 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1987 | 1 | 18 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1987 | 1 | 19 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1987 | 1 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1987 | 1 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1987 | 1 | 22 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1987 | 1 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1987 | 1 | 24 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1987 | 1 | 25 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1987 | 1 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1987 | 1 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1987 | 1 | 28 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1987 | 1 | 29 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1987 | 1 | 30 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1987 | 1 | 31 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1987 | 2 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1987 | 2 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1987 | 2 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1987 | 2 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 2 | 5 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 2 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 2 | 7 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 2 | 8 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 2 | 9 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1987 | 2 | 10 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1987 | 2 | 11 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1987 | 2 | 12 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1987 | 2 | 13 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1987 | 2 | 14 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1987 | 2 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1987 | 2 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1987 | 2 | 17 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1987 | 2 | 18 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1987 | 2 | 19 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1987 | 2 | 20 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1987 | 2 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1987 | 2 | 22 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1987 | 2 | 23 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1987 | 2 | 24 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1987 | 2 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1987 | 2 | 26 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1987 | 2 | 27 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1987 | 2 | 28 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1987 | 3 | 1 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1987 | 3 | 2 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1987 | 3 | 3 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1987 | 3 | 4 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1987 | 3 | 5 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1987 | 3 | 6 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1987 | 3 | 7 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1987 | 3 | 8 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1987 | 3 | 9 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1987 | 3 | 10 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1987 | 3 | 11 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1987 | 3 | 12 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1987 | 3 | 13 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1987 | 3 | 14 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1987 | 3 | 15 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1987 | 3 | 16 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1987 | 3 | 17 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1987 | 3 | 18 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1987 | 3 | 19 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1987 | 3 | 20 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1987 | 3 | 21 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1987 | 3 | 22 | 613.8776 | 25 | 588.8776 | 28.7722 | 139.3858 | 0.77441 | 27.9978 | 89.27% | 295.0341 | 277.3321 | 6655.97
1987 | 3 | 23 | 705.3061 | 25 | 680.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1987 | 3 | 24 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
1987 | 3 | 25 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1987 | 3 | 26 | 830.6939 | 25 | 805.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
1987 | 3 | 27 | 957.3878 | 25 | 932.3878 | 28.0852 | 139.3858 | 0.77441 | 27.3108 | 89.27% | 287.7945 | 270.5268 | 6492.6435
1987 | 3 | 28 | 948.2449 | 25 | 923.2449 | 28.1035 | 139.3858 | 0.77441 | 27.3291 | 89.27% | 287.9872 | 270.7079 | 6496.9906
1987 | 3 | 29 | 898.6122 | 25 | 873.6122 | 28.2028 | 139.3858 | 0.77441 | 27.4284 | 89.27% | 289.0332 | 271.6912 | 6520.5891
1987 | 3 | 30 | 1089.3061 | 25 | 1064.3061 | 27.8214 | 139.3858 | 0.77441 | 27.047 | 89.27% | 285.0142 | 267.9134 | 6429.9212
1987 | 3 | 31 | 4166.5306 | 25 | 4141.5306 | 21.6669 | 0 | 0 | 21.6669 | 0% | 0 | 0 | 0
1987 | 4 | 1 | 8829.3878 | 25 | 8804.3878 | 12.3412 | 0 | 0 | 12.3412 | 0% | 0 | 0 | 0
1987 | 4 | 2 | 2860.4082 | 25 | 2835.4082 | 24.2792 | 0 | 0 | 24.2792 | 0% | 0 | 0 | 0
1987 | 4 | 3 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1987 | 4 | 4 | 1022.6939 | 25 | 997.6939 | 27.9546 | 139.3858 | 0.77441 | 27.1802 | 89.27% | 286.4181 | 269.233 | 6461.5928
1987 | 4 | 5 | 869.8776 | 25 | 844.8776 | 28.2602 | 139.3858 | 0.77441 | 27.4858 | 89.27% | 289.6388 | 272.2605 | 6534.2514
1987 | 4 | 6 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
1987 | 4 | 7 | 1345.3061 | 25 | 1320.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
1987 | 4 | 8 | 1068.4082 | 25 | 1043.4082 | 27.8632 | 139.3858 | 0.77441 | 27.0888 | 89.27% | 285.4547 | 268.3274 | 6439.8574
1987 | 4 | 9 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1987 | 4 | 10 | 539.4286 | 25 | 514.4286 | 28.9211 | 139.3858 | 0.77441 | 28.1467 | 89.27% | 296.6032 | 278.807 | 6691.3677
1987 | 4 | 11 | 440.1633 | 25 | 415.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
1987 | 4 | 12 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1987 | 4 | 13 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1987 | 4 | 14 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1987 | 4 | 15 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1987 | 4 | 16 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1987 | 4 | 17 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1987 | 4 | 18 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1987 | 4 | 19 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1987 | 4 | 20 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1987 | 4 | 21 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1987 | 4 | 22 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1987 | 4 | 23 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1987 | 4 | 24 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1987 | 4 | 25 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1987 | 4 | 26 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1987 | 4 | 27 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1987 | 4 | 28 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1987 | 4 | 29 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1987 | 4 | 30 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1987 | 5 | 1 | 393.1429 | 25 | 368.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1987 | 5 | 2 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1987 | 5 | 3 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1987 | 5 | 4 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1987 | 5 | 5 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1987 | 5 | 6 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
1987 | 5 | 7 | 467.5918 | 25 | 442.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1987 | 5 | 8 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1987 | 5 | 9 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1987 | 5 | 10 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1987 | 5 | 11 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1987 | 5 | 12 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1987 | 5 | 13 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1987 | 5 | 14 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1987 | 5 | 15 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1987 | 5 | 16 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1987 | 5 | 17 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1987 | 5 | 18 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1987 | 5 | 19 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1987 | 5 | 20 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1987 | 5 | 21 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1987 | 5 | 22 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1987 | 5 | 23 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1987 | 5 | 24 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1987 | 5 | 25 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1987 | 5 | 26 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1987 | 5 | 27 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1987 | 5 | 28 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1987 | 5 | 29 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1987 | 5 | 30 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1987 | 5 | 31 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1987 | 6 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1987 | 6 | 2 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1987 | 6 | 3 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1987 | 6 | 4 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1987 | 6 | 5 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1987 | 6 | 6 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1987 | 6 | 7 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1987 | 6 | 8 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1987 | 6 | 9 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1987 | 6 | 10 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1987 | 6 | 11 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1987 | 6 | 12 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1987 | 6 | 13 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1987 | 6 | 14 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1987 | 6 | 15 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1987 | 6 | 16 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1987 | 6 | 17 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1987 | 6 | 18 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1987 | 6 | 19 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1987 | 6 | 20 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1987 | 6 | 21 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1987 | 6 | 22 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1987 | 6 | 23 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1987 | 6 | 24 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1987 | 6 | 25 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1987 | 6 | 26 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1987 | 6 | 27 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1987 | 6 | 28 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1987 | 6 | 29 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1987 | 6 | 30 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1987 | 7 | 1 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1987 | 7 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1987 | 7 | 3 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1987 | 7 | 4 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1987 | 7 | 5 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1987 | 7 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1987 | 7 | 7 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 7 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1987 | 7 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1987 | 7 | 10 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1987 | 7 | 11 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1987 | 7 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1987 | 7 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1987 | 7 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1987 | 7 | 15 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1987 | 7 | 16 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1987 | 7 | 17 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1987 | 7 | 18 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1987 | 7 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1987 | 7 | 20 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1987 | 7 | 21 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1987 | 7 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1987 | 7 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1987 | 7 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1987 | 7 | 25 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1987 | 7 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1987 | 7 | 27 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1987 | 7 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1987 | 7 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1987 | 7 | 30 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1987 | 7 | 31 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1987 | 8 | 1 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1987 | 8 | 2 | 9.7959 | 5 | 4.7959 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1987 | 8 | 3 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1987 | 8 | 4 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1987 | 8 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1987 | 8 | 6 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1987 | 8 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1987 | 8 | 8 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1987 | 8 | 9 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1987 | 8 | 10 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1987 | 8 | 11 | 10.449 | 5 | 5.449 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1987 | 8 | 12 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1987 | 8 | 13 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1987 | 8 | 14 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1987 | 8 | 15 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1987 | 8 | 16 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1987 | 8 | 17 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1987 | 8 | 18 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1987 | 8 | 19 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1987 | 8 | 20 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1987 | 8 | 21 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1987 | 8 | 22 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1987 | 8 | 23 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1987 | 8 | 24 | 4.8327 | 5 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1987 | 8 | 25 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1987 | 8 | 26 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1987 | 8 | 27 | 4.5714 | 5 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1987 | 8 | 28 | 4.5714 | 5 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1987 | 8 | 29 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1987 | 8 | 30 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1987 | 8 | 31 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1987 | 9 | 1 | 7.3143 | 15 | 0 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1987 | 9 | 2 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1987 | 9 | 3 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1987 | 9 | 4 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1987 | 9 | 5 | 5.6163 | 15 | 0 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1987 | 9 | 6 | 5.3551 | 15 | 0 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1987 | 9 | 7 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1987 | 9 | 8 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1987 | 9 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1987 | 9 | 10 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1987 | 9 | 11 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1987 | 9 | 12 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1987 | 9 | 13 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1987 | 9 | 14 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1987 | 9 | 15 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1987 | 9 | 16 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1987 | 9 | 17 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1987 | 9 | 18 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1987 | 9 | 19 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1987 | 9 | 20 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1987 | 9 | 21 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1987 | 9 | 22 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1987 | 9 | 23 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1987 | 9 | 24 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1987 | 9 | 25 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1987 | 9 | 26 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1987 | 9 | 27 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1987 | 9 | 28 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1987 | 9 | 29 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1987 | 9 | 30 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1987 | 10 | 1 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1987 | 10 | 2 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1987 | 10 | 3 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1987 | 10 | 4 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1987 | 10 | 5 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1987 | 10 | 6 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1987 | 10 | 7 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1987 | 10 | 8 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1987 | 10 | 9 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1987 | 10 | 10 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1987 | 10 | 11 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1987 | 10 | 12 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1987 | 10 | 13 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1987 | 10 | 14 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1987 | 10 | 15 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1987 | 10 | 16 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1987 | 10 | 17 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1987 | 10 | 18 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1987 | 10 | 19 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1987 | 10 | 20 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1987 | 10 | 21 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1987 | 10 | 22 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1987 | 10 | 23 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1987 | 10 | 24 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1987 | 10 | 25 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1987 | 10 | 26 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1987 | 10 | 27 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1987 | 10 | 28 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1987 | 10 | 29 | 429.7143 | 15 | 414.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1987 | 10 | 30 | 304.3265 | 15 | 289.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1987 | 10 | 31 | 220.7347 | 15 | 205.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1987 | 11 | 1 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1987 | 11 | 2 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1987 | 11 | 3 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1987 | 11 | 4 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1987 | 11 | 5 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1987 | 11 | 6 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1987 | 11 | 7 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1987 | 11 | 8 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1987 | 11 | 9 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1987 | 11 | 10 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1987 | 11 | 11 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1987 | 11 | 12 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1987 | 11 | 13 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1987 | 11 | 14 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1987 | 11 | 15 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1987 | 11 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1987 | 11 | 17 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1987 | 11 | 18 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1987 | 11 | 19 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1987 | 11 | 20 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1987 | 11 | 21 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1987 | 11 | 22 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1987 | 11 | 23 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1987 | 11 | 24 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1987 | 11 | 25 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1987 | 11 | 26 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1987 | 11 | 27 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1987 | 11 | 28 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1987 | 11 | 29 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
1987 | 11 | 30 | 313.4694 | 15 | 298.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1987 | 12 | 1 | 1238.2041 | 5 | 1233.2041 | 27.5236 | 139.3858 | 0.77441 | 26.7492 | 89.27% | 281.8761 | 264.9636 | 6359.1257
1987 | 12 | 2 | 683.102 | 5 | 678.102 | 28.6338 | 139.3858 | 0.77441 | 27.8594 | 89.27% | 293.5752 | 275.9607 | 6623.0563
1987 | 12 | 3 | 408.8163 | 5 | 403.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
1987 | 12 | 4 | 312.1633 | 5 | 307.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1987 | 12 | 5 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1987 | 12 | 6 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1987 | 12 | 7 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1987 | 12 | 8 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1987 | 12 | 9 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1987 | 12 | 10 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1987 | 12 | 11 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1987 | 12 | 12 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1987 | 12 | 13 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1987 | 12 | 14 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1987 | 12 | 15 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1987 | 12 | 16 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1987 | 12 | 17 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1987 | 12 | 18 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1987 | 12 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1987 | 12 | 20 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1987 | 12 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1987 | 12 | 22 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1987 | 12 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1987 | 12 | 24 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1987 | 12 | 25 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1987 | 12 | 26 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1987 | 12 | 27 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1987 | 12 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1987 | 12 | 29 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1987 | 12 | 30 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1987 | 12 | 31 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1988 | 1 | 1 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1988 | 1 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1988 | 1 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1988 | 1 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1988 | 1 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1988 | 1 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1988 | 1 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1988 | 1 | 8 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1988 | 1 | 9 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1988 | 1 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1988 | 1 | 11 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1988 | 1 | 12 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1988 | 1 | 13 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1988 | 1 | 14 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1988 | 1 | 15 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1988 | 1 | 16 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1988 | 1 | 17 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1988 | 1 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1988 | 1 | 19 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1988 | 1 | 20 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1988 | 1 | 21 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1988 | 1 | 22 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1988 | 1 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1988 | 1 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1988 | 1 | 25 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1988 | 1 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1988 | 1 | 27 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1988 | 1 | 28 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1988 | 1 | 29 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1988 | 1 | 30 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1988 | 1 | 31 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1988 | 2 | 1 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1988 | 2 | 2 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1988 | 2 | 3 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1988 | 2 | 4 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1988 | 2 | 5 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1988 | 2 | 6 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1988 | 2 | 7 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1988 | 2 | 8 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1988 | 2 | 9 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1988 | 2 | 10 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1988 | 2 | 11 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1988 | 2 | 12 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1988 | 2 | 13 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1988 | 2 | 14 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1988 | 2 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1988 | 2 | 16 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1988 | 2 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1988 | 2 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1988 | 2 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1988 | 2 | 20 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1988 | 2 | 21 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1988 | 2 | 22 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1988 | 2 | 23 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1988 | 2 | 24 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1988 | 2 | 25 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1988 | 2 | 26 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1988 | 2 | 27 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1988 | 2 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1988 | 2 | 29 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1988 | 3 | 1 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1988 | 3 | 2 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1988 | 3 | 3 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1988 | 3 | 4 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1988 | 3 | 5 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1988 | 3 | 6 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1988 | 3 | 7 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1988 | 3 | 8 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1988 | 3 | 9 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1988 | 3 | 10 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1988 | 3 | 11 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1988 | 3 | 12 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1988 | 3 | 13 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1988 | 3 | 14 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1988 | 3 | 15 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1988 | 3 | 16 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1988 | 3 | 17 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1988 | 3 | 18 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1988 | 3 | 19 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1988 | 3 | 20 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1988 | 3 | 21 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1988 | 3 | 22 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1988 | 3 | 23 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1988 | 3 | 24 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1988 | 3 | 25 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1988 | 3 | 26 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1988 | 3 | 27 | 572.0816 | 25 | 547.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
1988 | 3 | 28 | 784.9796 | 25 | 759.9796 | 28.43 | 139.3858 | 0.77441 | 27.6556 | 89.27% | 291.4281 | 273.9424 | 6574.6172
1988 | 3 | 29 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1988 | 3 | 30 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1988 | 3 | 31 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
1988 | 4 | 1 | 607.3469 | 25 | 582.3469 | 28.7853 | 139.3858 | 0.77441 | 28.0109 | 89.27% | 295.1718 | 277.4615 | 6659.075
1988 | 4 | 2 | 582.5306 | 25 | 557.5306 | 28.8349 | 139.3858 | 0.77441 | 28.0605 | 89.27% | 295.6948 | 277.9531 | 6670.8743
1988 | 4 | 3 | 629.551 | 25 | 604.551 | 28.7409 | 139.3858 | 0.77441 | 27.9665 | 89.27% | 294.7038 | 277.0216 | 6648.5178
1988 | 4 | 4 | 598.2041 | 25 | 573.2041 | 28.8036 | 139.3858 | 0.77441 | 28.0292 | 89.27% | 295.3645 | 277.6426 | 6663.4221
1988 | 4 | 5 | 783.6735 | 25 | 758.6735 | 28.4327 | 139.3858 | 0.77441 | 27.6582 | 89.27% | 291.4556 | 273.9683 | 6575.2383
1988 | 4 | 6 | 907.7551 | 25 | 882.7551 | 28.1845 | 139.3858 | 0.77441 | 27.4101 | 89.27% | 288.8405 | 271.5101 | 6516.242
1988 | 4 | 7 | 594.2857 | 25 | 569.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
1988 | 4 | 8 | 458.449 | 25 | 433.449 | 29.0831 | 139.3858 | 0.77441 | 28.3087 | 89.27% | 298.3099 | 280.4113 | 6729.8705
1988 | 4 | 9 | 393.1429 | 25 | 368.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1988 | 4 | 10 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1988 | 4 | 11 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1988 | 4 | 12 | 356.5714 | 25 | 331.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1988 | 4 | 13 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1988 | 4 | 14 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1988 | 4 | 15 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1988 | 4 | 16 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1988 | 4 | 17 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1988 | 4 | 18 | 348.7347 | 25 | 323.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1988 | 4 | 19 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1988 | 4 | 20 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1988 | 4 | 21 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1988 | 4 | 22 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1988 | 4 | 23 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1988 | 4 | 24 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1988 | 4 | 25 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1988 | 4 | 26 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1988 | 4 | 27 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1988 | 4 | 28 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1988 | 4 | 29 | 1060.5714 | 25 | 1035.5714 | 27.8789 | 139.3858 | 0.77441 | 27.1044 | 89.27% | 285.6198 | 268.4826 | 6443.5835
1988 | 4 | 30 | 948.2449 | 25 | 923.2449 | 28.1035 | 139.3858 | 0.77441 | 27.3291 | 89.27% | 287.9872 | 270.7079 | 6496.9906
1988 | 5 | 1 | 559.0204 | 25 | 534.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
1988 | 5 | 2 | 489.7959 | 25 | 464.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
1988 | 5 | 3 | 436.2449 | 25 | 411.2449 | 29.1275 | 139.3858 | 0.77441 | 28.3531 | 89.27% | 298.7778 | 280.8512 | 6740.4278
1988 | 5 | 4 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1988 | 5 | 5 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1988 | 5 | 6 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1988 | 5 | 7 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1988 | 5 | 8 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1988 | 5 | 9 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1988 | 5 | 10 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1988 | 5 | 11 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1988 | 5 | 12 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1988 | 5 | 13 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1988 | 5 | 14 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1988 | 5 | 15 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1988 | 5 | 16 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1988 | 5 | 17 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1988 | 5 | 18 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1988 | 5 | 19 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1988 | 5 | 20 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1988 | 5 | 21 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1988 | 5 | 22 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1988 | 5 | 23 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1988 | 5 | 24 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1988 | 5 | 25 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1988 | 5 | 26 | 361.7959 | 25 | 336.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1988 | 5 | 27 | 275.5918 | 25 | 250.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1988 | 5 | 28 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1988 | 5 | 29 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1988 | 5 | 30 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1988 | 5 | 31 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1988 | 6 | 1 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1988 | 6 | 2 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1988 | 6 | 3 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1988 | 6 | 4 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1988 | 6 | 5 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1988 | 6 | 6 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1988 | 6 | 7 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1988 | 6 | 8 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1988 | 6 | 9 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1988 | 6 | 10 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1988 | 6 | 11 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1988 | 6 | 12 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1988 | 6 | 13 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1988 | 6 | 14 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1988 | 6 | 15 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1988 | 6 | 16 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1988 | 6 | 17 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1988 | 6 | 18 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1988 | 6 | 19 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1988 | 6 | 20 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1988 | 6 | 21 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1988 | 6 | 22 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1988 | 6 | 23 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1988 | 6 | 24 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1988 | 6 | 25 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1988 | 6 | 26 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1988 | 6 | 27 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1988 | 6 | 28 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1988 | 6 | 29 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1988 | 6 | 30 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1988 | 7 | 1 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1988 | 7 | 2 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1988 | 7 | 3 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1988 | 7 | 4 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1988 | 7 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1988 | 7 | 6 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1988 | 7 | 7 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1988 | 7 | 8 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1988 | 7 | 9 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1988 | 7 | 10 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1988 | 7 | 11 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1988 | 7 | 12 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1988 | 7 | 13 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1988 | 7 | 14 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1988 | 7 | 15 | 9.7959 | 5 | 4.7959 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1988 | 7 | 16 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1988 | 7 | 17 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1988 | 7 | 18 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1988 | 7 | 19 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1988 | 7 | 20 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1988 | 7 | 21 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1988 | 7 | 22 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1988 | 7 | 23 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1988 | 7 | 24 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1988 | 7 | 25 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1988 | 7 | 26 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1988 | 7 | 27 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1988 | 7 | 28 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1988 | 7 | 29 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1988 | 7 | 30 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1988 | 7 | 31 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1988 | 8 | 1 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1988 | 8 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1988 | 8 | 3 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1988 | 8 | 4 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1988 | 8 | 5 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1988 | 8 | 6 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1988 | 8 | 7 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1988 | 8 | 8 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1988 | 8 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1988 | 8 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1988 | 8 | 11 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1988 | 8 | 12 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1988 | 8 | 13 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1988 | 8 | 14 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1988 | 8 | 15 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1988 | 8 | 16 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1988 | 8 | 17 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1988 | 8 | 18 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1988 | 8 | 19 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1988 | 8 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1988 | 8 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1988 | 8 | 22 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1988 | 8 | 23 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1988 | 8 | 24 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1988 | 8 | 25 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1988 | 8 | 26 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1988 | 8 | 27 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1988 | 8 | 28 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1988 | 8 | 29 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1988 | 8 | 30 | 393.1429 | 5 | 388.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1988 | 8 | 31 | 279.5102 | 5 | 274.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1988 | 9 | 1 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1988 | 9 | 2 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1988 | 9 | 3 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1988 | 9 | 4 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1988 | 9 | 5 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1988 | 9 | 6 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1988 | 9 | 7 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1988 | 9 | 8 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1988 | 9 | 9 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1988 | 9 | 10 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1988 | 9 | 11 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1988 | 9 | 12 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1988 | 9 | 13 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1988 | 9 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1988 | 9 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1988 | 9 | 16 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1988 | 9 | 17 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1988 | 9 | 18 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1988 | 9 | 19 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1988 | 9 | 20 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1988 | 9 | 21 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1988 | 9 | 22 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1988 | 9 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1988 | 9 | 24 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1988 | 9 | 25 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1988 | 9 | 26 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1988 | 9 | 27 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1988 | 9 | 28 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1988 | 9 | 29 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1988 | 9 | 30 | 12.4082 | 15 | 0 | 29.9752 | 0 | 0 | 29.9752 | 0% | 0 | 0 | 0
1988 | 10 | 1 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1988 | 10 | 2 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1988 | 10 | 3 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1988 | 10 | 4 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1988 | 10 | 5 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1988 | 10 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1988 | 10 | 7 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1988 | 10 | 8 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1988 | 10 | 9 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1988 | 10 | 10 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1988 | 10 | 11 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1988 | 10 | 12 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1988 | 10 | 13 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1988 | 10 | 14 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1988 | 10 | 15 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1988 | 10 | 16 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1988 | 10 | 17 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1988 | 10 | 18 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1988 | 10 | 19 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1988 | 10 | 20 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1988 | 10 | 21 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1988 | 10 | 22 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1988 | 10 | 23 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1988 | 10 | 24 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1988 | 10 | 25 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1988 | 10 | 26 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1988 | 10 | 27 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1988 | 10 | 28 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1988 | 10 | 29 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1988 | 10 | 30 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1988 | 10 | 31 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1988 | 11 | 1 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1988 | 11 | 2 | 918.2041 | 15 | 903.2041 | 28.1636 | 139.3858 | 0.77441 | 27.3892 | 89.27% | 288.6203 | 271.3031 | 6511.2739
1988 | 11 | 3 | 903.8367 | 15 | 888.8367 | 28.1923 | 139.3858 | 0.77441 | 27.4179 | 89.27% | 288.9231 | 271.5877 | 6518.105
1988 | 11 | 4 | 461.0612 | 15 | 446.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
1988 | 11 | 5 | 325.2245 | 15 | 310.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1988 | 11 | 6 | 577.3061 | 15 | 562.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
1988 | 11 | 7 | 522.449 | 15 | 507.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
1988 | 11 | 8 | 421.8776 | 15 | 406.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1988 | 11 | 9 | 336.9796 | 15 | 321.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1988 | 11 | 10 | 279.5102 | 15 | 264.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1988 | 11 | 11 | 249.4694 | 15 | 234.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1988 | 11 | 12 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1988 | 11 | 13 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1988 | 11 | 14 | 367.0204 | 15 | 352.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1988 | 11 | 15 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1988 | 11 | 16 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1988 | 11 | 17 | 270.3673 | 15 | 255.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1988 | 11 | 18 | 321.3061 | 15 | 306.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
1988 | 11 | 19 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1988 | 11 | 20 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1988 | 11 | 21 | 414.0408 | 15 | 399.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1988 | 11 | 22 | 360.4898 | 15 | 345.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1988 | 11 | 23 | 291.2653 | 15 | 276.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1988 | 11 | 24 | 241.6327 | 15 | 226.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1988 | 11 | 25 | 239.0204 | 15 | 224.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1988 | 11 | 26 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1988 | 11 | 27 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1988 | 11 | 28 | 218.1224 | 15 | 203.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1988 | 11 | 29 | 313.4694 | 15 | 298.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1988 | 11 | 30 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1988 | 12 | 1 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1988 | 12 | 2 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1988 | 12 | 3 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1988 | 12 | 4 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1988 | 12 | 5 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1988 | 12 | 6 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1988 | 12 | 7 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1988 | 12 | 8 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1988 | 12 | 9 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1988 | 12 | 10 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1988 | 12 | 11 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1988 | 12 | 12 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1988 | 12 | 13 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1988 | 12 | 14 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1988 | 12 | 15 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1988 | 12 | 16 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1988 | 12 | 17 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1988 | 12 | 18 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1988 | 12 | 19 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1988 | 12 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1988 | 12 | 21 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1988 | 12 | 22 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1988 | 12 | 23 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1988 | 12 | 24 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1988 | 12 | 25 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1988 | 12 | 26 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1988 | 12 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1988 | 12 | 28 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1988 | 12 | 29 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1988 | 12 | 30 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1988 | 12 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1989 | 1 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1989 | 1 | 2 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1989 | 1 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1989 | 1 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1989 | 1 | 5 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 1 | 6 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 1 | 7 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 1 | 8 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 1 | 9 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 1 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 11 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1989 | 1 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1989 | 1 | 15 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 16 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 1 | 17 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 1 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 1 | 19 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 1 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 1 | 21 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 1 | 22 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 1 | 23 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 24 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 25 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1989 | 1 | 26 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1989 | 1 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 28 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 29 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 1 | 31 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 2 | 1 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 2 | 2 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1989 | 2 | 3 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1989 | 2 | 4 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 2 | 5 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 2 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1989 | 2 | 7 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1989 | 2 | 8 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1989 | 2 | 9 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1989 | 2 | 10 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1989 | 2 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1989 | 2 | 12 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1989 | 2 | 13 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1989 | 2 | 14 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1989 | 2 | 15 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1989 | 2 | 16 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1989 | 2 | 17 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1989 | 2 | 18 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1989 | 2 | 19 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1989 | 2 | 20 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1989 | 2 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1989 | 2 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 2 | 23 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1989 | 2 | 24 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1989 | 2 | 25 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1989 | 2 | 26 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1989 | 2 | 27 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1989 | 2 | 28 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1989 | 3 | 1 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1989 | 3 | 2 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1989 | 3 | 3 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1989 | 3 | 4 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1989 | 3 | 5 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1989 | 3 | 6 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1989 | 3 | 7 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1989 | 3 | 8 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1989 | 3 | 9 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1989 | 3 | 10 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1989 | 3 | 11 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1989 | 3 | 12 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1989 | 3 | 13 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1989 | 3 | 14 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1989 | 3 | 15 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1989 | 3 | 16 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1989 | 3 | 17 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1989 | 3 | 18 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1989 | 3 | 19 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1989 | 3 | 20 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1989 | 3 | 21 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1989 | 3 | 22 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1989 | 3 | 23 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1989 | 3 | 24 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1989 | 3 | 25 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1989 | 3 | 26 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1989 | 3 | 27 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1989 | 3 | 28 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1989 | 3 | 29 | 801.9592 | 25 | 776.9592 | 28.3961 | 139.3858 | 0.77441 | 27.6217 | 89.27% | 291.0702 | 273.606 | 6566.5441
1989 | 3 | 30 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1989 | 3 | 31 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
1989 | 4 | 1 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1989 | 4 | 2 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1989 | 4 | 3 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1989 | 4 | 4 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
1989 | 4 | 5 | 640 | 25 | 615 | 28.72 | 139.3858 | 0.77441 | 27.9456 | 89.27% | 294.4836 | 276.8146 | 6643.5497
1989 | 4 | 6 | 1606.5306 | 25 | 1581.5306 | 26.7869 | 139.3858 | 0.77441 | 26.0125 | 89.27% | 274.1135 | 257.6667 | 6184
1989 | 4 | 7 | 1985.3061 | 25 | 1960.3061 | 26.0294 | 139.3858 | 0.77441 | 25.255 | 89.27% | 266.1306 | 250.1628 | 6003.9061
1989 | 4 | 8 | 1260.4082 | 25 | 1235.4082 | 27.4792 | 139.3858 | 0.77441 | 26.7048 | 89.27% | 281.4082 | 264.5237 | 6348.5684
1989 | 4 | 9 | 717.0612 | 25 | 692.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1989 | 4 | 10 | 565.551 | 25 | 540.551 | 28.8689 | 139.3858 | 0.77441 | 28.0945 | 89.27% | 296.0526 | 278.2895 | 6678.9474
1989 | 4 | 11 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1989 | 4 | 12 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1989 | 4 | 13 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1989 | 4 | 14 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1989 | 4 | 15 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1989 | 4 | 16 | 419.2653 | 25 | 394.2653 | 29.1615 | 139.3858 | 0.77441 | 28.3871 | 89.27% | 299.1357 | 281.1875 | 6748.5009
1989 | 4 | 17 | 609.9592 | 25 | 584.9592 | 28.7801 | 139.3858 | 0.77441 | 28.0057 | 89.27% | 295.1167 | 277.4097 | 6657.833
1989 | 4 | 18 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1989 | 4 | 19 | 560.3265 | 25 | 535.3265 | 28.8793 | 139.3858 | 0.77441 | 28.1049 | 89.27% | 296.1627 | 278.393 | 6681.4315
1989 | 4 | 20 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1989 | 4 | 21 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1989 | 4 | 22 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1989 | 4 | 23 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1989 | 4 | 24 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1989 | 4 | 25 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1989 | 4 | 26 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1989 | 4 | 27 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1989 | 4 | 28 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1989 | 4 | 29 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1989 | 4 | 30 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1989 | 5 | 1 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1989 | 5 | 2 | 655.6735 | 25 | 630.6735 | 28.6887 | 139.3858 | 0.77441 | 27.9142 | 89.27% | 294.1533 | 276.5041 | 6636.0975
1989 | 5 | 3 | 1293.0612 | 25 | 1268.0612 | 27.4139 | 139.3858 | 0.77441 | 26.6395 | 89.27% | 280.72 | 263.8768 | 6333.0431
1989 | 5 | 4 | 637.3878 | 25 | 612.3878 | 28.7252 | 139.3858 | 0.77441 | 27.9508 | 89.27% | 294.5386 | 276.8663 | 6644.7917
1989 | 5 | 5 | 428.4082 | 25 | 403.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
1989 | 5 | 6 | 1055.3469 | 25 | 1030.3469 | 27.8893 | 139.3858 | 0.77441 | 27.1149 | 89.27% | 285.7299 | 268.5861 | 6446.0675
1989 | 5 | 7 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
1989 | 5 | 8 | 717.0612 | 25 | 692.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1989 | 5 | 9 | 484.5714 | 25 | 459.5714 | 29.0309 | 139.3858 | 0.77441 | 28.2564 | 89.27% | 297.7593 | 279.8938 | 6717.4503
1989 | 5 | 10 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1989 | 5 | 11 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1989 | 5 | 12 | 4336.3265 | 25 | 4311.3265 | 21.3273 | 0 | 0 | 21.3273 | 0% | 0 | 0 | 0
1989 | 5 | 13 | 2716.7347 | 25 | 2691.7347 | 24.5665 | 0 | 0 | 24.5665 | 0% | 0 | 0 | 0
1989 | 5 | 14 | 1217.3061 | 25 | 1192.3061 | 27.5654 | 139.3858 | 0.77441 | 26.791 | 89.27% | 282.3166 | 265.3776 | 6369.0619
1989 | 5 | 15 | 771.9184 | 25 | 746.9184 | 28.4562 | 139.3858 | 0.77441 | 27.6818 | 89.27% | 291.7033 | 274.2011 | 6580.8274
1989 | 5 | 16 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1989 | 5 | 17 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1989 | 5 | 18 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1989 | 5 | 19 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1989 | 5 | 20 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1989 | 5 | 21 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1989 | 5 | 22 | 501.551 | 25 | 476.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
1989 | 5 | 23 | 348.7347 | 25 | 323.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1989 | 5 | 24 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1989 | 5 | 25 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1989 | 5 | 26 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1989 | 5 | 27 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1989 | 5 | 28 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1989 | 5 | 29 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1989 | 5 | 30 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1989 | 5 | 31 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1989 | 6 | 1 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1989 | 6 | 2 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1989 | 6 | 3 | 340.898 | 25 | 315.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
1989 | 6 | 4 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1989 | 6 | 5 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1989 | 6 | 6 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1989 | 6 | 7 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1989 | 6 | 8 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1989 | 6 | 9 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
1989 | 6 | 10 | 867.2653 | 25 | 842.2653 | 28.2655 | 139.3858 | 0.77441 | 27.4911 | 89.27% | 289.6939 | 272.3122 | 6535.4934
1989 | 6 | 11 | 926.0408 | 25 | 901.0408 | 28.1479 | 139.3858 | 0.77441 | 27.3735 | 89.27% | 288.4551 | 271.1478 | 6507.5478
1989 | 6 | 12 | 480.6531 | 25 | 455.6531 | 29.0387 | 139.3858 | 0.77441 | 28.2643 | 89.27% | 297.8419 | 279.9714 | 6719.3133
1989 | 6 | 13 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1989 | 6 | 14 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1989 | 6 | 15 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1989 | 6 | 16 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1989 | 6 | 17 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
1989 | 6 | 18 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1989 | 6 | 19 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1989 | 6 | 20 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1989 | 6 | 21 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1989 | 6 | 22 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1989 | 6 | 23 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1989 | 6 | 24 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1989 | 6 | 25 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1989 | 6 | 26 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1989 | 6 | 27 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1989 | 6 | 28 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1989 | 6 | 29 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1989 | 6 | 30 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1989 | 7 | 1 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1989 | 7 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1989 | 7 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1989 | 7 | 4 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1989 | 7 | 5 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1989 | 7 | 6 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 7 | 7 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1989 | 7 | 8 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1989 | 7 | 9 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1989 | 7 | 10 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1989 | 7 | 11 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1989 | 7 | 12 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1989 | 7 | 13 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1989 | 7 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1989 | 7 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1989 | 7 | 16 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1989 | 7 | 17 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1989 | 7 | 18 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1989 | 7 | 19 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1989 | 7 | 20 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1989 | 7 | 21 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1989 | 7 | 22 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1989 | 7 | 23 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1989 | 7 | 24 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1989 | 7 | 25 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1989 | 7 | 26 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1989 | 7 | 27 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1989 | 7 | 28 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1989 | 7 | 29 | 10.7102 | 5 | 5.7102 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1989 | 7 | 30 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1989 | 7 | 31 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1989 | 8 | 1 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1989 | 8 | 2 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1989 | 8 | 3 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1989 | 8 | 4 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1989 | 8 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1989 | 8 | 6 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1989 | 8 | 7 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1989 | 8 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1989 | 8 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1989 | 8 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1989 | 8 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1989 | 8 | 12 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1989 | 8 | 13 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1989 | 8 | 14 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1989 | 8 | 15 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1989 | 8 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1989 | 8 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1989 | 8 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 8 | 19 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1989 | 8 | 20 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1989 | 8 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1989 | 8 | 22 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1989 | 8 | 23 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1989 | 8 | 24 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1989 | 8 | 25 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1989 | 8 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1989 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1989 | 8 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1989 | 8 | 29 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
1989 | 8 | 30 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1989 | 8 | 31 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1989 | 9 | 1 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1989 | 9 | 2 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1989 | 9 | 3 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1989 | 9 | 4 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1989 | 9 | 5 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1989 | 9 | 6 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1989 | 9 | 7 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1989 | 9 | 8 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1989 | 9 | 9 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1989 | 9 | 10 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1989 | 9 | 11 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1989 | 9 | 12 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1989 | 9 | 13 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1989 | 9 | 14 | 6.6612 | 15 | 0 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1989 | 9 | 15 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1989 | 9 | 16 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1989 | 9 | 17 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1989 | 9 | 18 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1989 | 9 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1989 | 9 | 20 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1989 | 9 | 21 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1989 | 9 | 22 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1989 | 9 | 23 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1989 | 9 | 24 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1989 | 9 | 25 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1989 | 9 | 26 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1989 | 9 | 27 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1989 | 9 | 28 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1989 | 9 | 29 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1989 | 9 | 30 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1989 | 10 | 1 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1989 | 10 | 2 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1989 | 10 | 3 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1989 | 10 | 4 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1989 | 10 | 5 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1989 | 10 | 6 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1989 | 10 | 7 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1989 | 10 | 8 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1989 | 10 | 9 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1989 | 10 | 10 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1989 | 10 | 11 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1989 | 10 | 12 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1989 | 10 | 13 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1989 | 10 | 14 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1989 | 10 | 15 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1989 | 10 | 16 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1989 | 10 | 17 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1989 | 10 | 18 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1989 | 10 | 19 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1989 | 10 | 20 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1989 | 10 | 21 | 731.4286 | 15 | 716.4286 | 28.5371 | 139.3858 | 0.77441 | 27.7627 | 89.27% | 292.5567 | 275.0033 | 6600.0788
1989 | 10 | 22 | 446.6939 | 15 | 431.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1989 | 10 | 23 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1989 | 10 | 24 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1989 | 10 | 25 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1989 | 10 | 26 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1989 | 10 | 27 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1989 | 10 | 28 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1989 | 10 | 29 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1989 | 10 | 30 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1989 | 10 | 31 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1989 | 11 | 1 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1989 | 11 | 2 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1989 | 11 | 3 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1989 | 11 | 4 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1989 | 11 | 5 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1989 | 11 | 6 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1989 | 11 | 7 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1989 | 11 | 8 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1989 | 11 | 9 | 269.0612 | 15 | 254.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1989 | 11 | 10 | 526.3673 | 15 | 511.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
1989 | 11 | 11 | 336.9796 | 15 | 321.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1989 | 11 | 12 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1989 | 11 | 13 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1989 | 11 | 14 | 160.6531 | 15 | 145.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1989 | 11 | 15 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1989 | 11 | 16 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1989 | 11 | 17 | 361.7959 | 15 | 346.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1989 | 11 | 18 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1989 | 11 | 19 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1989 | 11 | 20 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1989 | 11 | 21 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1989 | 11 | 22 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1989 | 11 | 23 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1989 | 11 | 24 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1989 | 11 | 25 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1989 | 11 | 26 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1989 | 11 | 27 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1989 | 11 | 28 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1989 | 11 | 29 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1989 | 11 | 30 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1989 | 12 | 1 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1989 | 12 | 2 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1989 | 12 | 3 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1989 | 12 | 4 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1989 | 12 | 5 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1989 | 12 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1989 | 12 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1989 | 12 | 8 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1989 | 12 | 9 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1989 | 12 | 10 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1989 | 12 | 11 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1989 | 12 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1989 | 12 | 13 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1989 | 12 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1989 | 12 | 15 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1989 | 12 | 16 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1989 | 12 | 17 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1989 | 12 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1989 | 12 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1989 | 12 | 20 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1989 | 12 | 21 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1989 | 12 | 22 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1989 | 12 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1989 | 12 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1989 | 12 | 25 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1989 | 12 | 26 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 12 | 27 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 12 | 28 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1989 | 12 | 29 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1989 | 12 | 30 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1989 | 12 | 31 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1990 | 1 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1990 | 1 | 2 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1990 | 1 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1990 | 1 | 4 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1990 | 1 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1990 | 1 | 6 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1990 | 1 | 7 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1990 | 1 | 8 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1990 | 1 | 9 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1990 | 1 | 10 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1990 | 1 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1990 | 1 | 12 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1990 | 1 | 13 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1990 | 1 | 14 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1990 | 1 | 15 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1990 | 1 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1990 | 1 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1990 | 1 | 18 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1990 | 1 | 19 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1990 | 1 | 20 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1990 | 1 | 21 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1990 | 1 | 22 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1990 | 1 | 23 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1990 | 1 | 24 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1990 | 1 | 25 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1990 | 1 | 26 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1990 | 1 | 27 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1990 | 1 | 28 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1990 | 1 | 29 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1990 | 1 | 30 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1990 | 1 | 31 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1990 | 2 | 1 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1990 | 2 | 2 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1990 | 2 | 3 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1990 | 2 | 4 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1990 | 2 | 5 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1990 | 2 | 6 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1990 | 2 | 7 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1990 | 2 | 8 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1990 | 2 | 9 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1990 | 2 | 10 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1990 | 2 | 11 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1990 | 2 | 12 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1990 | 2 | 13 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1990 | 2 | 14 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1990 | 2 | 15 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1990 | 2 | 16 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1990 | 2 | 17 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1990 | 2 | 18 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1990 | 2 | 19 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1990 | 2 | 20 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1990 | 2 | 21 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1990 | 2 | 22 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1990 | 2 | 23 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1990 | 2 | 24 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1990 | 2 | 25 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1990 | 2 | 26 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1990 | 2 | 27 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1990 | 2 | 28 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1990 | 3 | 1 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1990 | 3 | 2 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1990 | 3 | 3 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1990 | 3 | 4 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1990 | 3 | 5 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1990 | 3 | 6 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1990 | 3 | 7 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1990 | 3 | 8 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1990 | 3 | 9 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1990 | 3 | 10 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1990 | 3 | 11 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1990 | 3 | 12 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1990 | 3 | 13 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1990 | 3 | 14 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1990 | 3 | 15 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1990 | 3 | 16 | 467.5918 | 25 | 442.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
1990 | 3 | 17 | 757.551 | 25 | 732.551 | 28.4849 | 139.3858 | 0.77441 | 27.7105 | 89.27% | 292.0061 | 274.4858 | 6587.6585
1990 | 3 | 18 | 1515.102 | 25 | 1490.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
1990 | 3 | 19 | 1142.8571 | 25 | 1117.8571 | 27.7143 | 139.3858 | 0.77441 | 26.9399 | 89.27% | 283.8856 | 266.8525 | 6404.4596
1990 | 3 | 20 | 877.7143 | 25 | 852.7143 | 28.2446 | 139.3858 | 0.77441 | 27.4702 | 89.27% | 289.4736 | 272.1052 | 6530.5253
1990 | 3 | 21 | 1052.7347 | 25 | 1027.7347 | 27.8945 | 139.3858 | 0.77441 | 27.1201 | 89.27% | 285.785 | 268.6379 | 6447.3095
1990 | 3 | 22 | 775.8367 | 25 | 750.8367 | 28.4483 | 139.3858 | 0.77441 | 27.6739 | 89.27% | 291.6208 | 274.1235 | 6578.9643
1990 | 3 | 23 | 662.2041 | 25 | 637.2041 | 28.6756 | 139.3858 | 0.77441 | 27.9012 | 89.27% | 294.0156 | 276.3747 | 6632.9925
1990 | 3 | 24 | 582.5306 | 25 | 557.5306 | 28.8349 | 139.3858 | 0.77441 | 28.0605 | 89.27% | 295.6948 | 277.9531 | 6670.8743
1990 | 3 | 25 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1990 | 3 | 26 | 361.7959 | 25 | 336.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1990 | 3 | 27 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1990 | 3 | 28 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1990 | 3 | 29 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1990 | 3 | 30 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1990 | 3 | 31 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1990 | 4 | 1 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1990 | 4 | 2 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1990 | 4 | 3 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1990 | 4 | 4 | 997.8776 | 25 | 972.8776 | 28.0042 | 139.3858 | 0.77441 | 27.2298 | 89.27% | 286.9411 | 269.7247 | 6473.3921
1990 | 4 | 5 | 1234.2857 | 25 | 1209.2857 | 27.5314 | 139.3858 | 0.77441 | 26.757 | 89.27% | 281.9587 | 265.0412 | 6360.9887
1990 | 4 | 6 | 805.8776 | 25 | 780.8776 | 28.3882 | 139.3858 | 0.77441 | 27.6138 | 89.27% | 290.9876 | 273.5284 | 6564.681
1990 | 4 | 7 | 564.2449 | 25 | 539.2449 | 28.8715 | 139.3858 | 0.77441 | 28.0971 | 89.27% | 296.0802 | 278.3154 | 6679.5685
1990 | 4 | 8 | 425.7959 | 25 | 400.7959 | 29.1484 | 139.3858 | 0.77441 | 28.374 | 89.27% | 298.998 | 281.0582 | 6745.3959
1990 | 4 | 9 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1990 | 4 | 10 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1990 | 4 | 11 | 684.4082 | 25 | 659.4082 | 28.6312 | 139.3858 | 0.77441 | 27.8568 | 89.27% | 293.5477 | 275.9348 | 6622.4353
1990 | 4 | 12 | 603.4286 | 25 | 578.4286 | 28.7931 | 139.3858 | 0.77441 | 28.0187 | 89.27% | 295.2543 | 277.5391 | 6660.9381
1990 | 4 | 13 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1990 | 4 | 14 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1990 | 4 | 15 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1990 | 4 | 16 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1990 | 4 | 17 | 408.8163 | 25 | 383.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
1990 | 4 | 18 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1990 | 4 | 19 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1990 | 4 | 20 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1990 | 4 | 21 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1990 | 4 | 22 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1990 | 4 | 23 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1990 | 4 | 24 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1990 | 4 | 25 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1990 | 4 | 26 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1990 | 4 | 27 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1990 | 4 | 28 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1990 | 4 | 29 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1990 | 4 | 30 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1990 | 5 | 1 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1990 | 5 | 2 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1990 | 5 | 3 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1990 | 5 | 4 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1990 | 5 | 5 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1990 | 5 | 6 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1990 | 5 | 7 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1990 | 5 | 8 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1990 | 5 | 9 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1990 | 5 | 10 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1990 | 5 | 11 | 987.4286 | 25 | 962.4286 | 28.0251 | 139.3858 | 0.77441 | 27.2507 | 89.27% | 287.1614 | 269.9317 | 6478.3602
1990 | 5 | 12 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1990 | 5 | 13 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1990 | 5 | 14 | 1158.5306 | 25 | 1133.5306 | 27.6829 | 139.3858 | 0.77441 | 26.9085 | 89.27% | 283.5553 | 266.542 | 6397.0075
1990 | 5 | 15 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
1990 | 5 | 16 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
1990 | 5 | 17 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1990 | 5 | 18 | 419.2653 | 25 | 394.2653 | 29.1615 | 139.3858 | 0.77441 | 28.3871 | 89.27% | 299.1357 | 281.1875 | 6748.5009
1990 | 5 | 19 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1990 | 5 | 20 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1990 | 5 | 21 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1990 | 5 | 22 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1990 | 5 | 23 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1990 | 5 | 24 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1990 | 5 | 25 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1990 | 5 | 26 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1990 | 5 | 27 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1990 | 5 | 28 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1990 | 5 | 29 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1990 | 5 | 30 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1990 | 5 | 31 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1990 | 6 | 1 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1990 | 6 | 2 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1990 | 6 | 3 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1990 | 6 | 4 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1990 | 6 | 5 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1990 | 6 | 6 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1990 | 6 | 7 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1990 | 6 | 8 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1990 | 6 | 9 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1990 | 6 | 10 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1990 | 6 | 11 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1990 | 6 | 12 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1990 | 6 | 13 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1990 | 6 | 14 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1990 | 6 | 15 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1990 | 6 | 16 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1990 | 6 | 17 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1990 | 6 | 18 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1990 | 6 | 19 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1990 | 6 | 20 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1990 | 6 | 21 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1990 | 6 | 22 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1990 | 6 | 23 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1990 | 6 | 24 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1990 | 6 | 25 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1990 | 6 | 26 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1990 | 6 | 27 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1990 | 6 | 28 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1990 | 6 | 29 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1990 | 6 | 30 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1990 | 7 | 1 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1990 | 7 | 2 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1990 | 7 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1990 | 7 | 4 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1990 | 7 | 5 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1990 | 7 | 6 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1990 | 7 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1990 | 7 | 8 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1990 | 7 | 9 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1990 | 7 | 10 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1990 | 7 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1990 | 7 | 12 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1990 | 7 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1990 | 7 | 14 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1990 | 7 | 15 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1990 | 7 | 16 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1990 | 7 | 17 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1990 | 7 | 18 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
1990 | 7 | 19 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1990 | 7 | 20 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1990 | 7 | 21 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1990 | 7 | 22 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1990 | 7 | 23 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1990 | 7 | 24 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1990 | 7 | 25 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1990 | 7 | 26 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
1990 | 7 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1990 | 7 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1990 | 7 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1990 | 7 | 30 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1990 | 7 | 31 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1990 | 8 | 1 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1990 | 8 | 2 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1990 | 8 | 3 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1990 | 8 | 4 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1990 | 8 | 5 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1990 | 8 | 6 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1990 | 8 | 7 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1990 | 8 | 8 | 278.2041 | 5 | 273.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1990 | 8 | 9 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1990 | 8 | 10 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1990 | 8 | 11 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1990 | 8 | 12 | 710.5306 | 5 | 705.5306 | 28.5789 | 139.3858 | 0.77441 | 27.8045 | 89.27% | 292.9971 | 275.4173 | 6610.015
1990 | 8 | 13 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1990 | 8 | 14 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1990 | 8 | 15 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1990 | 8 | 16 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1990 | 8 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1990 | 8 | 18 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1990 | 8 | 19 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1990 | 8 | 20 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1990 | 8 | 21 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1990 | 8 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1990 | 8 | 23 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1990 | 8 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1990 | 8 | 25 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1990 | 8 | 26 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1990 | 8 | 27 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1990 | 8 | 28 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1990 | 8 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1990 | 8 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1990 | 8 | 31 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1990 | 9 | 1 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1990 | 9 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1990 | 9 | 3 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1990 | 9 | 4 | 10.3184 | 15 | 0 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1990 | 9 | 5 | 9.7959 | 15 | 0 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1990 | 9 | 6 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1990 | 9 | 7 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1990 | 9 | 8 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1990 | 9 | 9 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1990 | 9 | 10 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1990 | 9 | 11 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1990 | 9 | 12 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1990 | 9 | 13 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1990 | 9 | 14 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1990 | 9 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1990 | 9 | 16 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1990 | 9 | 17 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1990 | 9 | 18 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1990 | 9 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1990 | 9 | 20 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1990 | 9 | 21 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1990 | 9 | 22 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1990 | 9 | 23 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1990 | 9 | 24 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1990 | 9 | 25 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1990 | 9 | 26 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1990 | 9 | 27 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1990 | 9 | 28 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1990 | 9 | 29 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1990 | 9 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1990 | 10 | 1 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1990 | 10 | 2 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1990 | 10 | 3 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1990 | 10 | 4 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1990 | 10 | 5 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1990 | 10 | 6 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1990 | 10 | 7 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1990 | 10 | 8 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1990 | 10 | 9 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1990 | 10 | 10 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1990 | 10 | 11 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1990 | 10 | 12 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1990 | 10 | 13 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1990 | 10 | 14 | 549.8776 | 15 | 534.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
1990 | 10 | 15 | 356.5714 | 15 | 341.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1990 | 10 | 16 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1990 | 10 | 17 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1990 | 10 | 18 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1990 | 10 | 19 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1990 | 10 | 20 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1990 | 10 | 21 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1990 | 10 | 22 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1990 | 10 | 23 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1990 | 10 | 24 | 1034.449 | 15 | 1019.449 | 27.9311 | 139.3858 | 0.77441 | 27.1567 | 89.27% | 286.1704 | 269.0002 | 6456.0037
1990 | 10 | 25 | 1099.7551 | 15 | 1084.7551 | 27.8005 | 139.3858 | 0.77441 | 27.0261 | 89.27% | 284.794 | 267.7064 | 6424.9531
1990 | 10 | 26 | 478.0408 | 15 | 463.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
1990 | 10 | 27 | 317.3878 | 15 | 302.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1990 | 10 | 28 | 244.2449 | 15 | 229.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1990 | 10 | 29 | 707.9184 | 15 | 692.9184 | 28.5842 | 139.3858 | 0.77441 | 27.8098 | 89.27% | 293.0522 | 275.469 | 6611.257
1990 | 10 | 30 | 549.8776 | 15 | 534.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
1990 | 10 | 31 | 363.102 | 15 | 348.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
1990 | 11 | 1 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1990 | 11 | 2 | 223.3469 | 15 | 208.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1990 | 11 | 3 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1990 | 11 | 4 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1990 | 11 | 5 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
1990 | 11 | 6 | 254.6939 | 15 | 239.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1990 | 11 | 7 | 359.1837 | 15 | 344.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1990 | 11 | 8 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1990 | 11 | 9 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1990 | 11 | 10 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1990 | 11 | 11 | 1097.1429 | 15 | 1082.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
1990 | 11 | 12 | 660.898 | 15 | 645.898 | 28.6782 | 139.3858 | 0.77441 | 27.9038 | 89.27% | 294.0432 | 276.4006 | 6633.6135
1990 | 11 | 13 | 398.3673 | 15 | 383.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1990 | 11 | 14 | 295.1837 | 15 | 280.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1990 | 11 | 15 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1990 | 11 | 16 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1990 | 11 | 17 | 220.7347 | 15 | 205.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1990 | 11 | 18 | 291.2653 | 15 | 276.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1990 | 11 | 19 | 246.8571 | 15 | 231.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
1990 | 11 | 20 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1990 | 11 | 21 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1990 | 11 | 22 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1990 | 11 | 23 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1990 | 11 | 24 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1990 | 11 | 25 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1990 | 11 | 26 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1990 | 11 | 27 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1990 | 11 | 28 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1990 | 11 | 29 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
1990 | 11 | 30 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1990 | 12 | 1 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1990 | 12 | 2 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1990 | 12 | 3 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1990 | 12 | 4 | 359.1837 | 5 | 354.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1990 | 12 | 5 | 1054.0408 | 5 | 1049.0408 | 27.8919 | 139.3858 | 0.77441 | 27.1175 | 89.27% | 285.7575 | 268.612 | 6446.6885
1990 | 12 | 6 | 551.1837 | 5 | 546.1837 | 28.8976 | 139.3858 | 0.77441 | 28.1232 | 89.27% | 296.3554 | 278.5741 | 6685.7786
1990 | 12 | 7 | 369.6327 | 5 | 364.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1990 | 12 | 8 | 291.2653 | 5 | 286.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1990 | 12 | 9 | 249.4694 | 5 | 244.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1990 | 12 | 10 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1990 | 12 | 11 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1990 | 12 | 12 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1990 | 12 | 13 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1990 | 12 | 14 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1990 | 12 | 15 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1990 | 12 | 16 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1990 | 12 | 17 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1990 | 12 | 18 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1990 | 12 | 19 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1990 | 12 | 20 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1990 | 12 | 21 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1990 | 12 | 22 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1990 | 12 | 23 | 497.6327 | 5 | 492.6327 | 29.0047 | 139.3858 | 0.77441 | 28.2303 | 89.27% | 297.484 | 279.635 | 6711.2401
1990 | 12 | 24 | 1515.102 | 5 | 1510.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
1990 | 12 | 25 | 1223.8367 | 5 | 1218.8367 | 27.5523 | 139.3858 | 0.77441 | 26.7779 | 89.27% | 282.1789 | 265.2482 | 6365.9568
1990 | 12 | 26 | 617.7959 | 5 | 612.7959 | 28.7644 | 139.3858 | 0.77441 | 27.99 | 89.27% | 294.9515 | 277.2545 | 6654.1069
1990 | 12 | 27 | 356.5714 | 5 | 351.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1990 | 12 | 28 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1990 | 12 | 29 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1990 | 12 | 30 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1990 | 12 | 31 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1991 | 1 | 1 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1991 | 1 | 2 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1991 | 1 | 3 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1991 | 1 | 4 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1991 | 1 | 5 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1991 | 1 | 6 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1991 | 1 | 7 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1991 | 1 | 8 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1991 | 1 | 9 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1991 | 1 | 10 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1991 | 1 | 11 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1991 | 1 | 12 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1991 | 1 | 13 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1991 | 1 | 14 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1991 | 1 | 15 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1991 | 1 | 16 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1991 | 1 | 17 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1991 | 1 | 18 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1991 | 1 | 19 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1991 | 1 | 20 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1991 | 1 | 21 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1991 | 1 | 22 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1991 | 1 | 23 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1991 | 1 | 24 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1991 | 1 | 25 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1991 | 1 | 26 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1991 | 1 | 27 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1991 | 1 | 28 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1991 | 1 | 29 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1991 | 1 | 30 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1991 | 1 | 31 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1991 | 2 | 1 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1991 | 2 | 2 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1991 | 2 | 3 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1991 | 2 | 4 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1991 | 2 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1991 | 2 | 6 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1991 | 2 | 7 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1991 | 2 | 8 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1991 | 2 | 9 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1991 | 2 | 10 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1991 | 2 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1991 | 2 | 12 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1991 | 2 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1991 | 2 | 14 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1991 | 2 | 15 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1991 | 2 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1991 | 2 | 17 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1991 | 2 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1991 | 2 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1991 | 2 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1991 | 2 | 21 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1991 | 2 | 22 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1991 | 2 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1991 | 2 | 24 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1991 | 2 | 25 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1991 | 2 | 26 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1991 | 2 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1991 | 2 | 28 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1991 | 3 | 1 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1991 | 3 | 2 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1991 | 3 | 3 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1991 | 3 | 4 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1991 | 3 | 5 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1991 | 3 | 6 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1991 | 3 | 7 | 407.5102 | 25 | 382.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1991 | 3 | 8 | 646.5306 | 25 | 621.5306 | 28.7069 | 139.3858 | 0.77441 | 27.9325 | 89.27% | 294.346 | 276.6852 | 6640.4446
1991 | 3 | 9 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1991 | 3 | 10 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1991 | 3 | 11 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1991 | 3 | 12 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1991 | 3 | 13 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1991 | 3 | 14 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1991 | 3 | 15 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1991 | 3 | 16 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1991 | 3 | 17 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1991 | 3 | 18 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1991 | 3 | 19 | 736.6531 | 25 | 711.6531 | 28.5267 | 139.3858 | 0.77441 | 27.7523 | 89.27% | 292.4466 | 274.8998 | 6597.5947
1991 | 3 | 20 | 821.551 | 25 | 796.551 | 28.3569 | 139.3858 | 0.77441 | 27.5825 | 89.27% | 290.6573 | 273.2179 | 6557.2289
1991 | 3 | 21 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
1991 | 3 | 22 | 348.7347 | 25 | 323.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
1991 | 3 | 23 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1991 | 3 | 24 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1991 | 3 | 25 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1991 | 3 | 26 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1991 | 3 | 27 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1991 | 3 | 28 | 668.7347 | 25 | 643.7347 | 28.6625 | 139.3858 | 0.77441 | 27.8881 | 89.27% | 293.878 | 276.2453 | 6629.8874
1991 | 3 | 29 | 856.8163 | 25 | 831.8163 | 28.2864 | 139.3858 | 0.77441 | 27.512 | 89.27% | 289.9141 | 272.5192 | 6540.4615
1991 | 3 | 30 | 594.2857 | 25 | 569.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
1991 | 3 | 31 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1991 | 4 | 1 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1991 | 4 | 2 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1991 | 4 | 3 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1991 | 4 | 4 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1991 | 4 | 5 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1991 | 4 | 6 | 681.7959 | 25 | 656.7959 | 28.6364 | 139.3858 | 0.77441 | 27.862 | 89.27% | 293.6027 | 275.9866 | 6623.6773
1991 | 4 | 7 | 890.7755 | 25 | 865.7755 | 28.2184 | 139.3858 | 0.77441 | 27.444 | 89.27% | 289.1984 | 271.8465 | 6524.3152
1991 | 4 | 8 | 689.6327 | 25 | 664.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
1991 | 4 | 9 | 564.2449 | 25 | 539.2449 | 28.8715 | 139.3858 | 0.77441 | 28.0971 | 89.27% | 296.0802 | 278.3154 | 6679.5685
1991 | 4 | 10 | 595.5918 | 25 | 570.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
1991 | 4 | 11 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1991 | 4 | 12 | 378.7755 | 25 | 353.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
1991 | 4 | 13 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1991 | 4 | 14 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1991 | 4 | 15 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1991 | 4 | 16 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1991 | 4 | 17 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1991 | 4 | 18 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1991 | 4 | 19 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1991 | 4 | 20 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1991 | 4 | 21 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1991 | 4 | 22 | 1684.898 | 25 | 1659.898 | 26.6302 | 139.3858 | 0.77441 | 25.8558 | 89.27% | 272.4618 | 256.1141 | 6146.7392
1991 | 4 | 23 | 1234.2857 | 25 | 1209.2857 | 27.5314 | 139.3858 | 0.77441 | 26.757 | 89.27% | 281.9587 | 265.0412 | 6360.9887
1991 | 4 | 24 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1991 | 4 | 25 | 485.8776 | 25 | 460.8776 | 29.0282 | 139.3858 | 0.77441 | 28.2538 | 89.27% | 297.7318 | 279.8679 | 6716.8293
1991 | 4 | 26 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1991 | 4 | 27 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1991 | 4 | 28 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1991 | 4 | 29 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1991 | 4 | 30 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1991 | 5 | 1 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
1991 | 5 | 2 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
1991 | 5 | 3 | 340.898 | 25 | 315.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
1991 | 5 | 4 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1991 | 5 | 5 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1991 | 5 | 6 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1991 | 5 | 7 | 988.7347 | 25 | 963.7347 | 28.0225 | 139.3858 | 0.77441 | 27.2481 | 89.27% | 287.1338 | 269.9058 | 6477.7392
1991 | 5 | 8 | 582.5306 | 25 | 557.5306 | 28.8349 | 139.3858 | 0.77441 | 28.0605 | 89.27% | 295.6948 | 277.9531 | 6670.8743
1991 | 5 | 9 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1991 | 5 | 10 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1991 | 5 | 11 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1991 | 5 | 12 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1991 | 5 | 13 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1991 | 5 | 14 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1991 | 5 | 15 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1991 | 5 | 16 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1991 | 5 | 17 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1991 | 5 | 18 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1991 | 5 | 19 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1991 | 5 | 20 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1991 | 5 | 21 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1991 | 5 | 22 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1991 | 5 | 23 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1991 | 5 | 24 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1991 | 5 | 25 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
1991 | 5 | 26 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1991 | 5 | 27 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1991 | 5 | 28 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1991 | 5 | 29 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1991 | 5 | 30 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1991 | 5 | 31 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1991 | 6 | 1 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1991 | 6 | 2 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1991 | 6 | 3 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1991 | 6 | 4 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1991 | 6 | 5 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1991 | 6 | 6 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1991 | 6 | 7 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1991 | 6 | 8 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1991 | 6 | 9 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1991 | 6 | 10 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1991 | 6 | 11 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1991 | 6 | 12 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1991 | 6 | 13 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
1991 | 6 | 14 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1991 | 6 | 15 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
1991 | 6 | 16 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1991 | 6 | 17 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1991 | 6 | 18 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1991 | 6 | 19 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1991 | 6 | 20 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1991 | 6 | 21 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1991 | 6 | 22 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1991 | 6 | 23 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1991 | 6 | 24 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1991 | 6 | 25 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1991 | 6 | 26 | 14.3673 | 25 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1991 | 6 | 27 | 13.0612 | 25 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1991 | 6 | 28 | 11.6245 | 25 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1991 | 6 | 29 | 10.8408 | 25 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1991 | 6 | 30 | 10.449 | 25 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1991 | 7 | 1 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1991 | 7 | 2 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1991 | 7 | 3 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1991 | 7 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1991 | 7 | 5 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1991 | 7 | 6 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1991 | 7 | 7 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1991 | 7 | 8 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1991 | 7 | 9 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1991 | 7 | 10 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1991 | 7 | 11 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1991 | 7 | 12 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1991 | 7 | 13 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1991 | 7 | 14 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1991 | 7 | 15 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1991 | 7 | 16 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1991 | 7 | 17 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1991 | 7 | 18 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1991 | 7 | 19 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1991 | 7 | 20 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1991 | 7 | 21 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1991 | 7 | 22 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1991 | 7 | 23 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1991 | 7 | 24 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1991 | 7 | 25 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1991 | 7 | 26 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1991 | 7 | 27 | 5.3551 | 5 | 0.3551 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1991 | 7 | 28 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1991 | 7 | 29 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1991 | 7 | 30 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1991 | 7 | 31 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1991 | 8 | 1 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1991 | 8 | 2 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1991 | 8 | 3 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1991 | 8 | 4 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1991 | 8 | 5 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1991 | 8 | 6 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1991 | 8 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1991 | 8 | 8 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1991 | 8 | 9 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1991 | 8 | 10 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1991 | 8 | 11 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1991 | 8 | 12 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1991 | 8 | 13 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1991 | 8 | 14 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1991 | 8 | 15 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1991 | 8 | 16 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1991 | 8 | 17 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1991 | 8 | 18 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1991 | 8 | 19 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1991 | 8 | 20 | 1115.4286 | 5 | 1110.4286 | 27.7691 | 139.3858 | 0.77441 | 26.9947 | 89.27% | 284.4637 | 267.3959 | 6417.5009
1991 | 8 | 21 | 525.0612 | 5 | 520.0612 | 28.9499 | 139.3858 | 0.77441 | 28.1755 | 89.27% | 296.906 | 279.0916 | 6698.1989
1991 | 8 | 22 | 394.449 | 5 | 389.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
1991 | 8 | 23 | 239.0204 | 5 | 234.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1991 | 8 | 24 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1991 | 8 | 25 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1991 | 8 | 26 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1991 | 8 | 27 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1991 | 8 | 28 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1991 | 8 | 29 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1991 | 8 | 30 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1991 | 8 | 31 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1991 | 9 | 1 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1991 | 9 | 2 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1991 | 9 | 3 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1991 | 9 | 4 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1991 | 9 | 5 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1991 | 9 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1991 | 9 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1991 | 9 | 8 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1991 | 9 | 9 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1991 | 9 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1991 | 9 | 11 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1991 | 9 | 12 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1991 | 9 | 13 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1991 | 9 | 14 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
1991 | 9 | 15 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1991 | 9 | 16 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1991 | 9 | 17 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1991 | 9 | 18 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1991 | 9 | 19 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1991 | 9 | 20 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1991 | 9 | 21 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1991 | 9 | 22 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1991 | 9 | 23 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1991 | 9 | 24 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1991 | 9 | 25 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1991 | 9 | 26 | 334.3673 | 15 | 319.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1991 | 9 | 27 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1991 | 9 | 28 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1991 | 9 | 29 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1991 | 9 | 30 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1991 | 10 | 1 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1991 | 10 | 2 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1991 | 10 | 3 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1991 | 10 | 4 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1991 | 10 | 5 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1991 | 10 | 6 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1991 | 10 | 7 | 833.3061 | 15 | 818.3061 | 28.3334 | 139.3858 | 0.77441 | 27.559 | 89.27% | 290.4096 | 272.985 | 6551.6398
1991 | 10 | 8 | 414.0408 | 15 | 399.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
1991 | 10 | 9 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1991 | 10 | 10 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1991 | 10 | 11 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1991 | 10 | 12 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1991 | 10 | 13 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1991 | 10 | 14 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1991 | 10 | 15 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1991 | 10 | 16 | 284.7347 | 15 | 269.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1991 | 10 | 17 | 370.9388 | 15 | 355.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1991 | 10 | 18 | 306.9388 | 15 | 291.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1991 | 10 | 19 | 266.449 | 15 | 251.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1991 | 10 | 20 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1991 | 10 | 21 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1991 | 10 | 22 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1991 | 10 | 23 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1991 | 10 | 24 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
1991 | 10 | 25 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1991 | 10 | 26 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1991 | 10 | 27 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1991 | 10 | 28 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1991 | 10 | 29 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1991 | 10 | 30 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1991 | 10 | 31 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1991 | 11 | 1 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1991 | 11 | 2 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1991 | 11 | 3 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1991 | 11 | 4 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1991 | 11 | 5 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1991 | 11 | 6 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1991 | 11 | 7 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1991 | 11 | 8 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1991 | 11 | 9 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1991 | 11 | 10 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1991 | 11 | 11 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1991 | 11 | 12 | 717.0612 | 15 | 702.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
1991 | 11 | 13 | 398.3673 | 15 | 383.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1991 | 11 | 14 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1991 | 11 | 15 | 244.2449 | 15 | 229.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1991 | 11 | 16 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1991 | 11 | 17 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1991 | 11 | 18 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1991 | 11 | 19 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1991 | 11 | 20 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1991 | 11 | 21 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1991 | 11 | 22 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1991 | 11 | 23 | 361.7959 | 15 | 346.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
1991 | 11 | 24 | 488.4898 | 15 | 473.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
1991 | 11 | 25 | 583.8367 | 15 | 568.8367 | 28.8323 | 139.3858 | 0.77441 | 28.0579 | 89.27% | 295.6673 | 277.9272 | 6670.2533
1991 | 11 | 26 | 374.8571 | 15 | 359.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1991 | 11 | 27 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1991 | 11 | 28 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1991 | 11 | 29 | 203.7551 | 15 | 188.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1991 | 11 | 30 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1991 | 12 | 1 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1991 | 12 | 2 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1991 | 12 | 3 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1991 | 12 | 4 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1991 | 12 | 5 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1991 | 12 | 6 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1991 | 12 | 7 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1991 | 12 | 8 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1991 | 12 | 9 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1991 | 12 | 10 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1991 | 12 | 11 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1991 | 12 | 12 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1991 | 12 | 13 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1991 | 12 | 14 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1991 | 12 | 15 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1991 | 12 | 16 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1991 | 12 | 17 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1991 | 12 | 18 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1991 | 12 | 19 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1991 | 12 | 20 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1991 | 12 | 21 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1991 | 12 | 22 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1991 | 12 | 23 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1991 | 12 | 24 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1991 | 12 | 25 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1991 | 12 | 26 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1991 | 12 | 27 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1991 | 12 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1991 | 12 | 29 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1991 | 12 | 30 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1991 | 12 | 31 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1992 | 1 | 1 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1992 | 1 | 2 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1992 | 1 | 3 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1992 | 1 | 4 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1992 | 1 | 5 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1992 | 1 | 6 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1992 | 1 | 7 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1992 | 1 | 8 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1992 | 1 | 9 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1992 | 1 | 10 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1992 | 1 | 11 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1992 | 1 | 12 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1992 | 1 | 13 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1992 | 1 | 14 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1992 | 1 | 15 | 344.8163 | 5 | 339.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1992 | 1 | 16 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1992 | 1 | 17 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1992 | 1 | 18 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
1992 | 1 | 19 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1992 | 1 | 20 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1992 | 1 | 21 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1992 | 1 | 22 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1992 | 1 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1992 | 1 | 24 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1992 | 1 | 25 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1992 | 1 | 26 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1992 | 1 | 27 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1992 | 1 | 28 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1992 | 1 | 29 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1992 | 1 | 30 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1992 | 1 | 31 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1992 | 2 | 1 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1992 | 2 | 2 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1992 | 2 | 3 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1992 | 2 | 4 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1992 | 2 | 5 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1992 | 2 | 6 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1992 | 2 | 7 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1992 | 2 | 8 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1992 | 2 | 9 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1992 | 2 | 10 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1992 | 2 | 11 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1992 | 2 | 12 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1992 | 2 | 13 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1992 | 2 | 14 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1992 | 2 | 15 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1992 | 2 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1992 | 2 | 17 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1992 | 2 | 18 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1992 | 2 | 19 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1992 | 2 | 20 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1992 | 2 | 21 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1992 | 2 | 22 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1992 | 2 | 23 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1992 | 2 | 24 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1992 | 2 | 25 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1992 | 2 | 26 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1992 | 2 | 27 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1992 | 2 | 28 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1992 | 2 | 29 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1992 | 3 | 1 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1992 | 3 | 2 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1992 | 3 | 3 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1992 | 3 | 4 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1992 | 3 | 5 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1992 | 3 | 6 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1992 | 3 | 7 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1992 | 3 | 8 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1992 | 3 | 9 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1992 | 3 | 10 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1992 | 3 | 11 | 881.6327 | 25 | 856.6327 | 28.2367 | 139.3858 | 0.77441 | 27.4623 | 89.27% | 289.3911 | 272.0276 | 6528.6623
1992 | 3 | 12 | 2142.0408 | 25 | 2117.0408 | 25.7159 | 139.3858 | 0.77441 | 24.9415 | 89.27% | 262.8273 | 247.0577 | 5929.3846
1992 | 3 | 13 | 792.8163 | 25 | 767.8163 | 28.4144 | 139.3858 | 0.77441 | 27.64 | 89.27% | 291.2629 | 273.7871 | 6570.8912
1992 | 3 | 14 | 380.0816 | 25 | 355.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1992 | 3 | 15 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1992 | 3 | 16 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1992 | 3 | 17 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1992 | 3 | 18 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1992 | 3 | 19 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1992 | 3 | 20 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1992 | 3 | 21 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1992 | 3 | 22 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1992 | 3 | 23 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1992 | 3 | 24 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1992 | 3 | 25 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1992 | 3 | 26 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1992 | 3 | 27 | 1153.3061 | 25 | 1128.3061 | 27.6934 | 139.3858 | 0.77441 | 26.919 | 89.27% | 283.6654 | 266.6455 | 6399.4915
1992 | 3 | 28 | 1776.3265 | 25 | 1751.3265 | 26.4473 | 139.3858 | 0.77441 | 25.6729 | 89.27% | 270.5349 | 254.3028 | 6103.2683
1992 | 3 | 29 | 2194.2857 | 25 | 2169.2857 | 25.6114 | 139.3858 | 0.77441 | 24.837 | 89.27% | 261.7262 | 246.0227 | 5904.544
1992 | 3 | 30 | 807.1837 | 25 | 782.1837 | 28.3856 | 139.3858 | 0.77441 | 27.6112 | 89.27% | 290.9601 | 273.5025 | 6564.06
1992 | 3 | 31 | 502.8571 | 25 | 477.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
1992 | 4 | 1 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1992 | 4 | 2 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1992 | 4 | 3 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
1992 | 4 | 4 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1992 | 4 | 5 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1992 | 4 | 6 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1992 | 4 | 7 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1992 | 4 | 8 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
1992 | 4 | 9 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1992 | 4 | 10 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1992 | 4 | 11 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1992 | 4 | 12 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1992 | 4 | 13 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1992 | 4 | 14 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1992 | 4 | 15 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1992 | 4 | 16 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1992 | 4 | 17 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1992 | 4 | 18 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1992 | 4 | 19 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1992 | 4 | 20 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
1992 | 4 | 21 | 637.3878 | 25 | 612.3878 | 28.7252 | 139.3858 | 0.77441 | 27.9508 | 89.27% | 294.5386 | 276.8663 | 6644.7917
1992 | 4 | 22 | 673.9592 | 25 | 648.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
1992 | 4 | 23 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1992 | 4 | 24 | 621.7143 | 25 | 596.7143 | 28.7566 | 139.3858 | 0.77441 | 27.9822 | 89.27% | 294.869 | 277.1768 | 6652.2439
1992 | 4 | 25 | 958.6939 | 25 | 933.6939 | 28.0826 | 139.3858 | 0.77441 | 27.3082 | 89.27% | 287.767 | 270.5009 | 6492.0225
1992 | 4 | 26 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
1992 | 4 | 27 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1992 | 4 | 28 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1992 | 4 | 29 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1992 | 4 | 30 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1992 | 5 | 1 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1992 | 5 | 2 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1992 | 5 | 3 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1992 | 5 | 4 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1992 | 5 | 5 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1992 | 5 | 6 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1992 | 5 | 7 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1992 | 5 | 8 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1992 | 5 | 9 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1992 | 5 | 10 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1992 | 5 | 11 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1992 | 5 | 12 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1992 | 5 | 13 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1992 | 5 | 14 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1992 | 5 | 15 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1992 | 5 | 16 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1992 | 5 | 17 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1992 | 5 | 18 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1992 | 5 | 19 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1992 | 5 | 20 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1992 | 5 | 21 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1992 | 5 | 22 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1992 | 5 | 23 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1992 | 5 | 24 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1992 | 5 | 25 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1992 | 5 | 26 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1992 | 5 | 27 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1992 | 5 | 28 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1992 | 5 | 29 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1992 | 5 | 30 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1992 | 5 | 31 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1992 | 6 | 1 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1992 | 6 | 2 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1992 | 6 | 3 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1992 | 6 | 4 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1992 | 6 | 5 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1992 | 6 | 6 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1992 | 6 | 7 | 380.0816 | 25 | 355.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1992 | 6 | 8 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1992 | 6 | 9 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1992 | 6 | 10 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1992 | 6 | 11 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1992 | 6 | 12 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1992 | 6 | 13 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1992 | 6 | 14 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1992 | 6 | 15 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1992 | 6 | 16 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1992 | 6 | 17 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1992 | 6 | 18 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1992 | 6 | 19 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1992 | 6 | 20 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1992 | 6 | 21 | 23.5102 | 25 | 0 | 29.953 | 0 | 0 | 29.953 | 0% | 0 | 0 | 0
1992 | 6 | 22 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1992 | 6 | 23 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1992 | 6 | 24 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1992 | 6 | 25 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1992 | 6 | 26 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1992 | 6 | 27 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1992 | 6 | 28 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1992 | 6 | 29 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1992 | 6 | 30 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1992 | 7 | 1 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1992 | 7 | 2 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1992 | 7 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1992 | 7 | 4 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1992 | 7 | 5 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1992 | 7 | 6 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1992 | 7 | 7 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1992 | 7 | 8 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1992 | 7 | 9 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1992 | 7 | 10 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1992 | 7 | 11 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1992 | 7 | 12 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1992 | 7 | 13 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1992 | 7 | 14 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1992 | 7 | 15 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1992 | 7 | 16 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1992 | 7 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1992 | 7 | 18 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1992 | 7 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1992 | 7 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1992 | 7 | 21 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1992 | 7 | 22 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1992 | 7 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1992 | 7 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1992 | 7 | 25 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1992 | 7 | 26 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1992 | 7 | 27 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1992 | 7 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1992 | 7 | 29 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1992 | 7 | 30 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1992 | 7 | 31 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1992 | 8 | 1 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1992 | 8 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1992 | 8 | 3 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1992 | 8 | 4 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1992 | 8 | 5 | 472.8163 | 5 | 467.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
1992 | 8 | 6 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1992 | 8 | 7 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1992 | 8 | 8 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1992 | 8 | 9 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1992 | 8 | 10 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1992 | 8 | 11 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1992 | 8 | 12 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1992 | 8 | 13 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1992 | 8 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1992 | 8 | 15 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1992 | 8 | 16 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1992 | 8 | 17 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1992 | 8 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1992 | 8 | 19 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1992 | 8 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1992 | 8 | 21 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1992 | 8 | 22 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1992 | 8 | 23 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1992 | 8 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1992 | 8 | 25 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1992 | 8 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1992 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1992 | 8 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1992 | 8 | 29 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1992 | 8 | 30 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1992 | 8 | 31 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1992 | 9 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1992 | 9 | 2 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
1992 | 9 | 3 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1992 | 9 | 4 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1992 | 9 | 5 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1992 | 9 | 6 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1992 | 9 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1992 | 9 | 8 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1992 | 9 | 9 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1992 | 9 | 10 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1992 | 9 | 11 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1992 | 9 | 12 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1992 | 9 | 13 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1992 | 9 | 14 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1992 | 9 | 15 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1992 | 9 | 16 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1992 | 9 | 17 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1992 | 9 | 18 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1992 | 9 | 19 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1992 | 9 | 20 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1992 | 9 | 21 | 12.5388 | 15 | 0 | 29.9749 | 0 | 0 | 29.9749 | 0% | 0 | 0 | 0
1992 | 9 | 22 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
1992 | 9 | 23 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1992 | 9 | 24 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1992 | 9 | 25 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1992 | 9 | 26 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1992 | 9 | 27 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1992 | 9 | 28 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1992 | 9 | 29 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1992 | 9 | 30 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1992 | 10 | 1 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1992 | 10 | 2 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1992 | 10 | 3 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1992 | 10 | 4 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1992 | 10 | 5 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1992 | 10 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1992 | 10 | 7 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1992 | 10 | 8 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1992 | 10 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1992 | 10 | 10 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1992 | 10 | 11 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1992 | 10 | 12 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1992 | 10 | 13 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1992 | 10 | 14 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1992 | 10 | 15 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1992 | 10 | 16 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1992 | 10 | 17 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1992 | 10 | 18 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1992 | 10 | 19 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1992 | 10 | 20 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1992 | 10 | 21 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1992 | 10 | 22 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1992 | 10 | 23 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1992 | 10 | 24 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1992 | 10 | 25 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1992 | 10 | 26 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1992 | 10 | 27 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1992 | 10 | 28 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1992 | 10 | 29 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1992 | 10 | 30 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1992 | 10 | 31 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1992 | 11 | 1 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1992 | 11 | 2 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1992 | 11 | 3 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1992 | 11 | 4 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1992 | 11 | 5 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1992 | 11 | 6 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1992 | 11 | 7 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1992 | 11 | 8 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1992 | 11 | 9 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1992 | 11 | 10 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1992 | 11 | 11 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1992 | 11 | 12 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1992 | 11 | 13 | 338.2857 | 15 | 323.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1992 | 11 | 14 | 350.0408 | 15 | 335.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
1992 | 11 | 15 | 216.8163 | 15 | 201.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1992 | 11 | 16 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1992 | 11 | 17 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1992 | 11 | 18 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1992 | 11 | 19 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1992 | 11 | 20 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1992 | 11 | 21 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1992 | 11 | 22 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1992 | 11 | 23 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1992 | 11 | 24 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1992 | 11 | 25 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1992 | 11 | 26 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1992 | 11 | 27 | 381.3878 | 15 | 366.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1992 | 11 | 28 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1992 | 11 | 29 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1992 | 11 | 30 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1992 | 12 | 1 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1992 | 12 | 2 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1992 | 12 | 3 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1992 | 12 | 4 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1992 | 12 | 5 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1992 | 12 | 6 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1992 | 12 | 7 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1992 | 12 | 8 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1992 | 12 | 9 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1992 | 12 | 10 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1992 | 12 | 11 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1992 | 12 | 12 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1992 | 12 | 13 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1992 | 12 | 14 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1992 | 12 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1992 | 12 | 16 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1992 | 12 | 17 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1992 | 12 | 18 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1992 | 12 | 19 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1992 | 12 | 20 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1992 | 12 | 21 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1992 | 12 | 22 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1992 | 12 | 23 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1992 | 12 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1992 | 12 | 25 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1992 | 12 | 26 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1992 | 12 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1992 | 12 | 28 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1992 | 12 | 29 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1992 | 12 | 30 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1992 | 12 | 31 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1993 | 1 | 1 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1993 | 1 | 2 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1993 | 1 | 3 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1993 | 1 | 4 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1993 | 1 | 5 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1993 | 1 | 6 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1993 | 1 | 7 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1993 | 1 | 8 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1993 | 1 | 9 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1993 | 1 | 10 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1993 | 1 | 11 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1993 | 1 | 12 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 1 | 13 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 1 | 14 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1993 | 1 | 15 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1993 | 1 | 16 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1993 | 1 | 17 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1993 | 1 | 18 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1993 | 1 | 19 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 1 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 1 | 21 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 1 | 22 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 1 | 23 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1993 | 1 | 24 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1993 | 1 | 25 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1993 | 1 | 26 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1993 | 1 | 27 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1993 | 1 | 28 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1993 | 1 | 29 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1993 | 1 | 30 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1993 | 1 | 31 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1993 | 2 | 1 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 3 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 4 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 5 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 6 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 7 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1993 | 2 | 8 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1993 | 2 | 9 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1993 | 2 | 10 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1993 | 2 | 11 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1993 | 2 | 12 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1993 | 2 | 13 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1993 | 2 | 14 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 15 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1993 | 2 | 16 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1993 | 2 | 17 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1993 | 2 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1993 | 2 | 19 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1993 | 2 | 20 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1993 | 2 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1993 | 2 | 22 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1993 | 2 | 23 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1993 | 2 | 24 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1993 | 2 | 25 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1993 | 2 | 26 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1993 | 2 | 27 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1993 | 2 | 28 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1993 | 3 | 1 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1993 | 3 | 2 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1993 | 3 | 3 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1993 | 3 | 4 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1993 | 3 | 5 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1993 | 3 | 6 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1993 | 3 | 7 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1993 | 3 | 8 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1993 | 3 | 9 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1993 | 3 | 10 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
1993 | 3 | 11 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1993 | 3 | 12 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1993 | 3 | 13 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1993 | 3 | 14 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1993 | 3 | 15 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1993 | 3 | 16 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1993 | 3 | 17 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1993 | 3 | 18 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1993 | 3 | 19 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1993 | 3 | 20 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
1993 | 3 | 21 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1993 | 3 | 22 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1993 | 3 | 23 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1993 | 3 | 24 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1993 | 3 | 25 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1993 | 3 | 26 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1993 | 3 | 27 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1993 | 3 | 28 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1993 | 3 | 29 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
1993 | 3 | 30 | 1077.551 | 25 | 1052.551 | 27.8449 | 139.3858 | 0.77441 | 27.0705 | 89.27% | 285.262 | 268.1463 | 6435.5103
1993 | 3 | 31 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1993 | 4 | 1 | 949.551 | 25 | 924.551 | 28.1009 | 139.3858 | 0.77441 | 27.3265 | 89.27% | 287.9596 | 270.6821 | 6496.3696
1993 | 4 | 2 | 540.7347 | 25 | 515.7347 | 28.9185 | 139.3858 | 0.77441 | 28.1441 | 89.27% | 296.5757 | 278.7811 | 6690.7467
1993 | 4 | 3 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1993 | 4 | 4 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1993 | 4 | 5 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1993 | 4 | 6 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1993 | 4 | 7 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1993 | 4 | 8 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1993 | 4 | 9 | 671.3469 | 25 | 646.3469 | 28.6573 | 139.3858 | 0.77441 | 27.8829 | 89.27% | 293.8229 | 276.1936 | 6628.6454
1993 | 4 | 10 | 852.898 | 25 | 827.898 | 28.2942 | 139.3858 | 0.77441 | 27.5198 | 89.27% | 289.9967 | 272.5969 | 6542.3246
1993 | 4 | 11 | 3435.102 | 25 | 3410.102 | 23.1298 | 0 | 0 | 23.1298 | 0% | 0 | 0 | 0
1993 | 4 | 12 | 3317.551 | 25 | 3292.551 | 23.3649 | 0 | 0 | 23.3649 | 0% | 0 | 0 | 0
1993 | 4 | 13 | 2155.102 | 25 | 2130.102 | 25.6898 | 139.3858 | 0.77441 | 24.9154 | 89.27% | 262.5521 | 246.7989 | 5923.1744
1993 | 4 | 14 | 1384.4898 | 25 | 1359.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
1993 | 4 | 15 | 1025.3061 | 25 | 1000.3061 | 27.9494 | 139.3858 | 0.77441 | 27.175 | 89.27% | 286.3631 | 269.1813 | 6460.3508
1993 | 4 | 16 | 719.6735 | 25 | 694.6735 | 28.5607 | 139.3858 | 0.77441 | 27.7862 | 89.27% | 292.8044 | 275.2362 | 6605.6679
1993 | 4 | 17 | 1737.1429 | 25 | 1712.1429 | 26.5257 | 139.3858 | 0.77441 | 25.7513 | 89.27% | 271.3608 | 255.0791 | 6121.8986
1993 | 4 | 18 | 1933.0612 | 25 | 1908.0612 | 26.1339 | 139.3858 | 0.77441 | 25.3595 | 89.27% | 267.2317 | 251.1978 | 6028.7467
1993 | 4 | 19 | 967.8367 | 25 | 942.8367 | 28.0643 | 139.3858 | 0.77441 | 27.2899 | 89.27% | 287.5743 | 270.3198 | 6487.6754
1993 | 4 | 20 | 694.8571 | 25 | 669.8571 | 28.6103 | 139.3858 | 0.77441 | 27.8359 | 89.27% | 293.3274 | 275.7278 | 6617.4671
1993 | 4 | 21 | 551.1837 | 25 | 526.1837 | 28.8976 | 139.3858 | 0.77441 | 28.1232 | 89.27% | 296.3554 | 278.5741 | 6685.7786
1993 | 4 | 22 | 523.7551 | 25 | 498.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
1993 | 4 | 23 | 723.5918 | 25 | 698.5918 | 28.5528 | 139.3858 | 0.77441 | 27.7784 | 89.27% | 292.7218 | 275.1585 | 6603.8049
1993 | 4 | 24 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1993 | 4 | 25 | 481.9592 | 25 | 456.9592 | 29.0361 | 139.3858 | 0.77441 | 28.2617 | 89.27% | 297.8144 | 279.9455 | 6718.6923
1993 | 4 | 26 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1993 | 4 | 27 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1993 | 4 | 28 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1993 | 4 | 29 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1993 | 4 | 30 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1993 | 5 | 1 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1993 | 5 | 2 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1993 | 5 | 3 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1993 | 5 | 4 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1993 | 5 | 5 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1993 | 5 | 6 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1993 | 5 | 7 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1993 | 5 | 8 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1993 | 5 | 9 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1993 | 5 | 10 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1993 | 5 | 11 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1993 | 5 | 12 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
1993 | 5 | 13 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1993 | 5 | 14 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1993 | 5 | 15 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1993 | 5 | 16 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1993 | 5 | 17 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1993 | 5 | 18 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1993 | 5 | 19 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1993 | 5 | 20 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1993 | 5 | 21 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
1993 | 5 | 22 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1993 | 5 | 23 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1993 | 5 | 24 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1993 | 5 | 25 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1993 | 5 | 26 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1993 | 5 | 27 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1993 | 5 | 28 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1993 | 5 | 29 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1993 | 5 | 30 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1993 | 5 | 31 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
1993 | 6 | 1 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1993 | 6 | 2 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1993 | 6 | 3 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1993 | 6 | 4 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
1993 | 6 | 5 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1993 | 6 | 6 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1993 | 6 | 7 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
1993 | 6 | 8 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1993 | 6 | 9 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1993 | 6 | 10 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1993 | 6 | 11 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1993 | 6 | 12 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
1993 | 6 | 13 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1993 | 6 | 14 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1993 | 6 | 15 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1993 | 6 | 16 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1993 | 6 | 17 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1993 | 6 | 18 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1993 | 6 | 19 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1993 | 6 | 20 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1993 | 6 | 21 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1993 | 6 | 22 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1993 | 6 | 23 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1993 | 6 | 24 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1993 | 6 | 25 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1993 | 6 | 26 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
1993 | 6 | 27 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1993 | 6 | 28 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1993 | 6 | 29 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1993 | 6 | 30 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1993 | 7 | 1 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1993 | 7 | 2 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1993 | 7 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1993 | 7 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1993 | 7 | 5 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1993 | 7 | 6 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1993 | 7 | 7 | 10.7102 | 5 | 5.7102 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1993 | 7 | 8 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1993 | 7 | 9 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1993 | 7 | 10 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1993 | 7 | 11 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1993 | 7 | 12 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1993 | 7 | 13 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1993 | 7 | 14 | 6.1388 | 5 | 1.1388 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1993 | 7 | 15 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1993 | 7 | 16 | 5.3551 | 5 | 0.3551 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 7 | 17 | 5.3551 | 5 | 0.3551 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 7 | 18 | 5.3551 | 5 | 0.3551 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 7 | 19 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1993 | 7 | 20 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1993 | 7 | 21 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1993 | 7 | 22 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1993 | 7 | 23 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1993 | 7 | 24 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1993 | 7 | 25 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1993 | 7 | 26 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1993 | 7 | 27 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1993 | 7 | 28 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1993 | 7 | 29 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1993 | 7 | 30 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1993 | 7 | 31 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1993 | 8 | 1 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1993 | 8 | 2 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1993 | 8 | 3 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1993 | 8 | 4 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1993 | 8 | 5 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1993 | 8 | 6 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1993 | 8 | 7 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1993 | 8 | 8 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1993 | 8 | 9 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1993 | 8 | 10 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1993 | 8 | 11 | 6.1388 | 5 | 1.1388 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1993 | 8 | 12 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1993 | 8 | 13 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1993 | 8 | 14 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1993 | 8 | 15 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 8 | 16 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1993 | 8 | 17 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1993 | 8 | 18 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1993 | 8 | 19 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1993 | 8 | 20 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1993 | 8 | 21 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1993 | 8 | 22 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1993 | 8 | 23 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1993 | 8 | 24 | 5.3551 | 5 | 0.3551 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 8 | 25 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1993 | 8 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1993 | 8 | 27 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1993 | 8 | 28 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1993 | 8 | 29 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1993 | 8 | 30 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1993 | 8 | 31 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1993 | 9 | 1 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1993 | 9 | 2 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 9 | 3 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 9 | 4 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 9 | 5 | 5.3551 | 15 | 0 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 9 | 6 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1993 | 9 | 7 | 5.3551 | 15 | 0 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 9 | 8 | 5.3551 | 15 | 0 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1993 | 9 | 9 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 9 | 10 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 9 | 11 | 5.6163 | 15 | 0 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1993 | 9 | 12 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1993 | 9 | 13 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1993 | 9 | 14 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1993 | 9 | 15 | 4.5714 | 15 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
1993 | 9 | 16 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1993 | 9 | 17 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1993 | 9 | 18 | 4.8327 | 15 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1993 | 9 | 19 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1993 | 9 | 20 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1993 | 9 | 21 | 4.8327 | 15 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
1993 | 9 | 22 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1993 | 9 | 23 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1993 | 9 | 24 | 4.702 | 15 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1993 | 9 | 25 | 5.0939 | 15 | 0 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
1993 | 9 | 26 | 5.8776 | 15 | 0 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
1993 | 9 | 27 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
1993 | 9 | 28 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1993 | 9 | 29 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1993 | 9 | 30 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1993 | 10 | 1 | 10.3184 | 15 | 0 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1993 | 10 | 2 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1993 | 10 | 3 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1993 | 10 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1993 | 10 | 5 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1993 | 10 | 6 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1993 | 10 | 7 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1993 | 10 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1993 | 10 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1993 | 10 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1993 | 10 | 11 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1993 | 10 | 12 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1993 | 10 | 13 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1993 | 10 | 14 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1993 | 10 | 15 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1993 | 10 | 16 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1993 | 10 | 17 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1993 | 10 | 18 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1993 | 10 | 19 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1993 | 10 | 20 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1993 | 10 | 21 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1993 | 10 | 22 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1993 | 10 | 23 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1993 | 10 | 24 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1993 | 10 | 25 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1993 | 10 | 26 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1993 | 10 | 27 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1993 | 10 | 28 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1993 | 10 | 29 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1993 | 10 | 30 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1993 | 10 | 31 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1993 | 11 | 1 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1993 | 11 | 2 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
1993 | 11 | 3 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1993 | 11 | 4 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1993 | 11 | 5 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1993 | 11 | 6 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
1993 | 11 | 7 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1993 | 11 | 8 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1993 | 11 | 9 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1993 | 11 | 10 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1993 | 11 | 11 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1993 | 11 | 12 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1993 | 11 | 13 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1993 | 11 | 14 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1993 | 11 | 15 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1993 | 11 | 16 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1993 | 11 | 17 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1993 | 11 | 18 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1993 | 11 | 19 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1993 | 11 | 20 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1993 | 11 | 21 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1993 | 11 | 22 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1993 | 11 | 23 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1993 | 11 | 24 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1993 | 11 | 25 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1993 | 11 | 26 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1993 | 11 | 27 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1993 | 11 | 28 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1993 | 11 | 29 | 919.5102 | 15 | 904.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
1993 | 11 | 30 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1993 | 12 | 1 | 249.4694 | 5 | 244.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1993 | 12 | 2 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1993 | 12 | 3 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1993 | 12 | 4 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1993 | 12 | 5 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1993 | 12 | 6 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1993 | 12 | 7 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1993 | 12 | 8 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1993 | 12 | 9 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
1993 | 12 | 10 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1993 | 12 | 11 | 417.9592 | 5 | 412.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
1993 | 12 | 12 | 445.3878 | 5 | 440.3878 | 29.1092 | 139.3858 | 0.77441 | 28.3348 | 89.27% | 298.5851 | 280.67 | 6736.0807
1993 | 12 | 13 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
1993 | 12 | 14 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1993 | 12 | 15 | 309.551 | 5 | 304.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1993 | 12 | 16 | 275.5918 | 5 | 270.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1993 | 12 | 17 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1993 | 12 | 18 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1993 | 12 | 19 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1993 | 12 | 20 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1993 | 12 | 21 | 270.3673 | 5 | 265.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1993 | 12 | 22 | 1017.4694 | 5 | 1012.4694 | 27.9651 | 139.3858 | 0.77441 | 27.1907 | 89.27% | 286.5282 | 269.3365 | 6464.0769
1993 | 12 | 23 | 560.3265 | 5 | 555.3265 | 28.8793 | 139.3858 | 0.77441 | 28.1049 | 89.27% | 296.1627 | 278.393 | 6681.4315
1993 | 12 | 24 | 333.0612 | 5 | 328.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1993 | 12 | 25 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1993 | 12 | 26 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
1993 | 12 | 27 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1993 | 12 | 28 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1993 | 12 | 29 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1993 | 12 | 30 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1993 | 12 | 31 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1994 | 1 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1994 | 1 | 2 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1994 | 1 | 3 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1994 | 1 | 4 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1994 | 1 | 5 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1994 | 1 | 6 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1994 | 1 | 7 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1994 | 1 | 8 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1994 | 1 | 9 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1994 | 1 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1994 | 1 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1994 | 1 | 12 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 1 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1994 | 1 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1994 | 1 | 15 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1994 | 1 | 16 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 1 | 17 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1994 | 1 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 1 | 19 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1994 | 1 | 20 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1994 | 1 | 21 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1994 | 1 | 22 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 1 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1994 | 1 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1994 | 1 | 25 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1994 | 1 | 26 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1994 | 1 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1994 | 1 | 28 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1994 | 1 | 29 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1994 | 1 | 30 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1994 | 1 | 31 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1994 | 2 | 1 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1994 | 2 | 2 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1994 | 2 | 3 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1994 | 2 | 4 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1994 | 2 | 5 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1994 | 2 | 6 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1994 | 2 | 7 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1994 | 2 | 8 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1994 | 2 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1994 | 2 | 10 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1994 | 2 | 11 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1994 | 2 | 12 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1994 | 2 | 13 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 2 | 14 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 2 | 15 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1994 | 2 | 16 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1994 | 2 | 17 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1994 | 2 | 18 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1994 | 2 | 19 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1994 | 2 | 20 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1994 | 2 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1994 | 2 | 22 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1994 | 2 | 23 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1994 | 2 | 24 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1994 | 2 | 25 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1994 | 2 | 26 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1994 | 2 | 27 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1994 | 2 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1994 | 3 | 1 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1994 | 3 | 2 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1994 | 3 | 3 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1994 | 3 | 4 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
1994 | 3 | 5 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1994 | 3 | 6 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1994 | 3 | 7 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1994 | 3 | 8 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1994 | 3 | 9 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1994 | 3 | 10 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1994 | 3 | 11 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
1994 | 3 | 12 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1994 | 3 | 13 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1994 | 3 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1994 | 3 | 15 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1994 | 3 | 16 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1994 | 3 | 17 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1994 | 3 | 18 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1994 | 3 | 19 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1994 | 3 | 20 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1994 | 3 | 21 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1994 | 3 | 22 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1994 | 3 | 23 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1994 | 3 | 24 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1994 | 3 | 25 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1994 | 3 | 26 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1994 | 3 | 27 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
1994 | 3 | 28 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1994 | 3 | 29 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1994 | 3 | 30 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1994 | 3 | 31 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1994 | 4 | 1 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1994 | 4 | 2 | 344.8163 | 25 | 319.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
1994 | 4 | 3 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
1994 | 4 | 4 | 481.9592 | 25 | 456.9592 | 29.0361 | 139.3858 | 0.77441 | 28.2617 | 89.27% | 297.8144 | 279.9455 | 6718.6923
1994 | 4 | 5 | 624.3265 | 25 | 599.3265 | 28.7513 | 139.3858 | 0.77441 | 27.9769 | 89.27% | 294.8139 | 277.1251 | 6651.0019
1994 | 4 | 6 | 727.5102 | 25 | 702.5102 | 28.545 | 139.3858 | 0.77441 | 27.7706 | 89.27% | 292.6393 | 275.0809 | 6601.9418
1994 | 4 | 7 | 1037.0612 | 25 | 1012.0612 | 27.9259 | 139.3858 | 0.77441 | 27.1515 | 89.27% | 286.1153 | 268.9484 | 6454.7617
1994 | 4 | 8 | 1013.551 | 25 | 988.551 | 27.9729 | 139.3858 | 0.77441 | 27.1985 | 89.27% | 286.6108 | 269.4142 | 6465.9399
1994 | 4 | 9 | 781.0612 | 25 | 756.0612 | 28.4379 | 139.3858 | 0.77441 | 27.6635 | 89.27% | 291.5107 | 274.02 | 6576.4803
1994 | 4 | 10 | 732.7347 | 25 | 707.7347 | 28.5345 | 139.3858 | 0.77441 | 27.7601 | 89.27% | 292.5292 | 274.9774 | 6599.4578
1994 | 4 | 11 | 812.4082 | 25 | 787.4082 | 28.3752 | 139.3858 | 0.77441 | 27.6008 | 89.27% | 290.85 | 273.399 | 6561.576
1994 | 4 | 12 | 875.102 | 25 | 850.102 | 28.2498 | 139.3858 | 0.77441 | 27.4754 | 89.27% | 289.5287 | 272.157 | 6531.7673
1994 | 4 | 13 | 1004.4082 | 25 | 979.4082 | 27.9912 | 139.3858 | 0.77441 | 27.2168 | 89.27% | 286.8035 | 269.5953 | 6470.287
1994 | 4 | 14 | 1475.9184 | 25 | 1450.9184 | 27.0482 | 139.3858 | 0.77441 | 26.2738 | 89.27% | 276.8662 | 260.2542 | 6246.1013
1994 | 4 | 15 | 1541.2245 | 25 | 1516.2245 | 26.9176 | 139.3858 | 0.77441 | 26.1431 | 89.27% | 275.4898 | 258.9604 | 6215.0506
1994 | 4 | 16 | 1815.5102 | 25 | 1790.5102 | 26.369 | 139.3858 | 0.77441 | 25.5946 | 89.27% | 269.7091 | 253.5266 | 6084.6379
1994 | 4 | 17 | 2024.4898 | 25 | 1999.4898 | 25.951 | 139.3858 | 0.77441 | 25.1766 | 89.27% | 265.3048 | 249.3865 | 5985.2758
1994 | 4 | 18 | 1257.7959 | 25 | 1232.7959 | 27.4844 | 139.3858 | 0.77441 | 26.71 | 89.27% | 281.4632 | 264.5754 | 6349.8105
1994 | 4 | 19 | 846.3673 | 25 | 821.3673 | 28.3073 | 139.3858 | 0.77441 | 27.5329 | 89.27% | 290.1343 | 272.7262 | 6545.4296
1994 | 4 | 20 | 704 | 25 | 679 | 28.592 | 139.3858 | 0.77441 | 27.8176 | 89.27% | 293.1348 | 275.5467 | 6613.1201
1994 | 4 | 21 | 637.3878 | 25 | 612.3878 | 28.7252 | 139.3858 | 0.77441 | 27.9508 | 89.27% | 294.5386 | 276.8663 | 6644.7917
1994 | 4 | 22 | 525.0612 | 25 | 500.0612 | 28.9499 | 139.3858 | 0.77441 | 28.1755 | 89.27% | 296.906 | 279.0916 | 6698.1989
1994 | 4 | 23 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
1994 | 4 | 24 | 440.1633 | 25 | 415.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
1994 | 4 | 25 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1994 | 4 | 26 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
1994 | 4 | 27 | 903.8367 | 25 | 878.8367 | 28.1923 | 139.3858 | 0.77441 | 27.4179 | 89.27% | 288.9231 | 271.5877 | 6518.105
1994 | 4 | 28 | 710.5306 | 25 | 685.5306 | 28.5789 | 139.3858 | 0.77441 | 27.8045 | 89.27% | 292.9971 | 275.4173 | 6610.015
1994 | 4 | 29 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
1994 | 4 | 30 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
1994 | 5 | 1 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
1994 | 5 | 2 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
1994 | 5 | 3 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1994 | 5 | 4 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1994 | 5 | 5 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1994 | 5 | 6 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1994 | 5 | 7 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1994 | 5 | 8 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1994 | 5 | 9 | 569.4694 | 25 | 544.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
1994 | 5 | 10 | 393.1429 | 25 | 368.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1994 | 5 | 11 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1994 | 5 | 12 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
1994 | 5 | 13 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
1994 | 5 | 14 | 267.7551 | 25 | 242.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
1994 | 5 | 15 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1994 | 5 | 16 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1994 | 5 | 17 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
1994 | 5 | 18 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
1994 | 5 | 19 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1994 | 5 | 20 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1994 | 5 | 21 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1994 | 5 | 22 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1994 | 5 | 23 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1994 | 5 | 24 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1994 | 5 | 25 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
1994 | 5 | 26 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1994 | 5 | 27 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1994 | 5 | 28 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1994 | 5 | 29 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1994 | 5 | 30 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1994 | 5 | 31 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1994 | 6 | 1 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1994 | 6 | 2 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1994 | 6 | 3 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1994 | 6 | 4 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1994 | 6 | 5 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1994 | 6 | 6 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1994 | 6 | 7 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1994 | 6 | 8 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1994 | 6 | 9 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1994 | 6 | 10 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1994 | 6 | 11 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1994 | 6 | 12 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1994 | 6 | 13 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1994 | 6 | 14 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1994 | 6 | 15 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1994 | 6 | 16 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1994 | 6 | 17 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1994 | 6 | 18 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1994 | 6 | 19 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1994 | 6 | 20 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1994 | 6 | 21 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
1994 | 6 | 22 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1994 | 6 | 23 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1994 | 6 | 24 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1994 | 6 | 25 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1994 | 6 | 26 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1994 | 6 | 27 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1994 | 6 | 28 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1994 | 6 | 29 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1994 | 6 | 30 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1994 | 7 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1994 | 7 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1994 | 7 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1994 | 7 | 4 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1994 | 7 | 5 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1994 | 7 | 6 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1994 | 7 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1994 | 7 | 8 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1994 | 7 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1994 | 7 | 10 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1994 | 7 | 11 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1994 | 7 | 12 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1994 | 7 | 13 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1994 | 7 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1994 | 7 | 15 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1994 | 7 | 16 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1994 | 7 | 17 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1994 | 7 | 18 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1994 | 7 | 19 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1994 | 7 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1994 | 7 | 21 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1994 | 7 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1994 | 7 | 23 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1994 | 7 | 24 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1994 | 7 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1994 | 7 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1994 | 7 | 27 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1994 | 7 | 28 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1994 | 7 | 29 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1994 | 7 | 30 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1994 | 7 | 31 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1994 | 8 | 1 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1994 | 8 | 2 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1994 | 8 | 3 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1994 | 8 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1994 | 8 | 5 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1994 | 8 | 6 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1994 | 8 | 7 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1994 | 8 | 8 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1994 | 8 | 9 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1994 | 8 | 10 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1994 | 8 | 11 | 7.4449 | 5 | 2.4449 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1994 | 8 | 12 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1994 | 8 | 13 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1994 | 8 | 14 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1994 | 8 | 15 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1994 | 8 | 16 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1994 | 8 | 17 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1994 | 8 | 18 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1994 | 8 | 19 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
1994 | 8 | 20 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1994 | 8 | 21 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1994 | 8 | 22 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1994 | 8 | 23 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1994 | 8 | 24 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1994 | 8 | 25 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1994 | 8 | 26 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1994 | 8 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1994 | 8 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1994 | 8 | 29 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1994 | 8 | 30 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1994 | 8 | 31 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1994 | 9 | 1 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1994 | 9 | 2 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
1994 | 9 | 3 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1994 | 9 | 4 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1994 | 9 | 5 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1994 | 9 | 6 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1994 | 9 | 7 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1994 | 9 | 8 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1994 | 9 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1994 | 9 | 10 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1994 | 9 | 11 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1994 | 9 | 12 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1994 | 9 | 13 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1994 | 9 | 14 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1994 | 9 | 15 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1994 | 9 | 16 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
1994 | 9 | 17 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1994 | 9 | 18 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1994 | 9 | 19 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1994 | 9 | 20 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1994 | 9 | 21 | 5.6163 | 15 | 0 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1994 | 9 | 22 | 5.3551 | 15 | 0 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
1994 | 9 | 23 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1994 | 9 | 24 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1994 | 9 | 25 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
1994 | 9 | 26 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1994 | 9 | 27 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1994 | 9 | 28 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1994 | 9 | 29 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1994 | 9 | 30 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1994 | 10 | 1 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1994 | 10 | 2 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1994 | 10 | 3 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1994 | 10 | 4 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1994 | 10 | 5 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1994 | 10 | 6 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1994 | 10 | 7 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1994 | 10 | 8 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1994 | 10 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1994 | 10 | 10 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1994 | 10 | 11 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1994 | 10 | 12 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1994 | 10 | 13 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1994 | 10 | 14 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1994 | 10 | 15 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1994 | 10 | 16 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1994 | 10 | 17 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1994 | 10 | 18 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1994 | 10 | 19 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1994 | 10 | 20 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1994 | 10 | 21 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1994 | 10 | 22 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1994 | 10 | 23 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1994 | 10 | 24 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1994 | 10 | 25 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1994 | 10 | 26 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1994 | 10 | 27 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1994 | 10 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1994 | 10 | 29 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1994 | 10 | 30 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1994 | 10 | 31 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1994 | 11 | 1 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1994 | 11 | 2 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1994 | 11 | 3 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
1994 | 11 | 4 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
1994 | 11 | 5 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1994 | 11 | 6 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1994 | 11 | 7 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1994 | 11 | 8 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1994 | 11 | 9 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1994 | 11 | 10 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1994 | 11 | 11 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1994 | 11 | 12 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1994 | 11 | 13 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1994 | 11 | 14 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1994 | 11 | 15 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1994 | 11 | 16 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1994 | 11 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1994 | 11 | 18 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1994 | 11 | 19 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1994 | 11 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1994 | 11 | 21 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1994 | 11 | 22 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1994 | 11 | 23 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
1994 | 11 | 24 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1994 | 11 | 25 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1994 | 11 | 26 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1994 | 11 | 27 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1994 | 11 | 28 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1994 | 11 | 29 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
1994 | 11 | 30 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1994 | 12 | 1 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1994 | 12 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1994 | 12 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1994 | 12 | 4 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1994 | 12 | 5 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1994 | 12 | 6 | 304.3265 | 5 | 299.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1994 | 12 | 7 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1994 | 12 | 8 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1994 | 12 | 9 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1994 | 12 | 10 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1994 | 12 | 11 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1994 | 12 | 12 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1994 | 12 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1994 | 12 | 14 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1994 | 12 | 15 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1994 | 12 | 16 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 12 | 17 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1994 | 12 | 18 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1994 | 12 | 19 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1994 | 12 | 20 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1994 | 12 | 21 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1994 | 12 | 22 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1994 | 12 | 23 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1994 | 12 | 24 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1994 | 12 | 25 | 466.2857 | 5 | 461.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
1994 | 12 | 26 | 343.5102 | 5 | 338.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1994 | 12 | 27 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1994 | 12 | 28 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1994 | 12 | 29 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1994 | 12 | 30 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1994 | 12 | 31 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1995 | 1 | 1 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1995 | 1 | 2 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1995 | 1 | 3 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1995 | 1 | 4 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1995 | 1 | 5 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1995 | 1 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1995 | 1 | 7 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1995 | 1 | 8 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1995 | 1 | 9 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1995 | 1 | 10 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1995 | 1 | 11 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
1995 | 1 | 12 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1995 | 1 | 13 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1995 | 1 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1995 | 1 | 15 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1995 | 1 | 16 | 309.551 | 5 | 304.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1995 | 1 | 17 | 641.3061 | 5 | 636.3061 | 28.7174 | 139.3858 | 0.77441 | 27.943 | 89.27% | 294.4561 | 276.7887 | 6642.9287
1995 | 1 | 18 | 442.7755 | 5 | 437.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1995 | 1 | 19 | 286.0408 | 5 | 281.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
1995 | 1 | 20 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1995 | 1 | 21 | 624.3265 | 5 | 619.3265 | 28.7513 | 139.3858 | 0.77441 | 27.9769 | 89.27% | 294.8139 | 277.1251 | 6651.0019
1995 | 1 | 22 | 501.551 | 5 | 496.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
1995 | 1 | 23 | 339.5918 | 5 | 334.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1995 | 1 | 24 | 257.3061 | 5 | 252.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1995 | 1 | 25 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1995 | 1 | 26 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1995 | 1 | 27 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
1995 | 1 | 28 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1995 | 1 | 29 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1995 | 1 | 30 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1995 | 1 | 31 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1995 | 2 | 1 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1995 | 2 | 2 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1995 | 2 | 3 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1995 | 2 | 4 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1995 | 2 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1995 | 2 | 6 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1995 | 2 | 7 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1995 | 2 | 8 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1995 | 2 | 9 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1995 | 2 | 10 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1995 | 2 | 11 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1995 | 2 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1995 | 2 | 13 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1995 | 2 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1995 | 2 | 15 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1995 | 2 | 16 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1995 | 2 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1995 | 2 | 18 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1995 | 2 | 19 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1995 | 2 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1995 | 2 | 21 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1995 | 2 | 22 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1995 | 2 | 23 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1995 | 2 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1995 | 2 | 25 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1995 | 2 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1995 | 2 | 27 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1995 | 2 | 28 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1995 | 3 | 1 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1995 | 3 | 2 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1995 | 3 | 3 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1995 | 3 | 4 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1995 | 3 | 5 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1995 | 3 | 6 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1995 | 3 | 7 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1995 | 3 | 8 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1995 | 3 | 9 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
1995 | 3 | 10 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1995 | 3 | 11 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
1995 | 3 | 12 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1995 | 3 | 13 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1995 | 3 | 14 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1995 | 3 | 15 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1995 | 3 | 16 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1995 | 3 | 17 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1995 | 3 | 18 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1995 | 3 | 19 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
1995 | 3 | 20 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1995 | 3 | 21 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1995 | 3 | 22 | 762.7755 | 25 | 737.7755 | 28.4744 | 139.3858 | 0.77441 | 27.7 | 89.27% | 291.896 | 274.3823 | 6585.1745
1995 | 3 | 23 | 654.3673 | 25 | 629.3673 | 28.6913 | 139.3858 | 0.77441 | 27.9169 | 89.27% | 294.1808 | 276.5299 | 6636.7186
1995 | 3 | 24 | 496.3265 | 25 | 471.3265 | 29.0073 | 139.3858 | 0.77441 | 28.2329 | 89.27% | 297.5116 | 279.6609 | 6711.8611
1995 | 3 | 25 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1995 | 3 | 26 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1995 | 3 | 27 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1995 | 3 | 28 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1995 | 3 | 29 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
1995 | 3 | 30 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1995 | 3 | 31 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1995 | 4 | 1 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1995 | 4 | 2 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1995 | 4 | 3 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
1995 | 4 | 4 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1995 | 4 | 5 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1995 | 4 | 6 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1995 | 4 | 7 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1995 | 4 | 8 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1995 | 4 | 9 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1995 | 4 | 10 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1995 | 4 | 11 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1995 | 4 | 12 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
1995 | 4 | 13 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1995 | 4 | 14 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1995 | 4 | 15 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1995 | 4 | 16 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1995 | 4 | 17 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1995 | 4 | 18 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1995 | 4 | 19 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1995 | 4 | 20 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
1995 | 4 | 21 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1995 | 4 | 22 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
1995 | 4 | 23 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1995 | 4 | 24 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1995 | 4 | 25 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
1995 | 4 | 26 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1995 | 4 | 27 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
1995 | 4 | 28 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1995 | 4 | 29 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
1995 | 4 | 30 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1995 | 5 | 1 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1995 | 5 | 2 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1995 | 5 | 3 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1995 | 5 | 4 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1995 | 5 | 5 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1995 | 5 | 6 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1995 | 5 | 7 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1995 | 5 | 8 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1995 | 5 | 9 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1995 | 5 | 10 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1995 | 5 | 11 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1995 | 5 | 12 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1995 | 5 | 13 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1995 | 5 | 14 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1995 | 5 | 15 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1995 | 5 | 16 | 488.4898 | 25 | 463.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
1995 | 5 | 17 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
1995 | 5 | 18 | 449.3061 | 25 | 424.3061 | 29.1014 | 139.3858 | 0.77441 | 28.327 | 89.27% | 298.5026 | 280.5924 | 6734.2176
1995 | 5 | 19 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1995 | 5 | 20 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
1995 | 5 | 21 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1995 | 5 | 22 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1995 | 5 | 23 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1995 | 5 | 24 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1995 | 5 | 25 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1995 | 5 | 26 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1995 | 5 | 27 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1995 | 5 | 28 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1995 | 5 | 29 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1995 | 5 | 30 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1995 | 5 | 31 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1995 | 6 | 1 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1995 | 6 | 2 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1995 | 6 | 3 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1995 | 6 | 4 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1995 | 6 | 5 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1995 | 6 | 6 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1995 | 6 | 7 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1995 | 6 | 8 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1995 | 6 | 9 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1995 | 6 | 10 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1995 | 6 | 11 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1995 | 6 | 12 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1995 | 6 | 13 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
1995 | 6 | 14 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1995 | 6 | 15 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1995 | 6 | 16 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
1995 | 6 | 17 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1995 | 6 | 18 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1995 | 6 | 19 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1995 | 6 | 20 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1995 | 6 | 21 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1995 | 6 | 22 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
1995 | 6 | 23 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1995 | 6 | 24 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1995 | 6 | 25 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1995 | 6 | 26 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1995 | 6 | 27 | 14.3673 | 25 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1995 | 6 | 28 | 12.2776 | 25 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1995 | 6 | 29 | 11.4939 | 25 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1995 | 6 | 30 | 10.5796 | 25 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1995 | 7 | 1 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1995 | 7 | 2 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1995 | 7 | 3 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1995 | 7 | 4 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1995 | 7 | 5 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1995 | 7 | 6 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1995 | 7 | 7 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1995 | 7 | 8 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1995 | 7 | 9 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1995 | 7 | 10 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1995 | 7 | 11 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1995 | 7 | 12 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1995 | 7 | 13 | 6.5306 | 5 | 1.5306 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1995 | 7 | 14 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1995 | 7 | 15 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1995 | 7 | 16 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1995 | 7 | 17 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1995 | 7 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
1995 | 7 | 19 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1995 | 7 | 20 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1995 | 7 | 21 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1995 | 7 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1995 | 7 | 23 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
1995 | 7 | 24 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1995 | 7 | 25 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1995 | 7 | 26 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1995 | 7 | 27 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1995 | 7 | 28 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1995 | 7 | 29 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
1995 | 7 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1995 | 7 | 31 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1995 | 8 | 1 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1995 | 8 | 2 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1995 | 8 | 3 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1995 | 8 | 4 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
1995 | 8 | 5 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1995 | 8 | 6 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1995 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1995 | 8 | 8 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1995 | 8 | 9 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
1995 | 8 | 10 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1995 | 8 | 11 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
1995 | 8 | 12 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
1995 | 8 | 13 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1995 | 8 | 14 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1995 | 8 | 15 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1995 | 8 | 16 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
1995 | 8 | 17 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1995 | 8 | 18 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
1995 | 8 | 19 | 3.0041 | 5 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
1995 | 8 | 20 | 2.4816 | 5 | 0 | 29.995 | 0 | 0 | 29.995 | 0% | 0 | 0 | 0
1995 | 8 | 21 | 2.2204 | 5 | 0 | 29.9956 | 0 | 0 | 29.9956 | 0% | 0 | 0 | 0
1995 | 8 | 22 | 1.9592 | 5 | 0 | 29.9961 | 0 | 0 | 29.9961 | 0% | 0 | 0 | 0
1995 | 8 | 23 | 1.698 | 5 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
1995 | 8 | 24 | 1.5673 | 5 | 0 | 29.9969 | 0 | 0 | 29.9969 | 0% | 0 | 0 | 0
1995 | 8 | 25 | 1.4367 | 5 | 0 | 29.9971 | 0 | 0 | 29.9971 | 0% | 0 | 0 | 0
1995 | 8 | 26 | 1.3061 | 5 | 0 | 29.9974 | 0 | 0 | 29.9974 | 0% | 0 | 0 | 0
1995 | 8 | 27 | 1.3061 | 5 | 0 | 29.9974 | 0 | 0 | 29.9974 | 0% | 0 | 0 | 0
1995 | 8 | 28 | 1.2408 | 5 | 0 | 29.9975 | 0 | 0 | 29.9975 | 0% | 0 | 0 | 0
1995 | 8 | 29 | 1.2408 | 5 | 0 | 29.9975 | 0 | 0 | 29.9975 | 0% | 0 | 0 | 0
1995 | 8 | 30 | 1.2016 | 5 | 0 | 29.9976 | 0 | 0 | 29.9976 | 0% | 0 | 0 | 0
1995 | 8 | 31 | 1.1624 | 5 | 0 | 29.9977 | 0 | 0 | 29.9977 | 0% | 0 | 0 | 0
1995 | 9 | 1 | 1.1624 | 15 | 0 | 29.9977 | 0 | 0 | 29.9977 | 0% | 0 | 0 | 0
1995 | 9 | 2 | 1.1886 | 15 | 0 | 29.9976 | 0 | 0 | 29.9976 | 0% | 0 | 0 | 0
1995 | 9 | 3 | 1.1363 | 15 | 0 | 29.9977 | 0 | 0 | 29.9977 | 0% | 0 | 0 | 0
1995 | 9 | 4 | 1.1233 | 15 | 0 | 29.9978 | 0 | 0 | 29.9978 | 0% | 0 | 0 | 0
1995 | 9 | 5 | 1.1233 | 15 | 0 | 29.9978 | 0 | 0 | 29.9978 | 0% | 0 | 0 | 0
1995 | 9 | 6 | 1.1233 | 15 | 0 | 29.9978 | 0 | 0 | 29.9978 | 0% | 0 | 0 | 0
1995 | 9 | 7 | 1.0841 | 15 | 0 | 29.9978 | 0 | 0 | 29.9978 | 0% | 0 | 0 | 0
1995 | 9 | 8 | 1.0057 | 15 | 0 | 29.998 | 0 | 0 | 29.998 | 0% | 0 | 0 | 0
1995 | 9 | 9 | 0.95347 | 15 | 0 | 29.9981 | 0 | 0 | 29.9981 | 0% | 0 | 0 | 0
1995 | 9 | 10 | 1.0449 | 15 | 0 | 29.9979 | 0 | 0 | 29.9979 | 0% | 0 | 0 | 0
1995 | 9 | 11 | 1.0841 | 15 | 0 | 29.9978 | 0 | 0 | 29.9978 | 0% | 0 | 0 | 0
1995 | 9 | 12 | 1.0841 | 15 | 0 | 29.9978 | 0 | 0 | 29.9978 | 0% | 0 | 0 | 0
1995 | 9 | 13 | 1.0318 | 15 | 0 | 29.9979 | 0 | 0 | 29.9979 | 0% | 0 | 0 | 0
1995 | 9 | 14 | 0.96653 | 15 | 0 | 29.9981 | 0 | 0 | 29.9981 | 0% | 0 | 0 | 0
1995 | 9 | 15 | 0.90122 | 15 | 0 | 29.9982 | 0 | 0 | 29.9982 | 0% | 0 | 0 | 0
1995 | 9 | 16 | 0.8751 | 15 | 0 | 29.9982 | 0 | 0 | 29.9982 | 0% | 0 | 0 | 0
1995 | 9 | 17 | 0.84898 | 15 | 0 | 29.9983 | 0 | 0 | 29.9983 | 0% | 0 | 0 | 0
1995 | 9 | 18 | 0.94041 | 15 | 0 | 29.9981 | 0 | 0 | 29.9981 | 0% | 0 | 0 | 0
1995 | 9 | 19 | 1.0057 | 15 | 0 | 29.998 | 0 | 0 | 29.998 | 0% | 0 | 0 | 0
1995 | 9 | 20 | 0.90122 | 15 | 0 | 29.9982 | 0 | 0 | 29.9982 | 0% | 0 | 0 | 0
1995 | 9 | 21 | 0.86204 | 15 | 0 | 29.9983 | 0 | 0 | 29.9983 | 0% | 0 | 0 | 0
1995 | 9 | 22 | 0.97959 | 15 | 0 | 29.998 | 0 | 0 | 29.998 | 0% | 0 | 0 | 0
1995 | 9 | 23 | 2.2204 | 15 | 0 | 29.9956 | 0 | 0 | 29.9956 | 0% | 0 | 0 | 0
1995 | 9 | 24 | 3.6571 | 15 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
1995 | 9 | 25 | 3.3959 | 15 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
1995 | 9 | 26 | 3.1347 | 15 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
1995 | 9 | 27 | 3.3959 | 15 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
1995 | 9 | 28 | 3.7878 | 15 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
1995 | 9 | 29 | 4.049 | 15 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
1995 | 9 | 30 | 3.9184 | 15 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
1995 | 10 | 1 | 3.9184 | 15 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
1995 | 10 | 2 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1995 | 10 | 3 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1995 | 10 | 4 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1995 | 10 | 5 | 9.4041 | 15 | 0 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1995 | 10 | 6 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1995 | 10 | 7 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
1995 | 10 | 8 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1995 | 10 | 9 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1995 | 10 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1995 | 10 | 11 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
1995 | 10 | 12 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1995 | 10 | 13 | 9.7959 | 15 | 0 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1995 | 10 | 14 | 9.4041 | 15 | 0 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1995 | 10 | 15 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1995 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1995 | 10 | 17 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1995 | 10 | 18 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1995 | 10 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1995 | 10 | 20 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1995 | 10 | 21 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1995 | 10 | 22 | 539.4286 | 15 | 524.4286 | 28.9211 | 139.3858 | 0.77441 | 28.1467 | 89.27% | 296.6032 | 278.807 | 6691.3677
1995 | 10 | 23 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1995 | 10 | 24 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1995 | 10 | 25 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1995 | 10 | 26 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1995 | 10 | 27 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1995 | 10 | 28 | 1040.9796 | 15 | 1025.9796 | 27.918 | 139.3858 | 0.77441 | 27.1436 | 89.27% | 286.0327 | 268.8708 | 6452.8987
1995 | 10 | 29 | 1436.7347 | 15 | 1421.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1995 | 10 | 30 | 565.551 | 15 | 550.551 | 28.8689 | 139.3858 | 0.77441 | 28.0945 | 89.27% | 296.0526 | 278.2895 | 6678.9474
1995 | 10 | 31 | 330.449 | 15 | 315.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1995 | 11 | 1 | 239.0204 | 15 | 224.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1995 | 11 | 2 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1995 | 11 | 3 | 391.8367 | 15 | 376.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
1995 | 11 | 4 | 300.4082 | 15 | 285.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
1995 | 11 | 5 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1995 | 11 | 6 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1995 | 11 | 7 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1995 | 11 | 8 | 407.5102 | 15 | 392.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1995 | 11 | 9 | 318.6939 | 15 | 303.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1995 | 11 | 10 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1995 | 11 | 11 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1995 | 11 | 12 | 850.2857 | 15 | 835.2857 | 28.2994 | 139.3858 | 0.77441 | 27.525 | 89.27% | 290.0517 | 272.6486 | 6543.5666
1995 | 11 | 13 | 1016.1633 | 15 | 1001.1633 | 27.9677 | 139.3858 | 0.77441 | 27.1933 | 89.27% | 286.5558 | 269.3624 | 6464.6979
1995 | 11 | 14 | 497.6327 | 15 | 482.6327 | 29.0047 | 139.3858 | 0.77441 | 28.2303 | 89.27% | 297.484 | 279.635 | 6711.2401
1995 | 11 | 15 | 1080.1633 | 15 | 1065.1633 | 27.8397 | 139.3858 | 0.77441 | 27.0653 | 89.27% | 285.2069 | 268.0945 | 6434.2683
1995 | 11 | 16 | 1289.1429 | 15 | 1274.1429 | 27.4217 | 139.3858 | 0.77441 | 26.6473 | 89.27% | 280.8026 | 263.9544 | 6334.9062
1995 | 11 | 17 | 687.0204 | 15 | 672.0204 | 28.626 | 139.3858 | 0.77441 | 27.8515 | 89.27% | 293.4926 | 275.8831 | 6621.1932
1995 | 11 | 18 | 442.7755 | 15 | 427.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
1995 | 11 | 19 | 347.4286 | 15 | 332.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
1995 | 11 | 20 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1995 | 11 | 21 | 293.8776 | 15 | 278.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
1995 | 11 | 22 | 303.0204 | 15 | 288.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1995 | 11 | 23 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
1995 | 11 | 24 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1995 | 11 | 25 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1995 | 11 | 26 | 181.551 | 15 | 166.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1995 | 11 | 27 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1995 | 11 | 28 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1995 | 11 | 29 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1995 | 11 | 30 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1995 | 12 | 1 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1995 | 12 | 2 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1995 | 12 | 3 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1995 | 12 | 4 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1995 | 12 | 5 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1995 | 12 | 6 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1995 | 12 | 7 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1995 | 12 | 8 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1995 | 12 | 9 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1995 | 12 | 10 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1995 | 12 | 11 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1995 | 12 | 12 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1995 | 12 | 13 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1995 | 12 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1995 | 12 | 15 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1995 | 12 | 16 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1995 | 12 | 17 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1995 | 12 | 18 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1995 | 12 | 19 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1995 | 12 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1995 | 12 | 21 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1995 | 12 | 22 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1995 | 12 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1995 | 12 | 24 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1995 | 12 | 25 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1995 | 12 | 26 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1995 | 12 | 27 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1995 | 12 | 28 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1995 | 12 | 29 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1995 | 12 | 30 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1995 | 12 | 31 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1996 | 1 | 1 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1996 | 1 | 2 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1996 | 1 | 3 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1996 | 1 | 4 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1996 | 1 | 5 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1996 | 1 | 6 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1996 | 1 | 7 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1996 | 1 | 8 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1996 | 1 | 9 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1996 | 1 | 10 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1996 | 1 | 11 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1996 | 1 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1996 | 1 | 13 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1996 | 1 | 14 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1996 | 1 | 15 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1996 | 1 | 16 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1996 | 1 | 17 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1996 | 1 | 18 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1996 | 1 | 19 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1996 | 1 | 20 | 1277.3878 | 5 | 1272.3878 | 27.4452 | 139.3858 | 0.77441 | 26.6708 | 89.27% | 281.0503 | 264.1873 | 6340.4953
1996 | 1 | 21 | 892.0816 | 5 | 887.0816 | 28.2158 | 139.3858 | 0.77441 | 27.4414 | 89.27% | 289.1708 | 271.8206 | 6523.6942
1996 | 1 | 22 | 510.6939 | 5 | 505.6939 | 28.9786 | 139.3858 | 0.77441 | 28.2042 | 89.27% | 297.2088 | 279.3763 | 6705.03
1996 | 1 | 23 | 365.7143 | 5 | 360.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1996 | 1 | 24 | 343.5102 | 5 | 338.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
1996 | 1 | 25 | 909.0612 | 5 | 904.0612 | 28.1819 | 139.3858 | 0.77441 | 27.4075 | 89.27% | 288.813 | 271.4842 | 6515.621
1996 | 1 | 26 | 586.449 | 5 | 581.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
1996 | 1 | 27 | 531.5918 | 5 | 526.5918 | 28.9368 | 139.3858 | 0.77441 | 28.1624 | 89.27% | 296.7683 | 278.9622 | 6695.0938
1996 | 1 | 28 | 2076.7347 | 5 | 2071.7347 | 25.8465 | 139.3858 | 0.77441 | 25.0721 | 89.27% | 264.2037 | 248.3515 | 5960.4352
1996 | 1 | 29 | 1157.2245 | 5 | 1152.2245 | 27.6856 | 139.3858 | 0.77441 | 26.9111 | 89.27% | 283.5828 | 266.5679 | 6397.6285
1996 | 1 | 30 | 658.2857 | 5 | 653.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
1996 | 1 | 31 | 454.5306 | 5 | 449.5306 | 29.0909 | 139.3858 | 0.77441 | 28.3165 | 89.27% | 298.3924 | 280.4889 | 6731.7336
1996 | 2 | 1 | 318.6939 | 5 | 313.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
1996 | 2 | 2 | 279.5102 | 5 | 274.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1996 | 2 | 3 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1996 | 2 | 4 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1996 | 2 | 5 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1996 | 2 | 6 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1996 | 2 | 7 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1996 | 2 | 8 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1996 | 2 | 9 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1996 | 2 | 10 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1996 | 2 | 11 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1996 | 2 | 12 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1996 | 2 | 13 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1996 | 2 | 14 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1996 | 2 | 15 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1996 | 2 | 16 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1996 | 2 | 17 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1996 | 2 | 18 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1996 | 2 | 19 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1996 | 2 | 20 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1996 | 2 | 21 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1996 | 2 | 22 | 700.0816 | 5 | 695.0816 | 28.5998 | 139.3858 | 0.77441 | 27.8254 | 89.27% | 293.2173 | 275.6243 | 6614.9831
1996 | 2 | 23 | 1068.4082 | 5 | 1063.4082 | 27.8632 | 139.3858 | 0.77441 | 27.0888 | 89.27% | 285.4547 | 268.3274 | 6439.8574
1996 | 2 | 24 | 931.2653 | 5 | 926.2653 | 28.1375 | 139.3858 | 0.77441 | 27.3631 | 89.27% | 288.345 | 271.0443 | 6505.0638
1996 | 2 | 25 | 941.7143 | 5 | 936.7143 | 28.1166 | 139.3858 | 0.77441 | 27.3422 | 89.27% | 288.1248 | 270.8373 | 6500.0957
1996 | 2 | 26 | 608.6531 | 5 | 603.6531 | 28.7827 | 139.3858 | 0.77441 | 28.0083 | 89.27% | 295.1442 | 277.4356 | 6658.454
1996 | 2 | 27 | 437.551 | 5 | 432.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
1996 | 2 | 28 | 389.2245 | 5 | 384.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
1996 | 2 | 29 | 380.0816 | 5 | 375.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1996 | 3 | 1 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1996 | 3 | 2 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1996 | 3 | 3 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1996 | 3 | 4 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1996 | 3 | 5 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1996 | 3 | 6 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1996 | 3 | 7 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
1996 | 3 | 8 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1996 | 3 | 9 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
1996 | 3 | 10 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
1996 | 3 | 11 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1996 | 3 | 12 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1996 | 3 | 13 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1996 | 3 | 14 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1996 | 3 | 15 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
1996 | 3 | 16 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
1996 | 3 | 17 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1996 | 3 | 18 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
1996 | 3 | 19 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1996 | 3 | 20 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1996 | 3 | 21 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1996 | 3 | 22 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1996 | 3 | 23 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
1996 | 3 | 24 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1996 | 3 | 25 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1996 | 3 | 26 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1996 | 3 | 27 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1996 | 3 | 28 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
1996 | 3 | 29 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1996 | 3 | 30 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
1996 | 3 | 31 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1996 | 4 | 1 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1996 | 4 | 2 | 382.6939 | 25 | 357.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
1996 | 4 | 3 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1996 | 4 | 4 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
1996 | 4 | 5 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1996 | 4 | 6 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
1996 | 4 | 7 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
1996 | 4 | 8 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1996 | 4 | 9 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1996 | 4 | 10 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1996 | 4 | 11 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1996 | 4 | 12 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1996 | 4 | 13 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
1996 | 4 | 14 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1996 | 4 | 15 | 384 | 25 | 359 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
1996 | 4 | 16 | 705.3061 | 25 | 680.3061 | 28.5894 | 139.3858 | 0.77441 | 27.815 | 89.27% | 293.1072 | 275.5208 | 6612.499
1996 | 4 | 17 | 3369.7959 | 25 | 3344.7959 | 23.2604 | 0 | 0 | 23.2604 | 0% | 0 | 0 | 0
1996 | 4 | 18 | 1671.8367 | 25 | 1646.8367 | 26.6563 | 139.3858 | 0.77441 | 25.8819 | 89.27% | 272.7371 | 256.3729 | 6152.9493
1996 | 4 | 19 | 1016.1633 | 25 | 991.1633 | 27.9677 | 139.3858 | 0.77441 | 27.1933 | 89.27% | 286.5558 | 269.3624 | 6464.6979
1996 | 4 | 20 | 796.7347 | 25 | 771.7347 | 28.4065 | 139.3858 | 0.77441 | 27.6321 | 89.27% | 291.1803 | 273.7095 | 6569.0281
1996 | 4 | 21 | 790.2041 | 25 | 765.2041 | 28.4196 | 139.3858 | 0.77441 | 27.6452 | 89.27% | 291.318 | 273.8389 | 6572.1332
1996 | 4 | 22 | 782.3673 | 25 | 757.3673 | 28.4353 | 139.3858 | 0.77441 | 27.6609 | 89.27% | 291.4831 | 273.9941 | 6575.8593
1996 | 4 | 23 | 664.8163 | 25 | 639.8163 | 28.6704 | 139.3858 | 0.77441 | 27.896 | 89.27% | 293.9606 | 276.3229 | 6631.7504
1996 | 4 | 24 | 1076.2449 | 25 | 1051.2449 | 27.8475 | 139.3858 | 0.77441 | 27.0731 | 89.27% | 285.2895 | 268.1721 | 6436.1313
1996 | 4 | 25 | 732.7347 | 25 | 707.7347 | 28.5345 | 139.3858 | 0.77441 | 27.7601 | 89.27% | 292.5292 | 274.9774 | 6599.4578
1996 | 4 | 26 | 502.8571 | 25 | 477.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
1996 | 4 | 27 | 471.5102 | 25 | 446.5102 | 29.057 | 139.3858 | 0.77441 | 28.2826 | 89.27% | 298.0346 | 280.1525 | 6723.6604
1996 | 4 | 28 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1996 | 4 | 29 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
1996 | 4 | 30 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1996 | 5 | 1 | 488.4898 | 25 | 463.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
1996 | 5 | 2 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1996 | 5 | 3 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1996 | 5 | 4 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
1996 | 5 | 5 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
1996 | 5 | 6 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1996 | 5 | 7 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1996 | 5 | 8 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1996 | 5 | 9 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1996 | 5 | 10 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1996 | 5 | 11 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
1996 | 5 | 12 | 837.2245 | 25 | 812.2245 | 28.3256 | 139.3858 | 0.77441 | 27.5511 | 89.27% | 290.327 | 272.9074 | 6549.7767
1996 | 5 | 13 | 641.3061 | 25 | 616.3061 | 28.7174 | 139.3858 | 0.77441 | 27.943 | 89.27% | 294.4561 | 276.7887 | 6642.9287
1996 | 5 | 14 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
1996 | 5 | 15 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
1996 | 5 | 16 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1996 | 5 | 17 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1996 | 5 | 18 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1996 | 5 | 19 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1996 | 5 | 20 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1996 | 5 | 21 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1996 | 5 | 22 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1996 | 5 | 23 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
1996 | 5 | 24 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1996 | 5 | 25 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1996 | 5 | 26 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1996 | 5 | 27 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1996 | 5 | 28 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1996 | 5 | 29 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1996 | 5 | 30 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1996 | 5 | 31 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1996 | 6 | 1 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
1996 | 6 | 2 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
1996 | 6 | 3 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1996 | 6 | 4 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1996 | 6 | 5 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1996 | 6 | 6 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1996 | 6 | 7 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1996 | 6 | 8 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1996 | 6 | 9 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1996 | 6 | 10 | 275.5918 | 25 | 250.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
1996 | 6 | 11 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1996 | 6 | 12 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1996 | 6 | 13 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1996 | 6 | 14 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1996 | 6 | 15 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
1996 | 6 | 16 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1996 | 6 | 17 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1996 | 6 | 18 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1996 | 6 | 19 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1996 | 6 | 20 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1996 | 6 | 21 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1996 | 6 | 22 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1996 | 6 | 23 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1996 | 6 | 24 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1996 | 6 | 25 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1996 | 6 | 26 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1996 | 6 | 27 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
1996 | 6 | 28 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1996 | 6 | 29 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1996 | 6 | 30 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1996 | 7 | 1 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1996 | 7 | 2 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1996 | 7 | 3 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1996 | 7 | 4 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1996 | 7 | 5 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1996 | 7 | 6 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
1996 | 7 | 7 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1996 | 7 | 8 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1996 | 7 | 9 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
1996 | 7 | 10 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1996 | 7 | 11 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1996 | 7 | 12 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1996 | 7 | 13 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1996 | 7 | 14 | 1737.1429 | 5 | 1732.1429 | 26.5257 | 139.3858 | 0.77441 | 25.7513 | 89.27% | 271.3608 | 255.0791 | 6121.8986
1996 | 7 | 15 | 1030.5306 | 5 | 1025.5306 | 27.9389 | 139.3858 | 0.77441 | 27.1645 | 89.27% | 286.253 | 269.0778 | 6457.8668
1996 | 7 | 16 | 881.6327 | 5 | 876.6327 | 28.2367 | 139.3858 | 0.77441 | 27.4623 | 89.27% | 289.3911 | 272.0276 | 6528.6623
1996 | 7 | 17 | 616.4898 | 5 | 611.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
1996 | 7 | 18 | 359.1837 | 5 | 354.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
1996 | 7 | 19 | 270.3673 | 5 | 265.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
1996 | 7 | 20 | 651.7551 | 5 | 646.7551 | 28.6965 | 139.3858 | 0.77441 | 27.9221 | 89.27% | 294.2358 | 276.5817 | 6637.9606
1996 | 7 | 21 | 395.7551 | 5 | 390.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1996 | 7 | 22 | 259.9184 | 5 | 254.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1996 | 7 | 23 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1996 | 7 | 24 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
1996 | 7 | 25 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1996 | 7 | 26 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
1996 | 7 | 27 | 244.2449 | 5 | 239.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1996 | 7 | 28 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1996 | 7 | 29 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1996 | 7 | 30 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1996 | 7 | 31 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1996 | 8 | 1 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1996 | 8 | 2 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1996 | 8 | 3 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
1996 | 8 | 4 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1996 | 8 | 5 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1996 | 8 | 6 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1996 | 8 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1996 | 8 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1996 | 8 | 9 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1996 | 8 | 10 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1996 | 8 | 11 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1996 | 8 | 12 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1996 | 8 | 13 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1996 | 8 | 14 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1996 | 8 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1996 | 8 | 16 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1996 | 8 | 17 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1996 | 8 | 18 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1996 | 8 | 19 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1996 | 8 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1996 | 8 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1996 | 8 | 22 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1996 | 8 | 23 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
1996 | 8 | 24 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1996 | 8 | 25 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1996 | 8 | 26 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1996 | 8 | 27 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1996 | 8 | 28 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1996 | 8 | 29 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1996 | 8 | 30 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1996 | 8 | 31 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1996 | 9 | 1 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
1996 | 9 | 2 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1996 | 9 | 3 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
1996 | 9 | 4 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1996 | 9 | 5 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1996 | 9 | 6 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1996 | 9 | 7 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1996 | 9 | 8 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1996 | 9 | 9 | 8.751 | 15 | 0 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
1996 | 9 | 10 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1996 | 9 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1996 | 9 | 12 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1996 | 9 | 13 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
1996 | 9 | 14 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1996 | 9 | 15 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1996 | 9 | 16 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
1996 | 9 | 17 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1996 | 9 | 18 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
1996 | 9 | 19 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1996 | 9 | 20 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1996 | 9 | 21 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1996 | 9 | 22 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1996 | 9 | 23 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
1996 | 9 | 24 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1996 | 9 | 25 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1996 | 9 | 26 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1996 | 9 | 27 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1996 | 9 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1996 | 9 | 29 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
1996 | 9 | 30 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1996 | 10 | 1 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1996 | 10 | 2 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
1996 | 10 | 3 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
1996 | 10 | 4 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1996 | 10 | 5 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1996 | 10 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1996 | 10 | 7 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1996 | 10 | 8 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1996 | 10 | 9 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1996 | 10 | 10 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1996 | 10 | 11 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
1996 | 10 | 12 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1996 | 10 | 13 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1996 | 10 | 14 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
1996 | 10 | 15 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1996 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1996 | 10 | 17 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1996 | 10 | 18 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1996 | 10 | 19 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
1996 | 10 | 20 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1996 | 10 | 21 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1996 | 10 | 22 | 2324.898 | 15 | 2309.898 | 25.3502 | 139.3858 | 0.77441 | 24.5758 | 89.27% | 258.9735 | 243.4351 | 5842.4427
1996 | 10 | 23 | 1358.3673 | 15 | 1343.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
1996 | 10 | 24 | 637.3878 | 15 | 622.3878 | 28.7252 | 139.3858 | 0.77441 | 27.9508 | 89.27% | 294.5386 | 276.8663 | 6644.7917
1996 | 10 | 25 | 390.5306 | 15 | 375.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1996 | 10 | 26 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1996 | 10 | 27 | 203.7551 | 15 | 188.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1996 | 10 | 28 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1996 | 10 | 29 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1996 | 10 | 30 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
1996 | 10 | 31 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1996 | 11 | 1 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1996 | 11 | 2 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1996 | 11 | 3 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1996 | 11 | 4 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1996 | 11 | 5 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1996 | 11 | 6 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1996 | 11 | 7 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1996 | 11 | 8 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1996 | 11 | 9 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1996 | 11 | 10 | 402.2857 | 15 | 387.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
1996 | 11 | 11 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
1996 | 11 | 12 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1996 | 11 | 13 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1996 | 11 | 14 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1996 | 11 | 15 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1996 | 11 | 16 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1996 | 11 | 17 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1996 | 11 | 18 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1996 | 11 | 19 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1996 | 11 | 20 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1996 | 11 | 21 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1996 | 11 | 22 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1996 | 11 | 23 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1996 | 11 | 24 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1996 | 11 | 25 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
1996 | 11 | 26 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1996 | 11 | 27 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1996 | 11 | 28 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1996 | 11 | 29 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1996 | 11 | 30 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1996 | 12 | 1 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1996 | 12 | 2 | 1632.6531 | 5 | 1627.6531 | 26.7347 | 139.3858 | 0.77441 | 25.9603 | 89.27% | 273.5629 | 257.1492 | 6171.5797
1996 | 12 | 3 | 1475.9184 | 5 | 1470.9184 | 27.0482 | 139.3858 | 0.77441 | 26.2738 | 89.27% | 276.8662 | 260.2542 | 6246.1013
1996 | 12 | 4 | 650.449 | 5 | 645.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
1996 | 12 | 5 | 385.3061 | 5 | 380.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
1996 | 12 | 6 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1996 | 12 | 7 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1996 | 12 | 8 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1996 | 12 | 9 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1996 | 12 | 10 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1996 | 12 | 11 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1996 | 12 | 12 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
1996 | 12 | 13 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1996 | 12 | 14 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1996 | 12 | 15 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1996 | 12 | 16 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1996 | 12 | 17 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1996 | 12 | 18 | 397.0612 | 5 | 392.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1996 | 12 | 19 | 471.5102 | 5 | 466.5102 | 29.057 | 139.3858 | 0.77441 | 28.2826 | 89.27% | 298.0346 | 280.1525 | 6723.6604
1996 | 12 | 20 | 549.8776 | 5 | 544.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
1996 | 12 | 21 | 335.6735 | 5 | 330.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
1996 | 12 | 22 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1996 | 12 | 23 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
1996 | 12 | 24 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1996 | 12 | 25 | 689.6327 | 5 | 684.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
1996 | 12 | 26 | 433.6327 | 5 | 428.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
1996 | 12 | 27 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1996 | 12 | 28 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1996 | 12 | 29 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1996 | 12 | 30 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
1996 | 12 | 31 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1997 | 1 | 1 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1997 | 1 | 2 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1997 | 1 | 3 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1997 | 1 | 4 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1997 | 1 | 5 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1997 | 1 | 6 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
1997 | 1 | 7 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1997 | 1 | 8 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1997 | 1 | 9 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
1997 | 1 | 10 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1997 | 1 | 11 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1997 | 1 | 12 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
1997 | 1 | 13 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1997 | 1 | 14 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1997 | 1 | 15 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1997 | 1 | 16 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1997 | 1 | 17 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1997 | 1 | 18 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1997 | 1 | 19 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1997 | 1 | 20 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1997 | 1 | 21 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1997 | 1 | 22 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1997 | 1 | 23 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1997 | 1 | 24 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1997 | 1 | 25 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1997 | 1 | 26 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1997 | 1 | 27 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1997 | 1 | 28 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1997 | 1 | 29 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1997 | 1 | 30 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1997 | 1 | 31 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1997 | 2 | 1 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1997 | 2 | 2 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1997 | 2 | 3 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1997 | 2 | 4 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1997 | 2 | 5 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1997 | 2 | 6 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1997 | 2 | 7 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1997 | 2 | 8 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1997 | 2 | 9 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1997 | 2 | 10 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1997 | 2 | 11 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1997 | 2 | 12 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1997 | 2 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1997 | 2 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1997 | 2 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1997 | 2 | 16 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1997 | 2 | 17 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1997 | 2 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1997 | 2 | 19 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1997 | 2 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1997 | 2 | 21 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1997 | 2 | 22 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1997 | 2 | 23 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
1997 | 2 | 24 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1997 | 2 | 25 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1997 | 2 | 26 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1997 | 2 | 27 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
1997 | 2 | 28 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1997 | 3 | 1 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1997 | 3 | 2 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
1997 | 3 | 3 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1997 | 3 | 4 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
1997 | 3 | 5 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1997 | 3 | 6 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
1997 | 3 | 7 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1997 | 3 | 8 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1997 | 3 | 9 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1997 | 3 | 10 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1997 | 3 | 11 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1997 | 3 | 12 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1997 | 3 | 13 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1997 | 3 | 14 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
1997 | 3 | 15 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1997 | 3 | 16 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1997 | 3 | 17 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1997 | 3 | 18 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1997 | 3 | 19 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1997 | 3 | 20 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1997 | 3 | 21 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1997 | 3 | 22 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1997 | 3 | 23 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1997 | 3 | 24 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1997 | 3 | 25 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
1997 | 3 | 26 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
1997 | 3 | 27 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1997 | 3 | 28 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1997 | 3 | 29 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1997 | 3 | 30 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1997 | 3 | 31 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1997 | 4 | 1 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
1997 | 4 | 2 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1997 | 4 | 3 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1997 | 4 | 4 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
1997 | 4 | 5 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1997 | 4 | 6 | 638.6939 | 25 | 613.6939 | 28.7226 | 139.3858 | 0.77441 | 27.9482 | 89.27% | 294.5111 | 276.8404 | 6644.1707
1997 | 4 | 7 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1997 | 4 | 8 | 1116.7347 | 25 | 1091.7347 | 27.7665 | 139.3858 | 0.77441 | 26.9921 | 89.27% | 284.4362 | 267.37 | 6416.8799
1997 | 4 | 9 | 654.3673 | 25 | 629.3673 | 28.6913 | 139.3858 | 0.77441 | 27.9169 | 89.27% | 294.1808 | 276.5299 | 6636.7186
1997 | 4 | 10 | 420.5714 | 25 | 395.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1997 | 4 | 11 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
1997 | 4 | 12 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1997 | 4 | 13 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
1997 | 4 | 14 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1997 | 4 | 15 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
1997 | 4 | 16 | 441.4694 | 25 | 416.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
1997 | 4 | 17 | 626.9388 | 25 | 601.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
1997 | 4 | 18 | 1201.6327 | 25 | 1176.6327 | 27.5967 | 139.3858 | 0.77441 | 26.8223 | 89.27% | 282.6469 | 265.6881 | 6376.514
1997 | 4 | 19 | 2546.9388 | 25 | 2521.9388 | 24.9061 | 0 | 0 | 24.9061 | 0% | 0 | 0 | 0
1997 | 4 | 20 | 1697.9592 | 25 | 1672.9592 | 26.6041 | 139.3858 | 0.77441 | 25.8297 | 89.27% | 272.1866 | 255.8554 | 6140.529
1997 | 4 | 21 | 1133.7143 | 25 | 1108.7143 | 27.7326 | 139.3858 | 0.77441 | 26.9582 | 89.27% | 284.0783 | 267.0336 | 6408.8067
1997 | 4 | 22 | 876.4082 | 25 | 851.4082 | 28.2472 | 139.3858 | 0.77441 | 27.4728 | 89.27% | 289.5012 | 272.1311 | 6531.1463
1997 | 4 | 23 | 740.5714 | 25 | 715.5714 | 28.5189 | 139.3858 | 0.77441 | 27.7444 | 89.27% | 292.364 | 274.8222 | 6595.7317
1997 | 4 | 24 | 636.0816 | 25 | 611.0816 | 28.7278 | 139.3858 | 0.77441 | 27.9534 | 89.27% | 294.5662 | 276.8922 | 6645.4127
1997 | 4 | 25 | 488.4898 | 25 | 463.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
1997 | 4 | 26 | 408.8163 | 25 | 383.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
1997 | 4 | 27 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1997 | 4 | 28 | 481.9592 | 25 | 456.9592 | 29.0361 | 139.3858 | 0.77441 | 28.2617 | 89.27% | 297.8144 | 279.9455 | 6718.6923
1997 | 4 | 29 | 835.9184 | 25 | 810.9184 | 28.3282 | 139.3858 | 0.77441 | 27.5538 | 89.27% | 290.3545 | 272.9332 | 6550.3977
1997 | 4 | 30 | 515.9184 | 25 | 490.9184 | 28.9682 | 139.3858 | 0.77441 | 28.1938 | 89.27% | 297.0987 | 279.2727 | 6702.5459
1997 | 5 | 1 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
1997 | 5 | 2 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
1997 | 5 | 3 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1997 | 5 | 4 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
1997 | 5 | 5 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1997 | 5 | 6 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1997 | 5 | 7 | 492.4082 | 25 | 467.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
1997 | 5 | 8 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1997 | 5 | 9 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
1997 | 5 | 10 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1997 | 5 | 11 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1997 | 5 | 12 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1997 | 5 | 13 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
1997 | 5 | 14 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1997 | 5 | 15 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1997 | 5 | 16 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
1997 | 5 | 17 | 372.2449 | 25 | 347.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
1997 | 5 | 18 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
1997 | 5 | 19 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1997 | 5 | 20 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1997 | 5 | 21 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1997 | 5 | 22 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
1997 | 5 | 23 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1997 | 5 | 24 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
1997 | 5 | 25 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1997 | 5 | 26 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1997 | 5 | 27 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
1997 | 5 | 28 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
1997 | 5 | 29 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1997 | 5 | 30 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1997 | 5 | 31 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
1997 | 6 | 1 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
1997 | 6 | 2 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
1997 | 6 | 3 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
1997 | 6 | 4 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1997 | 6 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1997 | 6 | 6 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
1997 | 6 | 7 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1997 | 6 | 8 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
1997 | 6 | 9 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1997 | 6 | 10 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
1997 | 6 | 11 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1997 | 6 | 12 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1997 | 6 | 13 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1997 | 6 | 14 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1997 | 6 | 15 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
1997 | 6 | 16 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
1997 | 6 | 17 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1997 | 6 | 18 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1997 | 6 | 19 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
1997 | 6 | 20 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1997 | 6 | 21 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
1997 | 6 | 22 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
1997 | 6 | 23 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1997 | 6 | 24 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
1997 | 6 | 25 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
1997 | 6 | 26 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
1997 | 6 | 27 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1997 | 6 | 28 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1997 | 6 | 29 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1997 | 6 | 30 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1997 | 7 | 1 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1997 | 7 | 2 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1997 | 7 | 3 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1997 | 7 | 4 | 504.1633 | 5 | 499.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
1997 | 7 | 5 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
1997 | 7 | 6 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1997 | 7 | 7 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1997 | 7 | 8 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1997 | 7 | 9 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1997 | 7 | 10 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1997 | 7 | 11 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
1997 | 7 | 12 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1997 | 7 | 13 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1997 | 7 | 14 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1997 | 7 | 15 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1997 | 7 | 16 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1997 | 7 | 17 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1997 | 7 | 18 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1997 | 7 | 19 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1997 | 7 | 20 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1997 | 7 | 21 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1997 | 7 | 22 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1997 | 7 | 23 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1997 | 7 | 24 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1997 | 7 | 25 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1997 | 7 | 26 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1997 | 7 | 27 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1997 | 7 | 28 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1997 | 7 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1997 | 7 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1997 | 7 | 31 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1997 | 8 | 1 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
1997 | 8 | 2 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
1997 | 8 | 3 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
1997 | 8 | 4 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1997 | 8 | 5 | 10.7102 | 5 | 5.7102 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
1997 | 8 | 6 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1997 | 8 | 7 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1997 | 8 | 8 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1997 | 8 | 9 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1997 | 8 | 10 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1997 | 8 | 11 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1997 | 8 | 12 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1997 | 8 | 13 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1997 | 8 | 14 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1997 | 8 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1997 | 8 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1997 | 8 | 17 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1997 | 8 | 18 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
1997 | 8 | 19 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1997 | 8 | 20 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
1997 | 8 | 21 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1997 | 8 | 22 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1997 | 8 | 23 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1997 | 8 | 24 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1997 | 8 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1997 | 8 | 26 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1997 | 8 | 27 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1997 | 8 | 28 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1997 | 8 | 29 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1997 | 8 | 30 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1997 | 8 | 31 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1997 | 9 | 1 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1997 | 9 | 2 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1997 | 9 | 3 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
1997 | 9 | 4 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1997 | 9 | 5 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
1997 | 9 | 6 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1997 | 9 | 7 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1997 | 9 | 8 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1997 | 9 | 9 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1997 | 9 | 10 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1997 | 9 | 11 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1997 | 9 | 12 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
1997 | 9 | 13 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1997 | 9 | 14 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1997 | 9 | 15 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1997 | 9 | 16 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1997 | 9 | 17 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
1997 | 9 | 18 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1997 | 9 | 19 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1997 | 9 | 20 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1997 | 9 | 21 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1997 | 9 | 22 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
1997 | 9 | 23 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 9 | 24 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1997 | 9 | 25 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1997 | 9 | 26 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1997 | 9 | 27 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1997 | 9 | 28 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1997 | 9 | 29 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1997 | 9 | 30 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1997 | 10 | 1 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
1997 | 10 | 2 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1997 | 10 | 3 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
1997 | 10 | 4 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
1997 | 10 | 5 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1997 | 10 | 6 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
1997 | 10 | 7 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
1997 | 10 | 8 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
1997 | 10 | 9 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
1997 | 10 | 10 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1997 | 10 | 11 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
1997 | 10 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 14 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 15 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 16 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 17 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 18 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 19 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 20 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 21 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 22 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
1997 | 10 | 23 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 24 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 25 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1997 | 10 | 26 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
1997 | 10 | 27 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
1997 | 10 | 28 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1997 | 10 | 29 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1997 | 10 | 30 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1997 | 10 | 31 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
1997 | 11 | 1 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
1997 | 11 | 2 | 1064.4898 | 15 | 1049.4898 | 27.871 | 139.3858 | 0.77441 | 27.0966 | 89.27% | 285.5373 | 268.405 | 6441.7204
1997 | 11 | 3 | 1155.9184 | 15 | 1140.9184 | 27.6882 | 139.3858 | 0.77441 | 26.9138 | 89.27% | 283.6104 | 266.5937 | 6398.2495
1997 | 11 | 4 | 531.5918 | 15 | 516.5918 | 28.9368 | 139.3858 | 0.77441 | 28.1624 | 89.27% | 296.7683 | 278.9622 | 6695.0938
1997 | 11 | 5 | 420.5714 | 15 | 405.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
1997 | 11 | 6 | 288.6531 | 15 | 273.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1997 | 11 | 7 | 219.4286 | 15 | 204.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1997 | 11 | 8 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1997 | 11 | 9 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1997 | 11 | 10 | 373.551 | 15 | 358.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1997 | 11 | 11 | 266.449 | 15 | 251.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1997 | 11 | 12 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
1997 | 11 | 13 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1997 | 11 | 14 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1997 | 11 | 15 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1997 | 11 | 16 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
1997 | 11 | 17 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
1997 | 11 | 18 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1997 | 11 | 19 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1997 | 11 | 20 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1997 | 11 | 21 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1997 | 11 | 22 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1997 | 11 | 23 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
1997 | 11 | 24 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1997 | 11 | 25 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1997 | 11 | 26 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1997 | 11 | 27 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
1997 | 11 | 28 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1997 | 11 | 29 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1997 | 11 | 30 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1997 | 12 | 1 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1997 | 12 | 2 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1997 | 12 | 3 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
1997 | 12 | 4 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1997 | 12 | 5 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1997 | 12 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1997 | 12 | 7 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1997 | 12 | 8 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1997 | 12 | 9 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1997 | 12 | 10 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
1997 | 12 | 11 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1997 | 12 | 12 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1997 | 12 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1997 | 12 | 14 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1997 | 12 | 15 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1997 | 12 | 16 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1997 | 12 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1997 | 12 | 18 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1997 | 12 | 19 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1997 | 12 | 20 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1997 | 12 | 21 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1997 | 12 | 22 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1997 | 12 | 23 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1997 | 12 | 24 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
1997 | 12 | 25 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
1997 | 12 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1997 | 12 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1997 | 12 | 28 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1997 | 12 | 29 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1997 | 12 | 30 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1997 | 12 | 31 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1998 | 1 | 1 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
1998 | 1 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1998 | 1 | 3 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1998 | 1 | 4 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1998 | 1 | 5 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1998 | 1 | 6 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1998 | 1 | 7 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
1998 | 1 | 8 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1998 | 1 | 9 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1998 | 1 | 10 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1998 | 1 | 11 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1998 | 1 | 12 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1998 | 1 | 13 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
1998 | 1 | 14 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1998 | 1 | 15 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1998 | 1 | 16 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1998 | 1 | 17 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
1998 | 1 | 18 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1998 | 1 | 19 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1998 | 1 | 20 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
1998 | 1 | 21 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1998 | 1 | 22 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1998 | 1 | 23 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1998 | 1 | 24 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1998 | 1 | 25 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1998 | 1 | 26 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1998 | 1 | 27 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1998 | 1 | 28 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
1998 | 1 | 29 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1998 | 1 | 30 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1998 | 1 | 31 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1998 | 2 | 1 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1998 | 2 | 2 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1998 | 2 | 3 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1998 | 2 | 4 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1998 | 2 | 5 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1998 | 2 | 6 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1998 | 2 | 7 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1998 | 2 | 8 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1998 | 2 | 9 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1998 | 2 | 10 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1998 | 2 | 11 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1998 | 2 | 12 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1998 | 2 | 13 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
1998 | 2 | 14 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1998 | 2 | 15 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1998 | 2 | 16 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1998 | 2 | 17 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1998 | 2 | 18 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
1998 | 2 | 19 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1998 | 2 | 20 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1998 | 2 | 21 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1998 | 2 | 22 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1998 | 2 | 23 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1998 | 2 | 24 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
1998 | 2 | 25 | 380.0816 | 5 | 375.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
1998 | 2 | 26 | 474.1224 | 5 | 469.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
1998 | 2 | 27 | 393.1429 | 5 | 388.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
1998 | 2 | 28 | 390.5306 | 5 | 385.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1998 | 3 | 1 | 431.0204 | 25 | 406.0204 | 29.138 | 139.3858 | 0.77441 | 28.3635 | 89.27% | 298.8879 | 280.9547 | 6742.9118
1998 | 3 | 2 | 462.3673 | 25 | 437.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
1998 | 3 | 3 | 481.9592 | 25 | 456.9592 | 29.0361 | 139.3858 | 0.77441 | 28.2617 | 89.27% | 297.8144 | 279.9455 | 6718.6923
1998 | 3 | 4 | 496.3265 | 25 | 471.3265 | 29.0073 | 139.3858 | 0.77441 | 28.2329 | 89.27% | 297.5116 | 279.6609 | 6711.8611
1998 | 3 | 5 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
1998 | 3 | 6 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
1998 | 3 | 7 | 325.2245 | 25 | 300.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
1998 | 3 | 8 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
1998 | 3 | 9 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
1998 | 3 | 10 | 2011.4286 | 25 | 1986.4286 | 25.9771 | 139.3858 | 0.77441 | 25.2027 | 89.27% | 265.58 | 249.6452 | 5991.4859
1998 | 3 | 11 | 1475.9184 | 25 | 1450.9184 | 27.0482 | 139.3858 | 0.77441 | 26.2738 | 89.27% | 276.8662 | 260.2542 | 6246.1013
1998 | 3 | 12 | 779.7551 | 25 | 754.7551 | 28.4405 | 139.3858 | 0.77441 | 27.6661 | 89.27% | 291.5382 | 274.0459 | 6577.1013
1998 | 3 | 13 | 509.3878 | 25 | 484.3878 | 28.9812 | 139.3858 | 0.77441 | 28.2068 | 89.27% | 297.2363 | 279.4021 | 6705.651
1998 | 3 | 14 | 356.5714 | 25 | 331.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1998 | 3 | 15 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
1998 | 3 | 16 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
1998 | 3 | 17 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1998 | 3 | 18 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1998 | 3 | 19 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
1998 | 3 | 20 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1998 | 3 | 21 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1998 | 3 | 22 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
1998 | 3 | 23 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1998 | 3 | 24 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1998 | 3 | 25 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1998 | 3 | 26 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
1998 | 3 | 27 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1998 | 3 | 28 | 824.1633 | 25 | 799.1633 | 28.3517 | 139.3858 | 0.77441 | 27.5773 | 89.27% | 290.6023 | 273.1661 | 6555.9868
1998 | 3 | 29 | 1410.6122 | 25 | 1385.6122 | 27.1788 | 139.3858 | 0.77441 | 26.4044 | 89.27% | 278.2426 | 261.548 | 6277.1519
1998 | 3 | 30 | 1684.898 | 25 | 1659.898 | 26.6302 | 139.3858 | 0.77441 | 25.8558 | 89.27% | 272.4618 | 256.1141 | 6146.7392
1998 | 3 | 31 | 1841.6327 | 25 | 1816.6327 | 26.3167 | 139.3858 | 0.77441 | 25.5423 | 89.27% | 269.1586 | 253.0091 | 6072.2176
1998 | 4 | 1 | 1684.898 | 25 | 1659.898 | 26.6302 | 139.3858 | 0.77441 | 25.8558 | 89.27% | 272.4618 | 256.1141 | 6146.7392
1998 | 4 | 2 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
1998 | 4 | 3 | 962.6122 | 25 | 937.6122 | 28.0748 | 139.3858 | 0.77441 | 27.3004 | 89.27% | 287.6844 | 270.4233 | 6490.1594
1998 | 4 | 4 | 668.7347 | 25 | 643.7347 | 28.6625 | 139.3858 | 0.77441 | 27.8881 | 89.27% | 293.878 | 276.2453 | 6629.8874
1998 | 4 | 5 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
1998 | 4 | 6 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
1998 | 4 | 7 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
1998 | 4 | 8 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
1998 | 4 | 9 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
1998 | 4 | 10 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
1998 | 4 | 11 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1998 | 4 | 12 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1998 | 4 | 13 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1998 | 4 | 14 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1998 | 4 | 15 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1998 | 4 | 16 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
1998 | 4 | 17 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
1998 | 4 | 18 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
1998 | 4 | 19 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
1998 | 4 | 20 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
1998 | 4 | 21 | 370.9388 | 25 | 345.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1998 | 4 | 22 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1998 | 4 | 23 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
1998 | 4 | 24 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1998 | 4 | 25 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1998 | 4 | 26 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
1998 | 4 | 27 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1998 | 4 | 28 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
1998 | 4 | 29 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
1998 | 4 | 30 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1998 | 5 | 1 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1998 | 5 | 2 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1998 | 5 | 3 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
1998 | 5 | 4 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1998 | 5 | 5 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1998 | 5 | 6 | 574.6939 | 25 | 549.6939 | 28.8506 | 139.3858 | 0.77441 | 28.0762 | 89.27% | 295.8599 | 278.1083 | 6674.6004
1998 | 5 | 7 | 1295.6735 | 25 | 1270.6735 | 27.4087 | 139.3858 | 0.77441 | 26.6342 | 89.27% | 280.6649 | 263.825 | 6331.8011
1998 | 5 | 8 | 790.2041 | 25 | 765.2041 | 28.4196 | 139.3858 | 0.77441 | 27.6452 | 89.27% | 291.318 | 273.8389 | 6572.1332
1998 | 5 | 9 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
1998 | 5 | 10 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
1998 | 5 | 11 | 398.3673 | 25 | 373.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
1998 | 5 | 12 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
1998 | 5 | 13 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1998 | 5 | 14 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1998 | 5 | 15 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
1998 | 5 | 16 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1998 | 5 | 17 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1998 | 5 | 18 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
1998 | 5 | 19 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
1998 | 5 | 20 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
1998 | 5 | 21 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1998 | 5 | 22 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1998 | 5 | 23 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1998 | 5 | 24 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1998 | 5 | 25 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1998 | 5 | 26 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1998 | 5 | 27 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1998 | 5 | 28 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1998 | 5 | 29 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1998 | 5 | 30 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
1998 | 5 | 31 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1998 | 6 | 1 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
1998 | 6 | 2 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1998 | 6 | 3 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
1998 | 6 | 4 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1998 | 6 | 5 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
1998 | 6 | 6 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
1998 | 6 | 7 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1998 | 6 | 8 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1998 | 6 | 9 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1998 | 6 | 10 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
1998 | 6 | 11 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
1998 | 6 | 12 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1998 | 6 | 13 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
1998 | 6 | 14 | 3226.1224 | 25 | 3201.1224 | 23.5478 | 0 | 0 | 23.5478 | 0% | 0 | 0 | 0
1998 | 6 | 15 | 2690.6122 | 25 | 2665.6122 | 24.6188 | 0 | 0 | 24.6188 | 0% | 0 | 0 | 0
1998 | 6 | 16 | 1580.4082 | 25 | 1555.4082 | 26.8392 | 139.3858 | 0.77441 | 26.0648 | 89.27% | 274.664 | 258.1842 | 6196.4202
1998 | 6 | 17 | 1893.8776 | 25 | 1868.8776 | 26.2122 | 139.3858 | 0.77441 | 25.4378 | 89.27% | 268.0575 | 251.974 | 6047.3771
1998 | 6 | 18 | 1027.9184 | 25 | 1002.9184 | 27.9442 | 139.3858 | 0.77441 | 27.1698 | 89.27% | 286.308 | 269.1295 | 6459.1088
1998 | 6 | 19 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
1998 | 6 | 20 | 747.102 | 25 | 722.102 | 28.5058 | 139.3858 | 0.77441 | 27.7314 | 89.27% | 292.2264 | 274.6928 | 6592.6266
1998 | 6 | 21 | 730.1224 | 25 | 705.1224 | 28.5398 | 139.3858 | 0.77441 | 27.7653 | 89.27% | 292.5842 | 275.0292 | 6600.6998
1998 | 6 | 22 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
1998 | 6 | 23 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
1998 | 6 | 24 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
1998 | 6 | 25 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
1998 | 6 | 26 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1998 | 6 | 27 | 920.8163 | 25 | 895.8163 | 28.1584 | 139.3858 | 0.77441 | 27.384 | 89.27% | 288.5652 | 271.2513 | 6510.0319
1998 | 6 | 28 | 1098.449 | 25 | 1073.449 | 27.8031 | 139.3858 | 0.77441 | 27.0287 | 89.27% | 284.8215 | 267.7323 | 6425.5741
1998 | 6 | 29 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
1998 | 6 | 30 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
1998 | 7 | 1 | 400.9796 | 5 | 395.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
1998 | 7 | 2 | 545.9592 | 5 | 540.9592 | 28.9081 | 139.3858 | 0.77441 | 28.1337 | 89.27% | 296.4655 | 278.6776 | 6688.2626
1998 | 7 | 3 | 336.9796 | 5 | 331.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1998 | 7 | 4 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
1998 | 7 | 5 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1998 | 7 | 6 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
1998 | 7 | 7 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1998 | 7 | 8 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
1998 | 7 | 9 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
1998 | 7 | 10 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1998 | 7 | 11 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
1998 | 7 | 12 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
1998 | 7 | 13 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
1998 | 7 | 14 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
1998 | 7 | 15 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1998 | 7 | 16 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1998 | 7 | 17 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1998 | 7 | 18 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1998 | 7 | 19 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1998 | 7 | 20 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1998 | 7 | 21 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1998 | 7 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1998 | 7 | 23 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1998 | 7 | 24 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1998 | 7 | 25 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1998 | 7 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1998 | 7 | 27 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1998 | 7 | 28 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1998 | 7 | 29 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1998 | 7 | 30 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1998 | 7 | 31 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
1998 | 8 | 1 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1998 | 8 | 2 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
1998 | 8 | 3 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1998 | 8 | 4 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1998 | 8 | 5 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1998 | 8 | 6 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1998 | 8 | 7 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1998 | 8 | 8 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1998 | 8 | 9 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1998 | 8 | 10 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1998 | 8 | 11 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1998 | 8 | 12 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
1998 | 8 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
1998 | 8 | 14 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1998 | 8 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1998 | 8 | 16 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1998 | 8 | 17 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1998 | 8 | 18 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
1998 | 8 | 19 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1998 | 8 | 20 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1998 | 8 | 21 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1998 | 8 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1998 | 8 | 23 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1998 | 8 | 24 | 12.8 | 5 | 7.8 | 29.9744 | 7.8 | 0.0024251 | 29.972 | 40.05% | 7.9293 | 7.4536 | 178.8855
1998 | 8 | 25 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1998 | 8 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1998 | 8 | 27 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1998 | 8 | 28 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1998 | 8 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1998 | 8 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
1998 | 8 | 31 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
1998 | 9 | 1 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
1998 | 9 | 2 | 10.3184 | 15 | 0 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1998 | 9 | 3 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
1998 | 9 | 4 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
1998 | 9 | 5 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
1998 | 9 | 6 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1998 | 9 | 7 | 8.098 | 15 | 0 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
1998 | 9 | 8 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
1998 | 9 | 9 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1998 | 9 | 10 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1998 | 9 | 11 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1998 | 9 | 12 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
1998 | 9 | 13 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1998 | 9 | 14 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1998 | 9 | 15 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
1998 | 9 | 16 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1998 | 9 | 17 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
1998 | 9 | 18 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
1998 | 9 | 19 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
1998 | 9 | 20 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1998 | 9 | 21 | 5.6163 | 15 | 0 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1998 | 9 | 22 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
1998 | 9 | 23 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1998 | 9 | 24 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
1998 | 9 | 25 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
1998 | 9 | 26 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
1998 | 9 | 27 | 9.4041 | 15 | 0 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
1998 | 9 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1998 | 9 | 29 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1998 | 9 | 30 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1998 | 10 | 1 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
1998 | 10 | 2 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
1998 | 10 | 3 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
1998 | 10 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
1998 | 10 | 5 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
1998 | 10 | 6 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1998 | 10 | 7 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1998 | 10 | 8 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
1998 | 10 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1998 | 10 | 10 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1998 | 10 | 11 | 1003.102 | 15 | 988.102 | 27.9938 | 139.3858 | 0.77441 | 27.2194 | 89.27% | 286.831 | 269.6212 | 6470.908
1998 | 10 | 12 | 606.0408 | 15 | 591.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
1998 | 10 | 13 | 288.6531 | 15 | 273.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
1998 | 10 | 14 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1998 | 10 | 15 | 407.5102 | 15 | 392.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
1998 | 10 | 16 | 340.898 | 15 | 325.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
1998 | 10 | 17 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1998 | 10 | 18 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1998 | 10 | 19 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
1998 | 10 | 20 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
1998 | 10 | 21 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1998 | 10 | 22 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1998 | 10 | 23 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1998 | 10 | 24 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1998 | 10 | 25 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1998 | 10 | 26 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1998 | 10 | 27 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1998 | 10 | 28 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
1998 | 10 | 29 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
1998 | 10 | 30 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1998 | 10 | 31 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1998 | 11 | 1 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1998 | 11 | 2 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1998 | 11 | 3 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
1998 | 11 | 4 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
1998 | 11 | 5 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
1998 | 11 | 6 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
1998 | 11 | 7 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1998 | 11 | 8 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
1998 | 11 | 9 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1998 | 11 | 10 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
1998 | 11 | 11 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1998 | 11 | 12 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1998 | 11 | 13 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1998 | 11 | 14 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1998 | 11 | 15 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1998 | 11 | 16 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
1998 | 11 | 17 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1998 | 11 | 18 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
1998 | 11 | 19 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
1998 | 11 | 20 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1998 | 11 | 21 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
1998 | 11 | 22 | 126.6939 | 15 | 111.6939 | 29.7466 | 111.6939 | 0.49727 | 29.2493 | 91.77% | 253.9042 | 238.6699 | 5728.0783
1998 | 11 | 23 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1998 | 11 | 24 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1998 | 11 | 25 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
1998 | 11 | 26 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1998 | 11 | 27 | 528.9796 | 15 | 513.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
1998 | 11 | 28 | 356.5714 | 15 | 341.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1998 | 11 | 29 | 236.4082 | 15 | 221.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
1998 | 11 | 30 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1998 | 12 | 1 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1998 | 12 | 2 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
1998 | 12 | 3 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
1998 | 12 | 4 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1998 | 12 | 5 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1998 | 12 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1998 | 12 | 7 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
1998 | 12 | 8 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
1998 | 12 | 9 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
1998 | 12 | 10 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1998 | 12 | 11 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1998 | 12 | 12 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1998 | 12 | 13 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
1998 | 12 | 14 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1998 | 12 | 15 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1998 | 12 | 16 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1998 | 12 | 17 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1998 | 12 | 18 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
1998 | 12 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1998 | 12 | 20 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1998 | 12 | 21 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1998 | 12 | 22 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
1998 | 12 | 23 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1998 | 12 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
1998 | 12 | 25 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
1998 | 12 | 26 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
1998 | 12 | 27 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1998 | 12 | 28 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1998 | 12 | 29 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
1998 | 12 | 30 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
1998 | 12 | 31 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1999 | 1 | 1 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
1999 | 1 | 2 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1999 | 1 | 3 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
1999 | 1 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1999 | 1 | 5 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
1999 | 1 | 6 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
1999 | 1 | 7 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1999 | 1 | 8 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1999 | 1 | 9 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
1999 | 1 | 10 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
1999 | 1 | 11 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
1999 | 1 | 12 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1999 | 1 | 13 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1999 | 1 | 14 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1999 | 1 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
1999 | 1 | 16 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1999 | 1 | 17 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
1999 | 1 | 18 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
1999 | 1 | 19 | 376.1633 | 5 | 371.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
1999 | 1 | 20 | 463.6735 | 5 | 458.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1999 | 1 | 21 | 306.9388 | 5 | 301.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
1999 | 1 | 22 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
1999 | 1 | 23 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
1999 | 1 | 24 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1999 | 1 | 25 | 493.7143 | 5 | 488.7143 | 29.0126 | 139.3858 | 0.77441 | 28.2382 | 89.27% | 297.5666 | 279.7126 | 6713.1032
1999 | 1 | 26 | 356.5714 | 5 | 351.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
1999 | 1 | 27 | 266.449 | 5 | 261.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
1999 | 1 | 28 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
1999 | 1 | 29 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
1999 | 1 | 30 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1999 | 1 | 31 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1999 | 2 | 1 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1999 | 2 | 2 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
1999 | 2 | 3 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1999 | 2 | 4 | 259.9184 | 5 | 254.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
1999 | 2 | 5 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
1999 | 2 | 6 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1999 | 2 | 7 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
1999 | 2 | 8 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
1999 | 2 | 9 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1999 | 2 | 10 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1999 | 2 | 11 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1999 | 2 | 12 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1999 | 2 | 13 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1999 | 2 | 14 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
1999 | 2 | 15 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
1999 | 2 | 16 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
1999 | 2 | 17 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
1999 | 2 | 18 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
1999 | 2 | 19 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
1999 | 2 | 20 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
1999 | 2 | 21 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1999 | 2 | 22 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1999 | 2 | 23 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
1999 | 2 | 24 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1999 | 2 | 25 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1999 | 2 | 26 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
1999 | 2 | 27 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
1999 | 2 | 28 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
1999 | 3 | 1 | 502.8571 | 25 | 477.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
1999 | 3 | 2 | 845.0612 | 25 | 820.0612 | 28.3099 | 139.3858 | 0.77441 | 27.5355 | 89.27% | 290.1618 | 272.7521 | 6546.0506
1999 | 3 | 3 | 471.5102 | 25 | 446.5102 | 29.057 | 139.3858 | 0.77441 | 28.2826 | 89.27% | 298.0346 | 280.1525 | 6723.6604
1999 | 3 | 4 | 1065.7959 | 25 | 1040.7959 | 27.8684 | 139.3858 | 0.77441 | 27.094 | 89.27% | 285.5097 | 268.3791 | 6441.0994
1999 | 3 | 5 | 1515.102 | 25 | 1490.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
1999 | 3 | 6 | 719.6735 | 25 | 694.6735 | 28.5607 | 139.3858 | 0.77441 | 27.7862 | 89.27% | 292.8044 | 275.2362 | 6605.6679
1999 | 3 | 7 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
1999 | 3 | 8 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
1999 | 3 | 9 | 282.1224 | 25 | 257.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
1999 | 3 | 10 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1999 | 3 | 11 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
1999 | 3 | 12 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1999 | 3 | 13 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
1999 | 3 | 14 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1999 | 3 | 15 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1999 | 3 | 16 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1999 | 3 | 17 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1999 | 3 | 18 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
1999 | 3 | 19 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
1999 | 3 | 20 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
1999 | 3 | 21 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
1999 | 3 | 22 | 694.8571 | 25 | 669.8571 | 28.6103 | 139.3858 | 0.77441 | 27.8359 | 89.27% | 293.3274 | 275.7278 | 6617.4671
1999 | 3 | 23 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
1999 | 3 | 24 | 818.9388 | 25 | 793.9388 | 28.3621 | 139.3858 | 0.77441 | 27.5877 | 89.27% | 290.7124 | 273.2696 | 6558.4709
1999 | 3 | 25 | 553.7959 | 25 | 528.7959 | 28.8924 | 139.3858 | 0.77441 | 28.118 | 89.27% | 296.3004 | 278.5224 | 6684.5366
1999 | 3 | 26 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
1999 | 3 | 27 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
1999 | 3 | 28 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
1999 | 3 | 29 | 1004.4082 | 25 | 979.4082 | 27.9912 | 139.3858 | 0.77441 | 27.2168 | 89.27% | 286.8035 | 269.5953 | 6470.287
1999 | 3 | 30 | 1249.9592 | 25 | 1224.9592 | 27.5001 | 139.3858 | 0.77441 | 26.7257 | 89.27% | 281.6284 | 264.7307 | 6353.5366
1999 | 3 | 31 | 1008.3265 | 25 | 983.3265 | 27.9833 | 139.3858 | 0.77441 | 27.2089 | 89.27% | 286.7209 | 269.5177 | 6468.424
1999 | 4 | 1 | 993.9592 | 25 | 968.9592 | 28.0121 | 139.3858 | 0.77441 | 27.2377 | 89.27% | 287.0237 | 269.8023 | 6475.2551
1999 | 4 | 2 | 929.9592 | 25 | 904.9592 | 28.1401 | 139.3858 | 0.77441 | 27.3657 | 89.27% | 288.3726 | 271.0702 | 6505.6848
1999 | 4 | 3 | 762.7755 | 25 | 737.7755 | 28.4744 | 139.3858 | 0.77441 | 27.7 | 89.27% | 291.896 | 274.3823 | 6585.1745
1999 | 4 | 4 | 617.7959 | 25 | 592.7959 | 28.7644 | 139.3858 | 0.77441 | 27.99 | 89.27% | 294.9515 | 277.2545 | 6654.1069
1999 | 4 | 5 | 510.6939 | 25 | 485.6939 | 28.9786 | 139.3858 | 0.77441 | 28.2042 | 89.27% | 297.2088 | 279.3763 | 6705.03
1999 | 4 | 6 | 461.0612 | 25 | 436.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
1999 | 4 | 7 | 453.2245 | 25 | 428.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
1999 | 4 | 8 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
1999 | 4 | 9 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
1999 | 4 | 10 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
1999 | 4 | 11 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
1999 | 4 | 12 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1999 | 4 | 13 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
1999 | 4 | 14 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
1999 | 4 | 15 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
1999 | 4 | 16 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1999 | 4 | 17 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1999 | 4 | 18 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
1999 | 4 | 19 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
1999 | 4 | 20 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1999 | 4 | 21 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
1999 | 4 | 22 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1999 | 4 | 23 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
1999 | 4 | 24 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
1999 | 4 | 25 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
1999 | 4 | 26 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
1999 | 4 | 27 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1999 | 4 | 28 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
1999 | 4 | 29 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
1999 | 4 | 30 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
1999 | 5 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1999 | 5 | 2 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
1999 | 5 | 3 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
1999 | 5 | 4 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1999 | 5 | 5 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1999 | 5 | 6 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
1999 | 5 | 7 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1999 | 5 | 8 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
1999 | 5 | 9 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
1999 | 5 | 10 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
1999 | 5 | 11 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
1999 | 5 | 12 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
1999 | 5 | 13 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1999 | 5 | 14 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
1999 | 5 | 15 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
1999 | 5 | 16 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
1999 | 5 | 17 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
1999 | 5 | 18 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
1999 | 5 | 19 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
1999 | 5 | 20 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1999 | 5 | 21 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
1999 | 5 | 22 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
1999 | 5 | 23 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
1999 | 5 | 24 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
1999 | 5 | 25 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
1999 | 5 | 26 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
1999 | 5 | 27 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
1999 | 5 | 28 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
1999 | 5 | 29 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
1999 | 5 | 30 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
1999 | 5 | 31 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
1999 | 6 | 1 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
1999 | 6 | 2 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
1999 | 6 | 3 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
1999 | 6 | 4 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1999 | 6 | 5 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
1999 | 6 | 6 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1999 | 6 | 7 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
1999 | 6 | 8 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
1999 | 6 | 9 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
1999 | 6 | 10 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
1999 | 6 | 11 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
1999 | 6 | 12 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
1999 | 6 | 13 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
1999 | 6 | 14 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1999 | 6 | 15 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
1999 | 6 | 16 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
1999 | 6 | 17 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1999 | 6 | 18 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1999 | 6 | 19 | 22.2041 | 25 | 0 | 29.9556 | 0 | 0 | 29.9556 | 0% | 0 | 0 | 0
1999 | 6 | 20 | 19.5918 | 25 | 0 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
1999 | 6 | 21 | 16.9796 | 25 | 0 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
1999 | 6 | 22 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
1999 | 6 | 23 | 14.3673 | 25 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
1999 | 6 | 24 | 12.8 | 25 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
1999 | 6 | 25 | 12.2776 | 25 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
1999 | 6 | 26 | 12.4082 | 25 | 0 | 29.9752 | 0 | 0 | 29.9752 | 0% | 0 | 0 | 0
1999 | 6 | 27 | 10.8408 | 25 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
1999 | 6 | 28 | 9.6653 | 25 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
1999 | 6 | 29 | 10.3184 | 25 | 0 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1999 | 6 | 30 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
1999 | 7 | 1 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1999 | 7 | 2 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1999 | 7 | 3 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1999 | 7 | 4 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
1999 | 7 | 5 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
1999 | 7 | 6 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1999 | 7 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
1999 | 7 | 8 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1999 | 7 | 9 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1999 | 7 | 10 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1999 | 7 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
1999 | 7 | 12 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1999 | 7 | 13 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1999 | 7 | 14 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
1999 | 7 | 15 | 9.7959 | 5 | 4.7959 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
1999 | 7 | 16 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
1999 | 7 | 17 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1999 | 7 | 18 | 6.1388 | 5 | 1.1388 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1999 | 7 | 19 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1999 | 7 | 20 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
1999 | 7 | 21 | 5.6163 | 5 | 0.61633 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
1999 | 7 | 22 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1999 | 7 | 23 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1999 | 7 | 24 | 4.049 | 5 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
1999 | 7 | 25 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
1999 | 7 | 26 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1999 | 7 | 27 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
1999 | 7 | 28 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
1999 | 7 | 29 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1999 | 7 | 30 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
1999 | 7 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
1999 | 8 | 1 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
1999 | 8 | 2 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
1999 | 8 | 3 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
1999 | 8 | 4 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
1999 | 8 | 5 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
1999 | 8 | 6 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
1999 | 8 | 7 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
1999 | 8 | 8 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
1999 | 8 | 9 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1999 | 8 | 10 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1999 | 8 | 11 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
1999 | 8 | 12 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
1999 | 8 | 13 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
1999 | 8 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
1999 | 8 | 15 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
1999 | 8 | 16 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1999 | 8 | 17 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
1999 | 8 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
1999 | 8 | 19 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
1999 | 8 | 20 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1999 | 8 | 21 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1999 | 8 | 22 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
1999 | 8 | 23 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
1999 | 8 | 24 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
1999 | 8 | 25 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
1999 | 8 | 26 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
1999 | 8 | 27 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
1999 | 8 | 28 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
1999 | 8 | 29 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
1999 | 8 | 30 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
1999 | 8 | 31 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
1999 | 9 | 1 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
1999 | 9 | 2 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
1999 | 9 | 3 | 4.9633 | 15 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
1999 | 9 | 4 | 4.4408 | 15 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
1999 | 9 | 5 | 3.9184 | 15 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
1999 | 9 | 6 | 3.6571 | 15 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
1999 | 9 | 7 | 4.049 | 15 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
1999 | 9 | 8 | 4.3102 | 15 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
1999 | 9 | 9 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
1999 | 9 | 10 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
1999 | 9 | 11 | 512 | 15 | 497 | 28.976 | 139.3858 | 0.77441 | 28.2016 | 89.27% | 297.1812 | 279.3504 | 6704.409
1999 | 9 | 12 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
1999 | 9 | 13 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1999 | 9 | 14 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1999 | 9 | 15 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
1999 | 9 | 16 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
1999 | 9 | 17 | 2364.0816 | 15 | 2349.0816 | 25.2718 | 139.3858 | 0.77441 | 24.4974 | 89.27% | 258.1477 | 242.6588 | 5823.8123
1999 | 9 | 18 | 1815.5102 | 15 | 1800.5102 | 26.369 | 139.3858 | 0.77441 | 25.5946 | 89.27% | 269.7091 | 253.5266 | 6084.6379
1999 | 9 | 19 | 696.1633 | 15 | 681.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
1999 | 9 | 20 | 370.9388 | 15 | 355.9388 | 29.2581 | 139.3858 | 0.77441 | 28.4837 | 89.27% | 300.1542 | 282.1449 | 6771.4784
1999 | 9 | 21 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
1999 | 9 | 22 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
1999 | 9 | 23 | 261.2245 | 15 | 246.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
1999 | 9 | 24 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
1999 | 9 | 25 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
1999 | 9 | 26 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
1999 | 9 | 27 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
1999 | 9 | 28 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1999 | 9 | 29 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
1999 | 9 | 30 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
1999 | 10 | 1 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
1999 | 10 | 2 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1999 | 10 | 3 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
1999 | 10 | 4 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
1999 | 10 | 5 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
1999 | 10 | 6 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
1999 | 10 | 7 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1999 | 10 | 8 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
1999 | 10 | 9 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1999 | 10 | 10 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
1999 | 10 | 11 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
1999 | 10 | 12 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
1999 | 10 | 13 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
1999 | 10 | 14 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
1999 | 10 | 15 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1999 | 10 | 16 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
1999 | 10 | 17 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
1999 | 10 | 18 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
1999 | 10 | 19 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
1999 | 10 | 20 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
1999 | 10 | 21 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1999 | 10 | 22 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1999 | 10 | 23 | 461.0612 | 15 | 446.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
1999 | 10 | 24 | 830.6939 | 15 | 815.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
1999 | 10 | 25 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1999 | 10 | 26 | 271.6735 | 15 | 256.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
1999 | 10 | 27 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
1999 | 10 | 28 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
1999 | 10 | 29 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
1999 | 10 | 30 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1999 | 10 | 31 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1999 | 11 | 1 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
1999 | 11 | 2 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
1999 | 11 | 3 | 466.2857 | 15 | 451.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
1999 | 11 | 4 | 514.6122 | 15 | 499.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
1999 | 11 | 5 | 295.1837 | 15 | 280.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
1999 | 11 | 6 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
1999 | 11 | 7 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
1999 | 11 | 8 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
1999 | 11 | 9 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
1999 | 11 | 10 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1999 | 11 | 11 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
1999 | 11 | 12 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
1999 | 11 | 13 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
1999 | 11 | 14 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
1999 | 11 | 15 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
1999 | 11 | 16 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
1999 | 11 | 17 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1999 | 11 | 18 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
1999 | 11 | 19 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
1999 | 11 | 20 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
1999 | 11 | 21 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
1999 | 11 | 22 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
1999 | 11 | 23 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
1999 | 11 | 24 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
1999 | 11 | 25 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
1999 | 11 | 26 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
1999 | 11 | 27 | 326.5306 | 15 | 311.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
1999 | 11 | 28 | 403.5918 | 15 | 388.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
1999 | 11 | 29 | 263.8367 | 15 | 248.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
1999 | 11 | 30 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
1999 | 12 | 1 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
1999 | 12 | 2 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
1999 | 12 | 3 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1999 | 12 | 4 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1999 | 12 | 5 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
1999 | 12 | 6 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
1999 | 12 | 7 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
1999 | 12 | 8 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1999 | 12 | 9 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
1999 | 12 | 10 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1999 | 12 | 11 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
1999 | 12 | 12 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
1999 | 12 | 13 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
1999 | 12 | 14 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
1999 | 12 | 15 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
1999 | 12 | 16 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
1999 | 12 | 17 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
1999 | 12 | 18 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
1999 | 12 | 19 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1999 | 12 | 20 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
1999 | 12 | 21 | 225.9592 | 5 | 220.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
1999 | 12 | 22 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
1999 | 12 | 23 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
1999 | 12 | 24 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
1999 | 12 | 25 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
1999 | 12 | 26 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
1999 | 12 | 27 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
1999 | 12 | 28 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
1999 | 12 | 29 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
1999 | 12 | 30 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
1999 | 12 | 31 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2000 | 1 | 1 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2000 | 1 | 2 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2000 | 1 | 3 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2000 | 1 | 4 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2000 | 1 | 5 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2000 | 1 | 6 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2000 | 1 | 7 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2000 | 1 | 8 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2000 | 1 | 9 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2000 | 1 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2000 | 1 | 11 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2000 | 1 | 12 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2000 | 1 | 13 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2000 | 1 | 14 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2000 | 1 | 15 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2000 | 1 | 16 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2000 | 1 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2000 | 1 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2000 | 1 | 19 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2000 | 1 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2000 | 1 | 21 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2000 | 1 | 22 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 1 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2000 | 1 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2000 | 1 | 25 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2000 | 1 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 1 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2000 | 1 | 28 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2000 | 1 | 29 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 1 | 30 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 1 | 31 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2000 | 2 | 1 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2000 | 2 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2000 | 2 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2000 | 2 | 4 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2000 | 2 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2000 | 2 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 2 | 7 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 2 | 8 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2000 | 2 | 9 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2000 | 2 | 10 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2000 | 2 | 11 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2000 | 2 | 12 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 2 | 13 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2000 | 2 | 14 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 2 | 15 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2000 | 2 | 16 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2000 | 2 | 17 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2000 | 2 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 2 | 19 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2000 | 2 | 20 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2000 | 2 | 21 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 2 | 22 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 2 | 23 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 2 | 24 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2000 | 2 | 25 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2000 | 2 | 26 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2000 | 2 | 27 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2000 | 2 | 28 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2000 | 2 | 29 | 342.2041 | 5 | 337.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
2000 | 3 | 1 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
2000 | 3 | 2 | 246.8571 | 25 | 221.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2000 | 3 | 3 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2000 | 3 | 4 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2000 | 3 | 5 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2000 | 3 | 6 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
2000 | 3 | 7 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2000 | 3 | 8 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2000 | 3 | 9 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2000 | 3 | 10 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
2000 | 3 | 11 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2000 | 3 | 12 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2000 | 3 | 13 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2000 | 3 | 14 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2000 | 3 | 15 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2000 | 3 | 16 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2000 | 3 | 17 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
2000 | 3 | 18 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2000 | 3 | 19 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2000 | 3 | 20 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2000 | 3 | 21 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2000 | 3 | 22 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2000 | 3 | 23 | 288.6531 | 25 | 263.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
2000 | 3 | 24 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
2000 | 3 | 25 | 480.6531 | 25 | 455.6531 | 29.0387 | 139.3858 | 0.77441 | 28.2643 | 89.27% | 297.8419 | 279.9714 | 6719.3133
2000 | 3 | 26 | 513.3061 | 25 | 488.3061 | 28.9734 | 139.3858 | 0.77441 | 28.199 | 89.27% | 297.1537 | 279.3245 | 6703.788
2000 | 3 | 27 | 613.8776 | 25 | 588.8776 | 28.7722 | 139.3858 | 0.77441 | 27.9978 | 89.27% | 295.0341 | 277.3321 | 6655.97
2000 | 3 | 28 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
2000 | 3 | 29 | 2220.4082 | 25 | 2195.4082 | 25.5592 | 139.3858 | 0.77441 | 24.7848 | 89.27% | 261.1757 | 245.5052 | 5892.1238
2000 | 3 | 30 | 1099.7551 | 25 | 1074.7551 | 27.8005 | 139.3858 | 0.77441 | 27.0261 | 89.27% | 284.794 | 267.7064 | 6424.9531
2000 | 3 | 31 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
2000 | 4 | 1 | 527.6735 | 25 | 502.6735 | 28.9447 | 139.3858 | 0.77441 | 28.1702 | 89.27% | 296.8509 | 279.0399 | 6696.9568
2000 | 4 | 2 | 489.7959 | 25 | 464.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
2000 | 4 | 3 | 756.2449 | 25 | 731.2449 | 28.4875 | 139.3858 | 0.77441 | 27.7131 | 89.27% | 292.0337 | 274.5116 | 6588.2795
2000 | 4 | 4 | 1332.2449 | 25 | 1307.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
2000 | 4 | 5 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
2000 | 4 | 6 | 770.6122 | 25 | 745.6122 | 28.4588 | 139.3858 | 0.77441 | 27.6844 | 89.27% | 291.7309 | 274.227 | 6581.4484
2000 | 4 | 7 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
2000 | 4 | 8 | 445.3878 | 25 | 420.3878 | 29.1092 | 139.3858 | 0.77441 | 28.3348 | 89.27% | 298.5851 | 280.67 | 6736.0807
2000 | 4 | 9 | 957.3878 | 25 | 932.3878 | 28.0852 | 139.3858 | 0.77441 | 27.3108 | 89.27% | 287.7945 | 270.5268 | 6492.6435
2000 | 4 | 10 | 1306.1224 | 25 | 1281.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
2000 | 4 | 11 | 683.102 | 25 | 658.102 | 28.6338 | 139.3858 | 0.77441 | 27.8594 | 89.27% | 293.5752 | 275.9607 | 6623.0563
2000 | 4 | 12 | 508.0816 | 25 | 483.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
2000 | 4 | 13 | 441.4694 | 25 | 416.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
2000 | 4 | 14 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
2000 | 4 | 15 | 305.6327 | 25 | 280.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
2000 | 4 | 16 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2000 | 4 | 17 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2000 | 4 | 18 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2000 | 4 | 19 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2000 | 4 | 20 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2000 | 4 | 21 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2000 | 4 | 22 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2000 | 4 | 23 | 816.3265 | 25 | 791.3265 | 28.3673 | 139.3858 | 0.77441 | 27.5929 | 89.27% | 290.7674 | 273.3214 | 6559.7129
2000 | 4 | 24 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
2000 | 4 | 25 | 830.6939 | 25 | 805.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
2000 | 4 | 26 | 489.7959 | 25 | 464.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
2000 | 4 | 27 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
2000 | 4 | 28 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2000 | 4 | 29 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
2000 | 4 | 30 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2000 | 5 | 1 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2000 | 5 | 2 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2000 | 5 | 3 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2000 | 5 | 4 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
2000 | 5 | 5 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2000 | 5 | 6 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
2000 | 5 | 7 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2000 | 5 | 8 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2000 | 5 | 9 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2000 | 5 | 10 | 976.9796 | 25 | 951.9796 | 28.046 | 139.3858 | 0.77441 | 27.2716 | 89.27% | 287.3816 | 270.1387 | 6483.3283
2000 | 5 | 11 | 834.6122 | 25 | 809.6122 | 28.3308 | 139.3858 | 0.77441 | 27.5564 | 89.27% | 290.382 | 272.9591 | 6551.0187
2000 | 5 | 12 | 677.8776 | 25 | 652.8776 | 28.6442 | 139.3858 | 0.77441 | 27.8698 | 89.27% | 293.6853 | 276.0642 | 6625.5403
2000 | 5 | 13 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
2000 | 5 | 14 | 410.1224 | 25 | 385.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
2000 | 5 | 15 | 334.3673 | 25 | 309.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
2000 | 5 | 16 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
2000 | 5 | 17 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2000 | 5 | 18 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2000 | 5 | 19 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2000 | 5 | 20 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2000 | 5 | 21 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2000 | 5 | 22 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2000 | 5 | 23 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
2000 | 5 | 24 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
2000 | 5 | 25 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
2000 | 5 | 26 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
2000 | 5 | 27 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2000 | 5 | 28 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2000 | 5 | 29 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2000 | 5 | 30 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
2000 | 5 | 31 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2000 | 6 | 1 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2000 | 6 | 2 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2000 | 6 | 3 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2000 | 6 | 4 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2000 | 6 | 5 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2000 | 6 | 6 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2000 | 6 | 7 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2000 | 6 | 8 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2000 | 6 | 9 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
2000 | 6 | 10 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2000 | 6 | 11 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
2000 | 6 | 12 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2000 | 6 | 13 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2000 | 6 | 14 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2000 | 6 | 15 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2000 | 6 | 16 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2000 | 6 | 17 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2000 | 6 | 18 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2000 | 6 | 19 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2000 | 6 | 20 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
2000 | 6 | 21 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
2000 | 6 | 22 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2000 | 6 | 23 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2000 | 6 | 24 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2000 | 6 | 25 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
2000 | 6 | 26 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2000 | 6 | 27 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
2000 | 6 | 28 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2000 | 6 | 29 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2000 | 6 | 30 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2000 | 7 | 1 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2000 | 7 | 2 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2000 | 7 | 3 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2000 | 7 | 4 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2000 | 7 | 5 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2000 | 7 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2000 | 7 | 7 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2000 | 7 | 8 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2000 | 7 | 9 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2000 | 7 | 10 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2000 | 7 | 11 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2000 | 7 | 12 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2000 | 7 | 13 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
2000 | 7 | 14 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
2000 | 7 | 15 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2000 | 7 | 16 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2000 | 7 | 17 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2000 | 7 | 18 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2000 | 7 | 19 | 347.4286 | 5 | 342.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
2000 | 7 | 20 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2000 | 7 | 21 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2000 | 7 | 22 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2000 | 7 | 23 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2000 | 7 | 24 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2000 | 7 | 25 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2000 | 7 | 26 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2000 | 7 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 7 | 28 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2000 | 7 | 29 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2000 | 7 | 30 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2000 | 7 | 31 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2000 | 8 | 1 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2000 | 8 | 2 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2000 | 8 | 3 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 8 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2000 | 8 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2000 | 8 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2000 | 8 | 7 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2000 | 8 | 8 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2000 | 8 | 9 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2000 | 8 | 10 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2000 | 8 | 11 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2000 | 8 | 12 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2000 | 8 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2000 | 8 | 14 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2000 | 8 | 15 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2000 | 8 | 16 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2000 | 8 | 17 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2000 | 8 | 18 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2000 | 8 | 19 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2000 | 8 | 20 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2000 | 8 | 21 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2000 | 8 | 22 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2000 | 8 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2000 | 8 | 24 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2000 | 8 | 25 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2000 | 8 | 26 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2000 | 8 | 27 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2000 | 8 | 28 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2000 | 8 | 29 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2000 | 8 | 30 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2000 | 8 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2000 | 9 | 1 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2000 | 9 | 2 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2000 | 9 | 3 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2000 | 9 | 4 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2000 | 9 | 5 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2000 | 9 | 6 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2000 | 9 | 7 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2000 | 9 | 8 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
2000 | 9 | 9 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
2000 | 9 | 10 | 9.7959 | 15 | 0 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
2000 | 9 | 11 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2000 | 9 | 12 | 8.3592 | 15 | 0 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
2000 | 9 | 13 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2000 | 9 | 14 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
2000 | 9 | 15 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
2000 | 9 | 16 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2000 | 9 | 17 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2000 | 9 | 18 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2000 | 9 | 19 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2000 | 9 | 20 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2000 | 9 | 21 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2000 | 9 | 22 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
2000 | 9 | 23 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
2000 | 9 | 24 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
2000 | 9 | 25 | 9.1429 | 15 | 0 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
2000 | 9 | 26 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
2000 | 9 | 27 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
2000 | 9 | 28 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2000 | 9 | 29 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
2000 | 9 | 30 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
2000 | 10 | 1 | 5.8776 | 15 | 0 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
2000 | 10 | 2 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
2000 | 10 | 3 | 5.8776 | 15 | 0 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
2000 | 10 | 4 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
2000 | 10 | 5 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
2000 | 10 | 6 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2000 | 10 | 7 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2000 | 10 | 8 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2000 | 10 | 9 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2000 | 10 | 10 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2000 | 10 | 11 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2000 | 10 | 12 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2000 | 10 | 13 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2000 | 10 | 14 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2000 | 10 | 15 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2000 | 10 | 16 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2000 | 10 | 17 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2000 | 10 | 18 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2000 | 10 | 19 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
2000 | 10 | 20 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2000 | 10 | 21 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2000 | 10 | 22 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
2000 | 10 | 23 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
2000 | 10 | 24 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2000 | 10 | 25 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2000 | 10 | 26 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2000 | 10 | 27 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2000 | 10 | 28 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2000 | 10 | 29 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2000 | 10 | 30 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2000 | 10 | 31 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2000 | 11 | 1 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2000 | 11 | 2 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2000 | 11 | 3 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2000 | 11 | 4 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2000 | 11 | 5 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2000 | 11 | 6 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2000 | 11 | 7 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2000 | 11 | 8 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2000 | 11 | 9 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2000 | 11 | 10 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2000 | 11 | 11 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2000 | 11 | 12 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
2000 | 11 | 13 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2000 | 11 | 14 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
2000 | 11 | 15 | 346.1224 | 15 | 331.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2000 | 11 | 16 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2000 | 11 | 17 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2000 | 11 | 18 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
2000 | 11 | 19 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2000 | 11 | 20 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
2000 | 11 | 21 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2000 | 11 | 22 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2000 | 11 | 23 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2000 | 11 | 24 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2000 | 11 | 25 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2000 | 11 | 26 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2000 | 11 | 27 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
2000 | 11 | 28 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2000 | 11 | 29 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2000 | 11 | 30 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
2000 | 12 | 1 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2000 | 12 | 2 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2000 | 12 | 3 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2000 | 12 | 4 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2000 | 12 | 5 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2000 | 12 | 6 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2000 | 12 | 7 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2000 | 12 | 8 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2000 | 12 | 9 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2000 | 12 | 10 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2000 | 12 | 11 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2000 | 12 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2000 | 12 | 13 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2000 | 12 | 14 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2000 | 12 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2000 | 12 | 16 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2000 | 12 | 17 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2000 | 12 | 18 | 1828.5714 | 5 | 1823.5714 | 26.3429 | 139.3858 | 0.77441 | 25.5684 | 89.27% | 269.4339 | 253.2678 | 6078.4277
2000 | 12 | 19 | 910.3673 | 5 | 905.3673 | 28.1793 | 139.3858 | 0.77441 | 27.4049 | 89.27% | 288.7855 | 271.4583 | 6515
2000 | 12 | 20 | 441.4694 | 5 | 436.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
2000 | 12 | 21 | 329.1429 | 5 | 324.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
2000 | 12 | 22 | 246.8571 | 5 | 241.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2000 | 12 | 23 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2000 | 12 | 24 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2000 | 12 | 25 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
2000 | 12 | 26 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2000 | 12 | 27 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2000 | 12 | 28 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2000 | 12 | 29 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2000 | 12 | 30 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2000 | 12 | 31 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2001 | 1 | 1 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2001 | 1 | 2 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2001 | 1 | 3 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2001 | 1 | 4 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2001 | 1 | 5 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2001 | 1 | 6 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2001 | 1 | 7 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2001 | 1 | 8 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2001 | 1 | 9 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2001 | 1 | 10 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2001 | 1 | 11 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2001 | 1 | 12 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2001 | 1 | 13 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2001 | 1 | 14 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2001 | 1 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2001 | 1 | 16 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2001 | 1 | 17 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2001 | 1 | 18 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2001 | 1 | 19 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 1 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 1 | 21 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 1 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2001 | 1 | 23 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2001 | 1 | 24 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2001 | 1 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 1 | 26 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 1 | 27 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 1 | 28 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 1 | 29 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2001 | 1 | 30 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2001 | 1 | 31 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 2 | 1 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2001 | 2 | 2 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 2 | 3 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 2 | 4 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 2 | 5 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 2 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2001 | 2 | 7 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2001 | 2 | 8 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2001 | 2 | 9 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2001 | 2 | 10 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2001 | 2 | 11 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2001 | 2 | 12 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 2 | 13 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2001 | 2 | 14 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2001 | 2 | 15 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2001 | 2 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 2 | 17 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 2 | 18 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 2 | 19 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2001 | 2 | 20 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2001 | 2 | 21 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2001 | 2 | 22 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2001 | 2 | 23 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2001 | 2 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2001 | 2 | 25 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2001 | 2 | 26 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 2 | 27 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2001 | 2 | 28 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2001 | 3 | 1 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2001 | 3 | 2 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2001 | 3 | 3 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
2001 | 3 | 4 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2001 | 3 | 5 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
2001 | 3 | 6 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2001 | 3 | 7 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2001 | 3 | 8 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2001 | 3 | 9 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2001 | 3 | 10 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2001 | 3 | 11 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2001 | 3 | 12 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2001 | 3 | 13 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2001 | 3 | 14 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2001 | 3 | 15 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2001 | 3 | 16 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
2001 | 3 | 17 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2001 | 3 | 18 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2001 | 3 | 19 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2001 | 3 | 20 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2001 | 3 | 21 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2001 | 3 | 22 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2001 | 3 | 23 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2001 | 3 | 24 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2001 | 3 | 25 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2001 | 3 | 26 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2001 | 3 | 27 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2001 | 3 | 28 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2001 | 3 | 29 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2001 | 3 | 30 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2001 | 3 | 31 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2001 | 4 | 1 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2001 | 4 | 2 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2001 | 4 | 3 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2001 | 4 | 4 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2001 | 4 | 5 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2001 | 4 | 6 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
2001 | 4 | 7 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2001 | 4 | 8 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2001 | 4 | 9 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2001 | 4 | 10 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
2001 | 4 | 11 | 581.2245 | 25 | 556.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
2001 | 4 | 12 | 758.8571 | 25 | 733.8571 | 28.4823 | 139.3858 | 0.77441 | 27.7079 | 89.27% | 291.9786 | 274.4599 | 6587.0375
2001 | 4 | 13 | 1219.9184 | 25 | 1194.9184 | 27.5602 | 139.3858 | 0.77441 | 26.7858 | 89.27% | 282.2615 | 265.3258 | 6367.8199
2001 | 4 | 14 | 1243.4286 | 25 | 1218.4286 | 27.5131 | 139.3858 | 0.77441 | 26.7387 | 89.27% | 281.766 | 264.8601 | 6356.6416
2001 | 4 | 15 | 1103.6735 | 25 | 1078.6735 | 27.7927 | 139.3858 | 0.77441 | 27.0182 | 89.27% | 284.7114 | 267.6288 | 6423.09
2001 | 4 | 16 | 1048.8163 | 25 | 1023.8163 | 27.9024 | 139.3858 | 0.77441 | 27.128 | 89.27% | 285.8676 | 268.7155 | 6449.1726
2001 | 4 | 17 | 1061.8776 | 25 | 1036.8776 | 27.8762 | 139.3858 | 0.77441 | 27.1018 | 89.27% | 285.5923 | 268.4568 | 6442.9624
2001 | 4 | 18 | 999.1837 | 25 | 974.1837 | 28.0016 | 139.3858 | 0.77441 | 27.2272 | 89.27% | 286.9136 | 269.6988 | 6472.7711
2001 | 4 | 19 | 694.8571 | 25 | 669.8571 | 28.6103 | 139.3858 | 0.77441 | 27.8359 | 89.27% | 293.3274 | 275.7278 | 6617.4671
2001 | 4 | 20 | 696.1633 | 25 | 671.1633 | 28.6077 | 139.3858 | 0.77441 | 27.8333 | 89.27% | 293.2999 | 275.7019 | 6616.8461
2001 | 4 | 21 | 912.9796 | 25 | 887.9796 | 28.174 | 139.3858 | 0.77441 | 27.3996 | 89.27% | 288.7304 | 271.4066 | 6513.7579
2001 | 4 | 22 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
2001 | 4 | 23 | 2011.4286 | 25 | 1986.4286 | 25.9771 | 139.3858 | 0.77441 | 25.2027 | 89.27% | 265.58 | 249.6452 | 5991.4859
2001 | 4 | 24 | 1893.8776 | 25 | 1868.8776 | 26.2122 | 139.3858 | 0.77441 | 25.4378 | 89.27% | 268.0575 | 251.974 | 6047.3771
2001 | 4 | 25 | 1802.449 | 25 | 1777.449 | 26.3951 | 139.3858 | 0.77441 | 25.6207 | 89.27% | 269.9844 | 253.7853 | 6090.848
2001 | 4 | 26 | 1172.898 | 25 | 1147.898 | 27.6542 | 139.3858 | 0.77441 | 26.8798 | 89.27% | 283.2525 | 266.2573 | 6390.1763
2001 | 4 | 27 | 888.1633 | 25 | 863.1633 | 28.2237 | 139.3858 | 0.77441 | 27.4493 | 89.27% | 289.2534 | 271.8982 | 6525.5572
2001 | 4 | 28 | 740.5714 | 25 | 715.5714 | 28.5189 | 139.3858 | 0.77441 | 27.7444 | 89.27% | 292.364 | 274.8222 | 6595.7317
2001 | 4 | 29 | 562.9388 | 25 | 537.9388 | 28.8741 | 139.3858 | 0.77441 | 28.0997 | 89.27% | 296.1077 | 278.3412 | 6680.1895
2001 | 4 | 30 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
2001 | 5 | 1 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
2001 | 5 | 2 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
2001 | 5 | 3 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2001 | 5 | 4 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2001 | 5 | 5 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2001 | 5 | 6 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2001 | 5 | 7 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2001 | 5 | 8 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2001 | 5 | 9 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
2001 | 5 | 10 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2001 | 5 | 11 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2001 | 5 | 12 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2001 | 5 | 13 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2001 | 5 | 14 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2001 | 5 | 15 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2001 | 5 | 16 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2001 | 5 | 17 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2001 | 5 | 18 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2001 | 5 | 19 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2001 | 5 | 20 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2001 | 5 | 21 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2001 | 5 | 22 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2001 | 5 | 23 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2001 | 5 | 24 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2001 | 5 | 25 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2001 | 5 | 26 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2001 | 5 | 27 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2001 | 5 | 28 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2001 | 5 | 29 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
2001 | 5 | 30 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2001 | 5 | 31 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2001 | 6 | 1 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2001 | 6 | 2 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2001 | 6 | 3 | 1121.9592 | 25 | 1096.9592 | 27.7561 | 139.3858 | 0.77441 | 26.9817 | 89.27% | 284.3261 | 267.2665 | 6414.3958
2001 | 6 | 4 | 862.0408 | 25 | 837.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
2001 | 6 | 5 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
2001 | 6 | 6 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
2001 | 6 | 7 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2001 | 6 | 8 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2001 | 6 | 9 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
2001 | 6 | 10 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2001 | 6 | 11 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2001 | 6 | 12 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2001 | 6 | 13 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2001 | 6 | 14 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2001 | 6 | 15 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2001 | 6 | 16 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2001 | 6 | 17 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2001 | 6 | 18 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2001 | 6 | 19 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2001 | 6 | 20 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2001 | 6 | 21 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2001 | 6 | 22 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
2001 | 6 | 23 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
2001 | 6 | 24 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2001 | 6 | 25 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2001 | 6 | 26 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2001 | 6 | 27 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2001 | 6 | 28 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2001 | 6 | 29 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2001 | 6 | 30 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
2001 | 7 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 7 | 2 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2001 | 7 | 3 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2001 | 7 | 4 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 7 | 5 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2001 | 7 | 6 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2001 | 7 | 7 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2001 | 7 | 8 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2001 | 7 | 9 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2001 | 7 | 10 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2001 | 7 | 11 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2001 | 7 | 12 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2001 | 7 | 13 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
2001 | 7 | 14 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2001 | 7 | 15 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2001 | 7 | 16 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2001 | 7 | 17 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2001 | 7 | 18 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2001 | 7 | 19 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2001 | 7 | 20 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2001 | 7 | 21 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2001 | 7 | 22 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2001 | 7 | 23 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2001 | 7 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2001 | 7 | 25 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2001 | 7 | 26 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2001 | 7 | 27 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2001 | 7 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2001 | 7 | 29 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2001 | 7 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2001 | 7 | 31 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
2001 | 8 | 1 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
2001 | 8 | 2 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
2001 | 8 | 3 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
2001 | 8 | 4 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2001 | 8 | 5 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
2001 | 8 | 6 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
2001 | 8 | 7 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
2001 | 8 | 8 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
2001 | 8 | 9 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
2001 | 8 | 10 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
2001 | 8 | 11 | 4.049 | 5 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
2001 | 8 | 12 | 3.9184 | 5 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
2001 | 8 | 13 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
2001 | 8 | 14 | 3.6571 | 5 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
2001 | 8 | 15 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
2001 | 8 | 16 | 3.2653 | 5 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
2001 | 8 | 17 | 3.2653 | 5 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
2001 | 8 | 18 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
2001 | 8 | 19 | 3.3959 | 5 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
2001 | 8 | 20 | 3.1347 | 5 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
2001 | 8 | 21 | 3.2653 | 5 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
2001 | 8 | 22 | 4.5714 | 5 | 0 | 29.9909 | 0 | 0 | 29.9909 | 0% | 0 | 0 | 0
2001 | 8 | 23 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
2001 | 8 | 24 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
2001 | 8 | 25 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
2001 | 8 | 26 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
2001 | 8 | 27 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
2001 | 8 | 28 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
2001 | 8 | 29 | 4.3102 | 5 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
2001 | 8 | 30 | 4.3102 | 5 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
2001 | 8 | 31 | 4.049 | 5 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
2001 | 9 | 1 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
2001 | 9 | 2 | 11.6245 | 15 | 0 | 29.9768 | 0 | 0 | 29.9768 | 0% | 0 | 0 | 0
2001 | 9 | 3 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2001 | 9 | 4 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
2001 | 9 | 5 | 5.6163 | 15 | 0 | 29.9888 | 0 | 0 | 29.9888 | 0% | 0 | 0 | 0
2001 | 9 | 6 | 4.702 | 15 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
2001 | 9 | 7 | 4.1796 | 15 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
2001 | 9 | 8 | 3.6571 | 15 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
2001 | 9 | 9 | 3.2653 | 15 | 0 | 29.9935 | 0 | 0 | 29.9935 | 0% | 0 | 0 | 0
2001 | 9 | 10 | 2.8735 | 15 | 0 | 29.9943 | 0 | 0 | 29.9943 | 0% | 0 | 0 | 0
2001 | 9 | 11 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
2001 | 9 | 12 | 2.2204 | 15 | 0 | 29.9956 | 0 | 0 | 29.9956 | 0% | 0 | 0 | 0
2001 | 9 | 13 | 2.0898 | 15 | 0 | 29.9958 | 0 | 0 | 29.9958 | 0% | 0 | 0 | 0
2001 | 9 | 14 | 1.9592 | 15 | 0 | 29.9961 | 0 | 0 | 29.9961 | 0% | 0 | 0 | 0
2001 | 9 | 15 | 1.698 | 15 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
2001 | 9 | 16 | 1.698 | 15 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
2001 | 9 | 17 | 1.5673 | 15 | 0 | 29.9969 | 0 | 0 | 29.9969 | 0% | 0 | 0 | 0
2001 | 9 | 18 | 1.5673 | 15 | 0 | 29.9969 | 0 | 0 | 29.9969 | 0% | 0 | 0 | 0
2001 | 9 | 19 | 1.4367 | 15 | 0 | 29.9971 | 0 | 0 | 29.9971 | 0% | 0 | 0 | 0
2001 | 9 | 20 | 1.4367 | 15 | 0 | 29.9971 | 0 | 0 | 29.9971 | 0% | 0 | 0 | 0
2001 | 9 | 21 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
2001 | 9 | 22 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
2001 | 9 | 23 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
2001 | 9 | 24 | 5.2245 | 15 | 0 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
2001 | 9 | 25 | 5.3551 | 15 | 0 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
2001 | 9 | 26 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2001 | 9 | 27 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2001 | 9 | 28 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2001 | 9 | 29 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2001 | 9 | 30 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2001 | 10 | 1 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2001 | 10 | 2 | 11.3633 | 15 | 0 | 29.9773 | 0 | 0 | 29.9773 | 0% | 0 | 0 | 0
2001 | 10 | 3 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2001 | 10 | 4 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
2001 | 10 | 5 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
2001 | 10 | 6 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
2001 | 10 | 7 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2001 | 10 | 8 | 12.9306 | 15 | 0 | 29.9741 | 0 | 0 | 29.9741 | 0% | 0 | 0 | 0
2001 | 10 | 9 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
2001 | 10 | 10 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
2001 | 10 | 11 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
2001 | 10 | 12 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
2001 | 10 | 13 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
2001 | 10 | 14 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
2001 | 10 | 15 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
2001 | 10 | 16 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2001 | 10 | 17 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2001 | 10 | 18 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2001 | 10 | 19 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2001 | 10 | 20 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2001 | 10 | 21 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2001 | 10 | 22 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2001 | 10 | 23 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2001 | 10 | 24 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2001 | 10 | 25 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2001 | 10 | 26 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2001 | 10 | 27 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2001 | 10 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2001 | 10 | 29 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2001 | 10 | 30 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2001 | 10 | 31 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2001 | 11 | 1 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2001 | 11 | 2 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2001 | 11 | 3 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2001 | 11 | 4 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2001 | 11 | 5 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2001 | 11 | 6 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2001 | 11 | 7 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
2001 | 11 | 8 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2001 | 11 | 9 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2001 | 11 | 10 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2001 | 11 | 11 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2001 | 11 | 12 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2001 | 11 | 13 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2001 | 11 | 14 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2001 | 11 | 15 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2001 | 11 | 16 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2001 | 11 | 17 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2001 | 11 | 18 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2001 | 11 | 19 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2001 | 11 | 20 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2001 | 11 | 21 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2001 | 11 | 22 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2001 | 11 | 23 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2001 | 11 | 24 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2001 | 11 | 25 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2001 | 11 | 26 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2001 | 11 | 27 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2001 | 11 | 28 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2001 | 11 | 29 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2001 | 11 | 30 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2001 | 12 | 1 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2001 | 12 | 2 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2001 | 12 | 3 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2001 | 12 | 4 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2001 | 12 | 5 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2001 | 12 | 6 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2001 | 12 | 7 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2001 | 12 | 8 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2001 | 12 | 9 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 12 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2001 | 12 | 11 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2001 | 12 | 12 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2001 | 12 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2001 | 12 | 14 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2001 | 12 | 15 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2001 | 12 | 16 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2001 | 12 | 17 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2001 | 12 | 18 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2001 | 12 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2001 | 12 | 20 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2001 | 12 | 21 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2001 | 12 | 22 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2001 | 12 | 23 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2001 | 12 | 24 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2001 | 12 | 25 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2001 | 12 | 26 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2001 | 12 | 27 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2001 | 12 | 28 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2001 | 12 | 29 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2001 | 12 | 30 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2001 | 12 | 31 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2002 | 1 | 1 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 1 | 2 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2002 | 1 | 3 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2002 | 1 | 4 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2002 | 1 | 5 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2002 | 1 | 6 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2002 | 1 | 7 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 1 | 8 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2002 | 1 | 9 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2002 | 1 | 10 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2002 | 1 | 11 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2002 | 1 | 12 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2002 | 1 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2002 | 1 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2002 | 1 | 15 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2002 | 1 | 16 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2002 | 1 | 17 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2002 | 1 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2002 | 1 | 19 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2002 | 1 | 20 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2002 | 1 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2002 | 1 | 22 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 1 | 23 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 1 | 24 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2002 | 1 | 25 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2002 | 1 | 26 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2002 | 1 | 27 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2002 | 1 | 28 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2002 | 1 | 29 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2002 | 1 | 30 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2002 | 1 | 31 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2002 | 2 | 1 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2002 | 2 | 2 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2002 | 2 | 3 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2002 | 2 | 4 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2002 | 2 | 5 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2002 | 2 | 6 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2002 | 2 | 7 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2002 | 2 | 8 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2002 | 2 | 9 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2002 | 2 | 10 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 2 | 11 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2002 | 2 | 12 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2002 | 2 | 13 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2002 | 2 | 14 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2002 | 2 | 15 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2002 | 2 | 16 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2002 | 2 | 17 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2002 | 2 | 18 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2002 | 2 | 19 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2002 | 2 | 20 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2002 | 2 | 21 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2002 | 2 | 22 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2002 | 2 | 23 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2002 | 2 | 24 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2002 | 2 | 25 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2002 | 2 | 26 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2002 | 2 | 27 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
2002 | 2 | 28 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2002 | 3 | 1 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2002 | 3 | 2 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
2002 | 3 | 3 | 246.8571 | 25 | 221.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2002 | 3 | 4 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
2002 | 3 | 5 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
2002 | 3 | 6 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2002 | 3 | 7 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2002 | 3 | 8 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
2002 | 3 | 9 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2002 | 3 | 10 | 526.3673 | 25 | 501.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
2002 | 3 | 11 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
2002 | 3 | 12 | 378.7755 | 25 | 353.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
2002 | 3 | 13 | 279.5102 | 25 | 254.5102 | 29.441 | 139.3858 | 0.77441 | 28.6666 | 89.27% | 302.0811 | 283.9562 | 6814.9493
2002 | 3 | 14 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
2002 | 3 | 15 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
2002 | 3 | 16 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2002 | 3 | 17 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2002 | 3 | 18 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2002 | 3 | 19 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2002 | 3 | 20 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
2002 | 3 | 21 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2002 | 3 | 22 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2002 | 3 | 23 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
2002 | 3 | 24 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
2002 | 3 | 25 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2002 | 3 | 26 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
2002 | 3 | 27 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2002 | 3 | 28 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2002 | 3 | 29 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2002 | 3 | 30 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
2002 | 3 | 31 | 449.3061 | 25 | 424.3061 | 29.1014 | 139.3858 | 0.77441 | 28.327 | 89.27% | 298.5026 | 280.5924 | 6734.2176
2002 | 4 | 1 | 698.7755 | 25 | 673.7755 | 28.6024 | 139.3858 | 0.77441 | 27.828 | 89.27% | 293.2449 | 275.6502 | 6615.6041
2002 | 4 | 2 | 813.7143 | 25 | 788.7143 | 28.3726 | 139.3858 | 0.77441 | 27.5982 | 89.27% | 290.8225 | 273.3731 | 6560.9549
2002 | 4 | 3 | 808.4898 | 25 | 783.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
2002 | 4 | 4 | 1174.2041 | 25 | 1149.2041 | 27.6516 | 139.3858 | 0.77441 | 26.8772 | 89.27% | 283.225 | 266.2315 | 6389.5553
2002 | 4 | 5 | 709.2245 | 25 | 684.2245 | 28.5816 | 139.3858 | 0.77441 | 27.8071 | 89.27% | 293.0246 | 275.4432 | 6610.636
2002 | 4 | 6 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
2002 | 4 | 7 | 384 | 25 | 359 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
2002 | 4 | 8 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
2002 | 4 | 9 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2002 | 4 | 10 | 434.9388 | 25 | 409.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
2002 | 4 | 11 | 450.6122 | 25 | 425.6122 | 29.0988 | 139.3858 | 0.77441 | 28.3244 | 89.27% | 298.475 | 280.5665 | 6733.5966
2002 | 4 | 12 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
2002 | 4 | 13 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2002 | 4 | 14 | 1724.0816 | 25 | 1699.0816 | 26.5518 | 139.3858 | 0.77441 | 25.7774 | 89.27% | 271.636 | 255.3379 | 6128.1088
2002 | 4 | 15 | 1384.4898 | 25 | 1359.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
2002 | 4 | 16 | 949.551 | 25 | 924.551 | 28.1009 | 139.3858 | 0.77441 | 27.3265 | 89.27% | 287.9596 | 270.6821 | 6496.3696
2002 | 4 | 17 | 612.5714 | 25 | 587.5714 | 28.7749 | 139.3858 | 0.77441 | 28.0004 | 89.27% | 295.0617 | 277.358 | 6656.591
2002 | 4 | 18 | 689.6327 | 25 | 664.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
2002 | 4 | 19 | 521.1429 | 25 | 496.1429 | 28.9577 | 139.3858 | 0.77441 | 28.1833 | 89.27% | 296.9886 | 279.1692 | 6700.0619
2002 | 4 | 20 | 397.0612 | 25 | 372.0612 | 29.2059 | 139.3858 | 0.77441 | 28.4315 | 89.27% | 299.6036 | 281.6274 | 6759.0581
2002 | 4 | 21 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
2002 | 4 | 22 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
2002 | 4 | 23 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2002 | 4 | 24 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2002 | 4 | 25 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2002 | 4 | 26 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2002 | 4 | 27 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2002 | 4 | 28 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2002 | 4 | 29 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
2002 | 4 | 30 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2002 | 5 | 1 | 403.5918 | 25 | 378.5918 | 29.1928 | 139.3858 | 0.77441 | 28.4184 | 89.27% | 299.466 | 281.498 | 6755.9531
2002 | 5 | 2 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
2002 | 5 | 3 | 581.2245 | 25 | 556.2245 | 28.8376 | 139.3858 | 0.77441 | 28.0631 | 89.27% | 295.7223 | 277.979 | 6671.4953
2002 | 5 | 4 | 394.449 | 25 | 369.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
2002 | 5 | 5 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
2002 | 5 | 6 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
2002 | 5 | 7 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2002 | 5 | 8 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2002 | 5 | 9 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2002 | 5 | 10 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2002 | 5 | 11 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2002 | 5 | 12 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2002 | 5 | 13 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2002 | 5 | 14 | 798.0408 | 25 | 773.0408 | 28.4039 | 139.3858 | 0.77441 | 27.6295 | 89.27% | 291.1528 | 273.6836 | 6568.4071
2002 | 5 | 15 | 801.9592 | 25 | 776.9592 | 28.3961 | 139.3858 | 0.77441 | 27.6217 | 89.27% | 291.0702 | 273.606 | 6566.5441
2002 | 5 | 16 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
2002 | 5 | 17 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2002 | 5 | 18 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
2002 | 5 | 19 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2002 | 5 | 20 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2002 | 5 | 21 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2002 | 5 | 22 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2002 | 5 | 23 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
2002 | 5 | 24 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2002 | 5 | 25 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2002 | 5 | 26 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2002 | 5 | 27 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2002 | 5 | 28 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2002 | 5 | 29 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2002 | 5 | 30 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2002 | 5 | 31 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2002 | 6 | 1 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2002 | 6 | 2 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2002 | 6 | 3 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2002 | 6 | 4 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2002 | 6 | 5 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2002 | 6 | 6 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
2002 | 6 | 7 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2002 | 6 | 8 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2002 | 6 | 9 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2002 | 6 | 10 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2002 | 6 | 11 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2002 | 6 | 12 | 966.5306 | 25 | 941.5306 | 28.0669 | 139.3858 | 0.77441 | 27.2925 | 89.27% | 287.6018 | 270.3457 | 6488.2964
2002 | 6 | 13 | 1242.1224 | 25 | 1217.1224 | 27.5158 | 139.3858 | 0.77441 | 26.7413 | 89.27% | 281.7936 | 264.8859 | 6357.2626
2002 | 6 | 14 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
2002 | 6 | 15 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
2002 | 6 | 16 | 450.6122 | 25 | 425.6122 | 29.0988 | 139.3858 | 0.77441 | 28.3244 | 89.27% | 298.475 | 280.5665 | 6733.5966
2002 | 6 | 17 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
2002 | 6 | 18 | 402.2857 | 25 | 377.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
2002 | 6 | 19 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
2002 | 6 | 20 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2002 | 6 | 21 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2002 | 6 | 22 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2002 | 6 | 23 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2002 | 6 | 24 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2002 | 6 | 25 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2002 | 6 | 26 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2002 | 6 | 27 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2002 | 6 | 28 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2002 | 6 | 29 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2002 | 6 | 30 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2002 | 7 | 1 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2002 | 7 | 2 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2002 | 7 | 3 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2002 | 7 | 4 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2002 | 7 | 5 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2002 | 7 | 6 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2002 | 7 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2002 | 7 | 8 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2002 | 7 | 9 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2002 | 7 | 10 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2002 | 7 | 11 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2002 | 7 | 12 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2002 | 7 | 13 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2002 | 7 | 14 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2002 | 7 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2002 | 7 | 16 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2002 | 7 | 17 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2002 | 7 | 18 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2002 | 7 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2002 | 7 | 20 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 7 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2002 | 7 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2002 | 7 | 23 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2002 | 7 | 24 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2002 | 7 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2002 | 7 | 26 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2002 | 7 | 27 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2002 | 7 | 28 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2002 | 7 | 29 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2002 | 7 | 30 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2002 | 7 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2002 | 8 | 1 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2002 | 8 | 2 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2002 | 8 | 3 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2002 | 8 | 4 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2002 | 8 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2002 | 8 | 6 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
2002 | 8 | 7 | 10.9714 | 5 | 5.9714 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
2002 | 8 | 8 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2002 | 8 | 9 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2002 | 8 | 10 | 6.9224 | 5 | 1.9224 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
2002 | 8 | 11 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
2002 | 8 | 12 | 5.7469 | 5 | 0.74694 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
2002 | 8 | 13 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
2002 | 8 | 14 | 5.0939 | 5 | 0.093878 | 29.9898 | 0 | 0 | 29.9898 | 0% | 0 | 0 | 0
2002 | 8 | 15 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
2002 | 8 | 16 | 4.4408 | 5 | 0 | 29.9911 | 0 | 0 | 29.9911 | 0% | 0 | 0 | 0
2002 | 8 | 17 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
2002 | 8 | 18 | 5.4857 | 5 | 0.48571 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
2002 | 8 | 19 | 5.2245 | 5 | 0.22449 | 29.9896 | 0 | 0 | 29.9896 | 0% | 0 | 0 | 0
2002 | 8 | 20 | 4.9633 | 5 | 0 | 29.9901 | 0 | 0 | 29.9901 | 0% | 0 | 0 | 0
2002 | 8 | 21 | 4.702 | 5 | 0 | 29.9906 | 0 | 0 | 29.9906 | 0% | 0 | 0 | 0
2002 | 8 | 22 | 4.3102 | 5 | 0 | 29.9914 | 0 | 0 | 29.9914 | 0% | 0 | 0 | 0
2002 | 8 | 23 | 4.1796 | 5 | 0 | 29.9916 | 0 | 0 | 29.9916 | 0% | 0 | 0 | 0
2002 | 8 | 24 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
2002 | 8 | 25 | 3.9184 | 5 | 0 | 29.9922 | 0 | 0 | 29.9922 | 0% | 0 | 0 | 0
2002 | 8 | 26 | 3.7878 | 5 | 0 | 29.9924 | 0 | 0 | 29.9924 | 0% | 0 | 0 | 0
2002 | 8 | 27 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
2002 | 8 | 28 | 3.1347 | 5 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
2002 | 8 | 29 | 3.0041 | 5 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
2002 | 8 | 30 | 3.6571 | 5 | 0 | 29.9927 | 0 | 0 | 29.9927 | 0% | 0 | 0 | 0
2002 | 8 | 31 | 3.5265 | 5 | 0 | 29.9929 | 0 | 0 | 29.9929 | 0% | 0 | 0 | 0
2002 | 9 | 1 | 3.1347 | 15 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
2002 | 9 | 2 | 3.1347 | 15 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
2002 | 9 | 3 | 3.1347 | 15 | 0 | 29.9937 | 0 | 0 | 29.9937 | 0% | 0 | 0 | 0
2002 | 9 | 4 | 3.3959 | 15 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
2002 | 9 | 5 | 3.3959 | 15 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
2002 | 9 | 6 | 3.0041 | 15 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
2002 | 9 | 7 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
2002 | 9 | 8 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
2002 | 9 | 9 | 2.2204 | 15 | 0 | 29.9956 | 0 | 0 | 29.9956 | 0% | 0 | 0 | 0
2002 | 9 | 10 | 1.9592 | 15 | 0 | 29.9961 | 0 | 0 | 29.9961 | 0% | 0 | 0 | 0
2002 | 9 | 11 | 1.8286 | 15 | 0 | 29.9963 | 0 | 0 | 29.9963 | 0% | 0 | 0 | 0
2002 | 9 | 12 | 1.698 | 15 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
2002 | 9 | 13 | 1.698 | 15 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
2002 | 9 | 14 | 1.698 | 15 | 0 | 29.9966 | 0 | 0 | 29.9966 | 0% | 0 | 0 | 0
2002 | 9 | 15 | 1.8286 | 15 | 0 | 29.9963 | 0 | 0 | 29.9963 | 0% | 0 | 0 | 0
2002 | 9 | 16 | 4.8327 | 15 | 0 | 29.9903 | 0 | 0 | 29.9903 | 0% | 0 | 0 | 0
2002 | 9 | 17 | 7.1837 | 15 | 0 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
2002 | 9 | 18 | 5.4857 | 15 | 0 | 29.989 | 0 | 0 | 29.989 | 0% | 0 | 0 | 0
2002 | 9 | 19 | 4.049 | 15 | 0 | 29.9919 | 0 | 0 | 29.9919 | 0% | 0 | 0 | 0
2002 | 9 | 20 | 3.3959 | 15 | 0 | 29.9932 | 0 | 0 | 29.9932 | 0% | 0 | 0 | 0
2002 | 9 | 21 | 3.0041 | 15 | 0 | 29.994 | 0 | 0 | 29.994 | 0% | 0 | 0 | 0
2002 | 9 | 22 | 2.8735 | 15 | 0 | 29.9943 | 0 | 0 | 29.9943 | 0% | 0 | 0 | 0
2002 | 9 | 23 | 2.7429 | 15 | 0 | 29.9945 | 0 | 0 | 29.9945 | 0% | 0 | 0 | 0
2002 | 9 | 24 | 2.6122 | 15 | 0 | 29.9948 | 0 | 0 | 29.9948 | 0% | 0 | 0 | 0
2002 | 9 | 25 | 2.4816 | 15 | 0 | 29.995 | 0 | 0 | 29.995 | 0% | 0 | 0 | 0
2002 | 9 | 26 | 2.351 | 15 | 0 | 29.9953 | 0 | 0 | 29.9953 | 0% | 0 | 0 | 0
2002 | 9 | 27 | 2.4816 | 15 | 0 | 29.995 | 0 | 0 | 29.995 | 0% | 0 | 0 | 0
2002 | 9 | 28 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2002 | 9 | 29 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2002 | 9 | 30 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2002 | 10 | 1 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
2002 | 10 | 2 | 5.7469 | 15 | 0 | 29.9885 | 0 | 0 | 29.9885 | 0% | 0 | 0 | 0
2002 | 10 | 3 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
2002 | 10 | 4 | 8.8816 | 15 | 0 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
2002 | 10 | 5 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
2002 | 10 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2002 | 10 | 7 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2002 | 10 | 8 | 12.0163 | 15 | 0 | 29.976 | 0 | 0 | 29.976 | 0% | 0 | 0 | 0
2002 | 10 | 9 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
2002 | 10 | 10 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
2002 | 10 | 11 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
2002 | 10 | 12 | 10.3184 | 15 | 0 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
2002 | 10 | 13 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
2002 | 10 | 14 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2002 | 10 | 15 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2002 | 10 | 16 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2002 | 10 | 17 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2002 | 10 | 18 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2002 | 10 | 19 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2002 | 10 | 20 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2002 | 10 | 21 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2002 | 10 | 22 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2002 | 10 | 23 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2002 | 10 | 24 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2002 | 10 | 25 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2002 | 10 | 26 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2002 | 10 | 27 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2002 | 10 | 28 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2002 | 10 | 29 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2002 | 10 | 30 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2002 | 10 | 31 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2002 | 11 | 1 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2002 | 11 | 2 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2002 | 11 | 3 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2002 | 11 | 4 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2002 | 11 | 5 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2002 | 11 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2002 | 11 | 7 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2002 | 11 | 8 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2002 | 11 | 9 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
2002 | 11 | 10 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2002 | 11 | 11 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2002 | 11 | 12 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2002 | 11 | 13 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2002 | 11 | 14 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2002 | 11 | 15 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2002 | 11 | 16 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2002 | 11 | 17 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2002 | 11 | 18 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2002 | 11 | 19 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2002 | 11 | 20 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2002 | 11 | 21 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2002 | 11 | 22 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2002 | 11 | 23 | 239.0204 | 15 | 224.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
2002 | 11 | 24 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2002 | 11 | 25 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
2002 | 11 | 26 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
2002 | 11 | 27 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2002 | 11 | 28 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2002 | 11 | 29 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2002 | 11 | 30 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2002 | 12 | 1 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2002 | 12 | 2 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2002 | 12 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2002 | 12 | 4 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2002 | 12 | 5 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2002 | 12 | 6 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2002 | 12 | 7 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2002 | 12 | 8 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2002 | 12 | 9 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2002 | 12 | 10 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2002 | 12 | 11 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2002 | 12 | 12 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2002 | 12 | 13 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2002 | 12 | 14 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2002 | 12 | 15 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2002 | 12 | 16 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2002 | 12 | 17 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2002 | 12 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2002 | 12 | 19 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2002 | 12 | 20 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2002 | 12 | 21 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2002 | 12 | 22 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2002 | 12 | 23 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2002 | 12 | 24 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2002 | 12 | 25 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2002 | 12 | 26 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2002 | 12 | 27 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2002 | 12 | 28 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2002 | 12 | 29 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2002 | 12 | 30 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2002 | 12 | 31 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2003 | 1 | 1 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2003 | 1 | 2 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2003 | 1 | 3 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2003 | 1 | 4 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2003 | 1 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2003 | 1 | 6 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2003 | 1 | 7 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2003 | 1 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2003 | 1 | 9 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2003 | 1 | 10 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2003 | 1 | 11 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2003 | 1 | 12 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2003 | 1 | 13 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2003 | 1 | 14 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2003 | 1 | 15 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2003 | 1 | 16 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2003 | 1 | 17 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2003 | 1 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2003 | 1 | 19 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2003 | 1 | 20 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2003 | 1 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2003 | 1 | 22 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 1 | 23 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 1 | 24 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 1 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 1 | 26 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 1 | 27 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 1 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2003 | 1 | 29 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 1 | 30 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 1 | 31 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 2 | 1 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 2 | 2 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2003 | 2 | 3 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 2 | 4 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2003 | 2 | 5 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2003 | 2 | 6 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2003 | 2 | 7 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2003 | 2 | 8 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2003 | 2 | 9 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2003 | 2 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2003 | 2 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2003 | 2 | 12 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2003 | 2 | 13 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2003 | 2 | 14 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2003 | 2 | 15 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 2 | 16 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 2 | 17 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 2 | 18 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 2 | 19 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 2 | 20 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2003 | 2 | 21 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2003 | 2 | 22 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2003 | 2 | 23 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 2 | 24 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2003 | 2 | 25 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2003 | 2 | 26 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2003 | 2 | 27 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 2 | 28 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 3 | 1 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
2003 | 3 | 2 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
2003 | 3 | 3 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2003 | 3 | 4 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 5 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 6 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 7 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 8 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 9 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 10 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 11 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 12 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2003 | 3 | 13 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2003 | 3 | 14 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2003 | 3 | 15 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
2003 | 3 | 16 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
2003 | 3 | 17 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2003 | 3 | 18 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
2003 | 3 | 19 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2003 | 3 | 20 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2003 | 3 | 21 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2003 | 3 | 22 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2003 | 3 | 23 | 343.5102 | 25 | 318.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
2003 | 3 | 24 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2003 | 3 | 25 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
2003 | 3 | 26 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
2003 | 3 | 27 | 628.2449 | 25 | 603.2449 | 28.7435 | 139.3858 | 0.77441 | 27.9691 | 89.27% | 294.7313 | 277.0475 | 6649.1388
2003 | 3 | 28 | 690.9388 | 25 | 665.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
2003 | 3 | 29 | 653.0612 | 25 | 628.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
2003 | 3 | 30 | 1189.8776 | 25 | 1164.8776 | 27.6202 | 139.3858 | 0.77441 | 26.8458 | 89.27% | 282.8946 | 265.921 | 6382.1032
2003 | 3 | 31 | 811.102 | 25 | 786.102 | 28.3778 | 139.3858 | 0.77441 | 27.6034 | 89.27% | 290.8775 | 273.4249 | 6562.197
2003 | 4 | 1 | 485.8776 | 25 | 460.8776 | 29.0282 | 139.3858 | 0.77441 | 28.2538 | 89.27% | 297.7318 | 279.8679 | 6716.8293
2003 | 4 | 2 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
2003 | 4 | 3 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2003 | 4 | 4 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2003 | 4 | 5 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2003 | 4 | 6 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2003 | 4 | 7 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2003 | 4 | 8 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2003 | 4 | 9 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2003 | 4 | 10 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2003 | 4 | 11 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2003 | 4 | 12 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
2003 | 4 | 13 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
2003 | 4 | 14 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
2003 | 4 | 15 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
2003 | 4 | 16 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
2003 | 4 | 17 | 342.2041 | 25 | 317.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
2003 | 4 | 18 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2003 | 4 | 19 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2003 | 4 | 20 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2003 | 4 | 21 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2003 | 4 | 22 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2003 | 4 | 23 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2003 | 4 | 24 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
2003 | 4 | 25 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2003 | 4 | 26 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
2003 | 4 | 27 | 666.1224 | 25 | 641.1224 | 28.6678 | 139.3858 | 0.77441 | 27.8933 | 89.27% | 293.933 | 276.2971 | 6631.1294
2003 | 4 | 28 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
2003 | 4 | 29 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
2003 | 4 | 30 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2003 | 5 | 1 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2003 | 5 | 2 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2003 | 5 | 3 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
2003 | 5 | 4 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
2003 | 5 | 5 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2003 | 5 | 6 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
2003 | 5 | 7 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2003 | 5 | 8 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2003 | 5 | 9 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2003 | 5 | 10 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
2003 | 5 | 11 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2003 | 5 | 12 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2003 | 5 | 13 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2003 | 5 | 14 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2003 | 5 | 15 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2003 | 5 | 16 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2003 | 5 | 17 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
2003 | 5 | 18 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2003 | 5 | 19 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2003 | 5 | 20 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2003 | 5 | 21 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2003 | 5 | 22 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2003 | 5 | 23 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2003 | 5 | 24 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2003 | 5 | 25 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2003 | 5 | 26 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2003 | 5 | 27 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2003 | 5 | 28 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2003 | 5 | 29 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2003 | 5 | 30 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
2003 | 5 | 31 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
2003 | 6 | 1 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2003 | 6 | 2 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2003 | 6 | 3 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2003 | 6 | 4 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2003 | 6 | 5 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2003 | 6 | 6 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2003 | 6 | 7 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
2003 | 6 | 8 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2003 | 6 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2003 | 6 | 10 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2003 | 6 | 11 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2003 | 6 | 12 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2003 | 6 | 13 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2003 | 6 | 14 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2003 | 6 | 15 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2003 | 6 | 16 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2003 | 6 | 17 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2003 | 6 | 18 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2003 | 6 | 19 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2003 | 6 | 20 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2003 | 6 | 21 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2003 | 6 | 22 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2003 | 6 | 23 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
2003 | 6 | 24 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2003 | 6 | 25 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2003 | 6 | 26 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2003 | 6 | 27 | 24.8163 | 25 | 0 | 29.9504 | 0 | 0 | 29.9504 | 0% | 0 | 0 | 0
2003 | 6 | 28 | 20.898 | 25 | 0 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2003 | 6 | 29 | 18.2857 | 25 | 0 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2003 | 6 | 30 | 15.6735 | 25 | 0 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2003 | 7 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2003 | 7 | 2 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
2003 | 7 | 3 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
2003 | 7 | 4 | 9.7959 | 5 | 4.7959 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
2003 | 7 | 5 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2003 | 7 | 6 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
2003 | 7 | 7 | 7.8367 | 5 | 2.8367 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2003 | 7 | 8 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
2003 | 7 | 9 | 7.1837 | 5 | 2.1837 | 29.9856 | 0 | 0 | 29.9856 | 0% | 0 | 0 | 0
2003 | 7 | 10 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
2003 | 7 | 11 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
2003 | 7 | 12 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2003 | 7 | 13 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2003 | 7 | 14 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
2003 | 7 | 15 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
2003 | 7 | 16 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
2003 | 7 | 17 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
2003 | 7 | 18 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2003 | 7 | 19 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2003 | 7 | 20 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2003 | 7 | 21 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
2003 | 7 | 22 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
2003 | 7 | 23 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
2003 | 7 | 24 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2003 | 7 | 25 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2003 | 7 | 26 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2003 | 7 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2003 | 7 | 28 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 7 | 29 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2003 | 7 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2003 | 7 | 31 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
2003 | 8 | 1 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
2003 | 8 | 2 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2003 | 8 | 3 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2003 | 8 | 4 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2003 | 8 | 5 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2003 | 8 | 6 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2003 | 8 | 7 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2003 | 8 | 8 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2003 | 8 | 9 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2003 | 8 | 10 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2003 | 8 | 11 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2003 | 8 | 12 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2003 | 8 | 13 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2003 | 8 | 14 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
2003 | 8 | 15 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2003 | 8 | 16 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2003 | 8 | 17 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2003 | 8 | 18 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2003 | 8 | 19 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2003 | 8 | 20 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2003 | 8 | 21 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2003 | 8 | 22 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2003 | 8 | 23 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2003 | 8 | 24 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2003 | 8 | 25 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
2003 | 8 | 26 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
2003 | 8 | 27 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
2003 | 8 | 28 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2003 | 8 | 29 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2003 | 8 | 30 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
2003 | 8 | 31 | 7.3143 | 5 | 2.3143 | 29.9854 | 0 | 0 | 29.9854 | 0% | 0 | 0 | 0
2003 | 9 | 1 | 6.7918 | 15 | 0 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
2003 | 9 | 2 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
2003 | 9 | 3 | 6.1388 | 15 | 0 | 29.9877 | 0 | 0 | 29.9877 | 0% | 0 | 0 | 0
2003 | 9 | 4 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2003 | 9 | 5 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2003 | 9 | 6 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2003 | 9 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2003 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2003 | 9 | 9 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2003 | 9 | 10 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
2003 | 9 | 11 | 9.5347 | 15 | 0 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
2003 | 9 | 12 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
2003 | 9 | 13 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2003 | 9 | 14 | 7.4449 | 15 | 0 | 29.9851 | 0 | 0 | 29.9851 | 0% | 0 | 0 | 0
2003 | 9 | 15 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2003 | 9 | 16 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2003 | 9 | 17 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2003 | 9 | 18 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2003 | 9 | 19 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2003 | 9 | 20 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2003 | 9 | 21 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2003 | 9 | 22 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2003 | 9 | 23 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2003 | 9 | 24 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
2003 | 9 | 25 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
2003 | 9 | 26 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
2003 | 9 | 27 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2003 | 9 | 28 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2003 | 9 | 29 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
2003 | 9 | 30 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
2003 | 10 | 1 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2003 | 10 | 2 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2003 | 10 | 3 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2003 | 10 | 4 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2003 | 10 | 5 | 246.8571 | 15 | 231.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2003 | 10 | 6 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2003 | 10 | 7 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
2003 | 10 | 8 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
2003 | 10 | 9 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2003 | 10 | 10 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2003 | 10 | 11 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2003 | 10 | 12 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2003 | 10 | 13 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2003 | 10 | 14 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2003 | 10 | 15 | 568.1633 | 15 | 553.1633 | 28.8637 | 139.3858 | 0.77441 | 28.0893 | 89.27% | 295.9976 | 278.2377 | 6677.7054
2003 | 10 | 16 | 862.0408 | 15 | 847.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
2003 | 10 | 17 | 402.2857 | 15 | 387.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
2003 | 10 | 18 | 272.9796 | 15 | 257.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2003 | 10 | 19 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2003 | 10 | 20 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2003 | 10 | 21 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2003 | 10 | 22 | 382.6939 | 15 | 367.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
2003 | 10 | 23 | 272.9796 | 15 | 257.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2003 | 10 | 24 | 228.5714 | 15 | 213.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2003 | 10 | 25 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2003 | 10 | 26 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2003 | 10 | 27 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
2003 | 10 | 28 | 1024 | 15 | 1009 | 27.952 | 139.3858 | 0.77441 | 27.1776 | 89.27% | 286.3906 | 269.2072 | 6460.9718
2003 | 10 | 29 | 1093.2245 | 15 | 1078.2245 | 27.8136 | 139.3858 | 0.77441 | 27.0391 | 89.27% | 284.9317 | 267.8358 | 6428.0581
2003 | 10 | 30 | 1619.5918 | 15 | 1604.5918 | 26.7608 | 139.3858 | 0.77441 | 25.9864 | 89.27% | 273.8382 | 257.4079 | 6177.7898
2003 | 10 | 31 | 765.3878 | 15 | 750.3878 | 28.4692 | 139.3858 | 0.77441 | 27.6948 | 89.27% | 291.841 | 274.3305 | 6583.9324
2003 | 11 | 1 | 488.4898 | 15 | 473.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
2003 | 11 | 2 | 377.4694 | 15 | 362.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
2003 | 11 | 3 | 363.102 | 15 | 348.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
2003 | 11 | 4 | 343.5102 | 15 | 328.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
2003 | 11 | 5 | 296.4898 | 15 | 281.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2003 | 11 | 6 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2003 | 11 | 7 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2003 | 11 | 8 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2003 | 11 | 9 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2003 | 11 | 10 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2003 | 11 | 11 | 160.6531 | 15 | 145.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2003 | 11 | 12 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2003 | 11 | 13 | 462.3673 | 15 | 447.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
2003 | 11 | 14 | 513.3061 | 15 | 498.3061 | 28.9734 | 139.3858 | 0.77441 | 28.199 | 89.27% | 297.1537 | 279.3245 | 6703.788
2003 | 11 | 15 | 320 | 15 | 305 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
2003 | 11 | 16 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2003 | 11 | 17 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2003 | 11 | 18 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2003 | 11 | 19 | 184.1633 | 15 | 169.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2003 | 11 | 20 | 688.3265 | 15 | 673.3265 | 28.6233 | 139.3858 | 0.77441 | 27.8489 | 89.27% | 293.4651 | 275.8572 | 6620.5722
2003 | 11 | 21 | 916.898 | 15 | 901.898 | 28.1662 | 139.3858 | 0.77441 | 27.3918 | 89.27% | 288.6478 | 271.329 | 6511.8949
2003 | 11 | 22 | 495.0204 | 15 | 480.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
2003 | 11 | 23 | 361.7959 | 15 | 346.7959 | 29.2764 | 139.3858 | 0.77441 | 28.502 | 89.27% | 300.3469 | 282.3261 | 6775.8255
2003 | 11 | 24 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
2003 | 11 | 25 | 259.9184 | 15 | 244.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2003 | 11 | 26 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2003 | 11 | 27 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2003 | 11 | 28 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2003 | 11 | 29 | 765.3878 | 15 | 750.3878 | 28.4692 | 139.3858 | 0.77441 | 27.6948 | 89.27% | 291.841 | 274.3305 | 6583.9324
2003 | 11 | 30 | 559.0204 | 15 | 544.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
2003 | 12 | 1 | 384 | 5 | 379 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
2003 | 12 | 2 | 296.4898 | 5 | 291.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2003 | 12 | 3 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2003 | 12 | 4 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2003 | 12 | 5 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2003 | 12 | 6 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2003 | 12 | 7 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
2003 | 12 | 8 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2003 | 12 | 9 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2003 | 12 | 10 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2003 | 12 | 11 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2003 | 12 | 12 | 1371.4286 | 5 | 1366.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
2003 | 12 | 13 | 1018.7755 | 5 | 1013.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
2003 | 12 | 14 | 553.7959 | 5 | 548.7959 | 28.8924 | 139.3858 | 0.77441 | 28.118 | 89.27% | 296.3004 | 278.5224 | 6684.5366
2003 | 12 | 15 | 434.9388 | 5 | 429.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
2003 | 12 | 16 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
2003 | 12 | 17 | 398.3673 | 5 | 393.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
2003 | 12 | 18 | 3291.4286 | 5 | 3286.4286 | 23.4171 | 0 | 0 | 23.4171 | 0% | 0 | 0 | 0
2003 | 12 | 19 | 1711.0204 | 5 | 1706.0204 | 26.578 | 139.3858 | 0.77441 | 25.8035 | 89.27% | 271.9113 | 255.5966 | 6134.3189
2003 | 12 | 20 | 928.6531 | 5 | 923.6531 | 28.1427 | 139.3858 | 0.77441 | 27.3683 | 89.27% | 288.4001 | 271.0961 | 6506.3058
2003 | 12 | 21 | 572.0816 | 5 | 567.0816 | 28.8558 | 139.3858 | 0.77441 | 28.0814 | 89.27% | 295.915 | 278.1601 | 6675.8424
2003 | 12 | 22 | 466.2857 | 5 | 461.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
2003 | 12 | 23 | 387.9184 | 5 | 382.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2003 | 12 | 24 | 353.9592 | 5 | 348.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
2003 | 12 | 25 | 1170.2857 | 5 | 1165.2857 | 27.6594 | 139.3858 | 0.77441 | 26.885 | 89.27% | 283.3076 | 266.3091 | 6391.4184
2003 | 12 | 26 | 1280 | 5 | 1275 | 27.44 | 139.3858 | 0.77441 | 26.6656 | 89.27% | 280.9953 | 264.1356 | 6339.2533
2003 | 12 | 27 | 768 | 5 | 763 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
2003 | 12 | 28 | 517.2245 | 5 | 512.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
2003 | 12 | 29 | 415.3469 | 5 | 410.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
2003 | 12 | 30 | 368.3265 | 5 | 363.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
2003 | 12 | 31 | 333.0612 | 5 | 328.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
2004 | 1 | 1 | 301.7143 | 5 | 296.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2004 | 1 | 2 | 266.449 | 5 | 261.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
2004 | 1 | 3 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2004 | 1 | 4 | 252.0816 | 5 | 247.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2004 | 1 | 5 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2004 | 1 | 6 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2004 | 1 | 7 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2004 | 1 | 8 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2004 | 1 | 9 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2004 | 1 | 10 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2004 | 1 | 11 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2004 | 1 | 12 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2004 | 1 | 13 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2004 | 1 | 14 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2004 | 1 | 15 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2004 | 1 | 16 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2004 | 1 | 17 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2004 | 1 | 18 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2004 | 1 | 19 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2004 | 1 | 20 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2004 | 1 | 21 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2004 | 1 | 22 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2004 | 1 | 23 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2004 | 1 | 24 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2004 | 1 | 25 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2004 | 1 | 26 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2004 | 1 | 27 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2004 | 1 | 28 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2004 | 1 | 29 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2004 | 1 | 30 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2004 | 1 | 31 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2004 | 2 | 1 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2004 | 2 | 2 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2004 | 2 | 3 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2004 | 2 | 4 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2004 | 2 | 5 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2004 | 2 | 6 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2004 | 2 | 7 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2004 | 2 | 8 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2004 | 2 | 9 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2004 | 2 | 10 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2004 | 2 | 11 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2004 | 2 | 12 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2004 | 2 | 13 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2004 | 2 | 14 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2004 | 2 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2004 | 2 | 16 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2004 | 2 | 17 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2004 | 2 | 18 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 2 | 19 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 2 | 20 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 2 | 21 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 2 | 22 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2004 | 2 | 23 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2004 | 2 | 24 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2004 | 2 | 25 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2004 | 2 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 2 | 27 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2004 | 2 | 28 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2004 | 2 | 29 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2004 | 3 | 1 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
2004 | 3 | 2 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2004 | 3 | 3 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
2004 | 3 | 4 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2004 | 3 | 5 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
2004 | 3 | 6 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2004 | 3 | 7 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2004 | 3 | 8 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2004 | 3 | 9 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2004 | 3 | 10 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2004 | 3 | 11 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
2004 | 3 | 12 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2004 | 3 | 13 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2004 | 3 | 14 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
2004 | 3 | 15 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2004 | 3 | 16 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2004 | 3 | 17 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2004 | 3 | 18 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2004 | 3 | 19 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2004 | 3 | 20 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2004 | 3 | 21 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2004 | 3 | 22 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2004 | 3 | 23 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2004 | 3 | 24 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2004 | 3 | 25 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2004 | 3 | 26 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2004 | 3 | 27 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
2004 | 3 | 28 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
2004 | 3 | 29 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
2004 | 3 | 30 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2004 | 3 | 31 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
2004 | 4 | 1 | 446.6939 | 25 | 421.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
2004 | 4 | 2 | 830.6939 | 25 | 805.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
2004 | 4 | 3 | 1076.2449 | 25 | 1051.2449 | 27.8475 | 139.3858 | 0.77441 | 27.0731 | 89.27% | 285.2895 | 268.1721 | 6436.1313
2004 | 4 | 4 | 694.8571 | 25 | 669.8571 | 28.6103 | 139.3858 | 0.77441 | 27.8359 | 89.27% | 293.3274 | 275.7278 | 6617.4671
2004 | 4 | 5 | 562.9388 | 25 | 537.9388 | 28.8741 | 139.3858 | 0.77441 | 28.0997 | 89.27% | 296.1077 | 278.3412 | 6680.1895
2004 | 4 | 6 | 414.0408 | 25 | 389.0408 | 29.1719 | 139.3858 | 0.77441 | 28.3975 | 89.27% | 299.2458 | 281.291 | 6750.985
2004 | 4 | 7 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2004 | 4 | 8 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
2004 | 4 | 9 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2004 | 4 | 10 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
2004 | 4 | 11 | 246.8571 | 25 | 221.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2004 | 4 | 12 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2004 | 4 | 13 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2004 | 4 | 14 | 1345.3061 | 25 | 1320.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
2004 | 4 | 15 | 1110.2041 | 25 | 1085.2041 | 27.7796 | 139.3858 | 0.77441 | 27.0052 | 89.27% | 284.5738 | 267.4994 | 6419.985
2004 | 4 | 16 | 656.9796 | 25 | 631.9796 | 28.686 | 139.3858 | 0.77441 | 27.9116 | 89.27% | 294.1257 | 276.4782 | 6635.4765
2004 | 4 | 17 | 448 | 25 | 423 | 29.104 | 139.3858 | 0.77441 | 28.3296 | 89.27% | 298.5301 | 280.6183 | 6734.8386
2004 | 4 | 18 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
2004 | 4 | 19 | 316.0816 | 25 | 291.0816 | 29.3678 | 139.3858 | 0.77441 | 28.5934 | 89.27% | 301.3103 | 283.2317 | 6797.561
2004 | 4 | 20 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
2004 | 4 | 21 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2004 | 4 | 22 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2004 | 4 | 23 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2004 | 4 | 24 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2004 | 4 | 25 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
2004 | 4 | 26 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2004 | 4 | 27 | 274.2857 | 25 | 249.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
2004 | 4 | 28 | 239.0204 | 25 | 214.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
2004 | 4 | 29 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2004 | 4 | 30 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2004 | 5 | 1 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
2004 | 5 | 2 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
2004 | 5 | 3 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
2004 | 5 | 4 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
2004 | 5 | 5 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2004 | 5 | 6 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2004 | 5 | 7 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2004 | 5 | 8 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2004 | 5 | 9 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
2004 | 5 | 10 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2004 | 5 | 11 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2004 | 5 | 12 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
2004 | 5 | 13 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2004 | 5 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2004 | 5 | 15 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2004 | 5 | 16 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
2004 | 5 | 17 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
2004 | 5 | 18 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2004 | 5 | 19 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
2004 | 5 | 20 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2004 | 5 | 21 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2004 | 5 | 22 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2004 | 5 | 23 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2004 | 5 | 24 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2004 | 5 | 25 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
2004 | 5 | 26 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
2004 | 5 | 27 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2004 | 5 | 28 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2004 | 5 | 29 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2004 | 5 | 30 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2004 | 5 | 31 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
2004 | 6 | 1 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
2004 | 6 | 2 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
2004 | 6 | 3 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2004 | 6 | 4 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
2004 | 6 | 5 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2004 | 6 | 6 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2004 | 6 | 7 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2004 | 6 | 8 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2004 | 6 | 9 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2004 | 6 | 10 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2004 | 6 | 11 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2004 | 6 | 12 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2004 | 6 | 13 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
2004 | 6 | 14 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
2004 | 6 | 15 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2004 | 6 | 16 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
2004 | 6 | 17 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
2004 | 6 | 18 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2004 | 6 | 19 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2004 | 6 | 20 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2004 | 6 | 21 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2004 | 6 | 22 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
2004 | 6 | 23 | 30.0408 | 25 | 5.0408 | 29.9399 | 0 | 0 | 29.9399 | 0% | 0 | 0 | 0
2004 | 6 | 24 | 28.7347 | 25 | 3.7347 | 29.9425 | 0 | 0 | 29.9425 | 0% | 0 | 0 | 0
2004 | 6 | 25 | 26.1224 | 25 | 1.1224 | 29.9478 | 0 | 0 | 29.9478 | 0% | 0 | 0 | 0
2004 | 6 | 26 | 27.4286 | 25 | 2.4286 | 29.9451 | 0 | 0 | 29.9451 | 0% | 0 | 0 | 0
2004 | 6 | 27 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
2004 | 6 | 28 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
2004 | 6 | 29 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
2004 | 6 | 30 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2004 | 7 | 1 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2004 | 7 | 2 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2004 | 7 | 3 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2004 | 7 | 4 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2004 | 7 | 5 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2004 | 7 | 6 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2004 | 7 | 7 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2004 | 7 | 8 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2004 | 7 | 9 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2004 | 7 | 10 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2004 | 7 | 11 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2004 | 7 | 12 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2004 | 7 | 13 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2004 | 7 | 14 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2004 | 7 | 15 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2004 | 7 | 16 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2004 | 7 | 17 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2004 | 7 | 18 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2004 | 7 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2004 | 7 | 20 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2004 | 7 | 21 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2004 | 7 | 22 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2004 | 7 | 23 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2004 | 7 | 24 | 387.9184 | 5 | 382.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2004 | 7 | 25 | 245.551 | 5 | 240.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
2004 | 7 | 26 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2004 | 7 | 27 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2004 | 7 | 28 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2004 | 7 | 29 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2004 | 7 | 30 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2004 | 7 | 31 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2004 | 8 | 1 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2004 | 8 | 2 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2004 | 8 | 3 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2004 | 8 | 4 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2004 | 8 | 5 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2004 | 8 | 6 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2004 | 8 | 7 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2004 | 8 | 8 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2004 | 8 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2004 | 8 | 10 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2004 | 8 | 11 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2004 | 8 | 12 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2004 | 8 | 13 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2004 | 8 | 14 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2004 | 8 | 15 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2004 | 8 | 16 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2004 | 8 | 17 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2004 | 8 | 18 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2004 | 8 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2004 | 8 | 20 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2004 | 8 | 21 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2004 | 8 | 22 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2004 | 8 | 23 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2004 | 8 | 24 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2004 | 8 | 25 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2004 | 8 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 8 | 27 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2004 | 8 | 28 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2004 | 8 | 29 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 8 | 30 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2004 | 8 | 31 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2004 | 9 | 1 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2004 | 9 | 2 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2004 | 9 | 3 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2004 | 9 | 4 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2004 | 9 | 5 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2004 | 9 | 6 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2004 | 9 | 7 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2004 | 9 | 8 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2004 | 9 | 9 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2004 | 9 | 10 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2004 | 9 | 11 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
2004 | 9 | 12 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2004 | 9 | 13 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2004 | 9 | 14 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
2004 | 9 | 15 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2004 | 9 | 16 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2004 | 9 | 17 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2004 | 9 | 18 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2004 | 9 | 19 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
2004 | 9 | 20 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2004 | 9 | 21 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2004 | 9 | 22 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2004 | 9 | 23 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2004 | 9 | 24 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2004 | 9 | 25 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2004 | 9 | 26 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2004 | 9 | 27 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2004 | 9 | 28 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2004 | 9 | 29 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2004 | 9 | 30 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2004 | 10 | 1 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2004 | 10 | 2 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2004 | 10 | 3 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2004 | 10 | 4 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2004 | 10 | 5 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2004 | 10 | 6 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2004 | 10 | 7 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2004 | 10 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2004 | 10 | 9 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2004 | 10 | 10 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2004 | 10 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2004 | 10 | 12 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2004 | 10 | 13 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2004 | 10 | 14 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2004 | 10 | 15 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2004 | 10 | 16 | 240.3265 | 15 | 225.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2004 | 10 | 17 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2004 | 10 | 18 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
2004 | 10 | 19 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
2004 | 10 | 20 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2004 | 10 | 21 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2004 | 10 | 22 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2004 | 10 | 23 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2004 | 10 | 24 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2004 | 10 | 25 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
2004 | 10 | 26 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2004 | 10 | 27 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2004 | 10 | 28 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2004 | 10 | 29 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2004 | 10 | 30 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
2004 | 10 | 31 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2004 | 11 | 1 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2004 | 11 | 2 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2004 | 11 | 3 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2004 | 11 | 4 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
2004 | 11 | 5 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2004 | 11 | 6 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2004 | 11 | 7 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
2004 | 11 | 8 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
2004 | 11 | 9 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
2004 | 11 | 10 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2004 | 11 | 11 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2004 | 11 | 12 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2004 | 11 | 13 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2004 | 11 | 14 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2004 | 11 | 15 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2004 | 11 | 16 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2004 | 11 | 17 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2004 | 11 | 18 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2004 | 11 | 19 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2004 | 11 | 20 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2004 | 11 | 21 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2004 | 11 | 22 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2004 | 11 | 23 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2004 | 11 | 24 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2004 | 11 | 25 | 406.2041 | 15 | 391.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
2004 | 11 | 26 | 387.9184 | 15 | 372.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2004 | 11 | 27 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2004 | 11 | 28 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
2004 | 11 | 29 | 1645.7143 | 15 | 1630.7143 | 26.7086 | 139.3858 | 0.77441 | 25.9342 | 89.27% | 273.2877 | 256.8904 | 6165.3696
2004 | 11 | 30 | 825.4694 | 15 | 810.4694 | 28.3491 | 139.3858 | 0.77441 | 27.5747 | 89.27% | 290.5747 | 273.1402 | 6555.3658
2004 | 12 | 1 | 753.6327 | 5 | 748.6327 | 28.4927 | 139.3858 | 0.77441 | 27.7183 | 89.27% | 292.0887 | 274.5634 | 6589.5216
2004 | 12 | 2 | 1293.0612 | 5 | 1288.0612 | 27.4139 | 139.3858 | 0.77441 | 26.6395 | 89.27% | 280.72 | 263.8768 | 6333.0431
2004 | 12 | 3 | 642.6122 | 5 | 637.6122 | 28.7148 | 139.3858 | 0.77441 | 27.9404 | 89.27% | 294.4285 | 276.7628 | 6642.3077
2004 | 12 | 4 | 421.8776 | 5 | 416.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
2004 | 12 | 5 | 322.6122 | 5 | 317.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
2004 | 12 | 6 | 246.8571 | 5 | 241.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2004 | 12 | 7 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2004 | 12 | 8 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2004 | 12 | 9 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2004 | 12 | 10 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2004 | 12 | 11 | 223.3469 | 5 | 218.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2004 | 12 | 12 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2004 | 12 | 13 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2004 | 12 | 14 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2004 | 12 | 15 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2004 | 12 | 16 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2004 | 12 | 17 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2004 | 12 | 18 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2004 | 12 | 19 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2004 | 12 | 20 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2004 | 12 | 21 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2004 | 12 | 22 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2004 | 12 | 23 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2004 | 12 | 24 | 821.551 | 5 | 816.551 | 28.3569 | 139.3858 | 0.77441 | 27.5825 | 89.27% | 290.6573 | 273.2179 | 6557.2289
2004 | 12 | 25 | 493.7143 | 5 | 488.7143 | 29.0126 | 139.3858 | 0.77441 | 28.2382 | 89.27% | 297.5666 | 279.7126 | 6713.1032
2004 | 12 | 26 | 308.2449 | 5 | 303.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2004 | 12 | 27 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2004 | 12 | 28 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2004 | 12 | 29 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2004 | 12 | 30 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2004 | 12 | 31 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2005 | 1 | 1 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2005 | 1 | 2 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2005 | 1 | 3 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2005 | 1 | 4 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2005 | 1 | 5 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2005 | 1 | 6 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2005 | 1 | 7 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2005 | 1 | 8 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2005 | 1 | 9 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2005 | 1 | 10 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2005 | 1 | 11 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2005 | 1 | 12 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2005 | 1 | 13 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2005 | 1 | 14 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2005 | 1 | 15 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2005 | 1 | 16 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2005 | 1 | 17 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2005 | 1 | 18 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2005 | 1 | 19 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2005 | 1 | 20 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2005 | 1 | 21 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2005 | 1 | 22 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2005 | 1 | 23 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2005 | 1 | 24 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2005 | 1 | 25 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2005 | 1 | 26 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2005 | 1 | 27 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2005 | 1 | 28 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2005 | 1 | 29 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2005 | 1 | 30 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2005 | 1 | 31 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2005 | 2 | 1 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2005 | 2 | 2 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2005 | 2 | 3 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2005 | 2 | 4 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2005 | 2 | 5 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2005 | 2 | 6 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2005 | 2 | 7 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2005 | 2 | 8 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2005 | 2 | 9 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2005 | 2 | 10 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2005 | 2 | 11 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2005 | 2 | 12 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2005 | 2 | 13 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2005 | 2 | 14 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2005 | 2 | 15 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2005 | 2 | 16 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2005 | 2 | 17 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
2005 | 2 | 18 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2005 | 2 | 19 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2005 | 2 | 20 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2005 | 2 | 21 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2005 | 2 | 22 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2005 | 2 | 23 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2005 | 2 | 24 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2005 | 2 | 25 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2005 | 2 | 26 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2005 | 2 | 27 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2005 | 2 | 28 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2005 | 3 | 1 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2005 | 3 | 2 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2005 | 3 | 3 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2005 | 3 | 4 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2005 | 3 | 5 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2005 | 3 | 6 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2005 | 3 | 7 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2005 | 3 | 8 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2005 | 3 | 9 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2005 | 3 | 10 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2005 | 3 | 11 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2005 | 3 | 12 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2005 | 3 | 13 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2005 | 3 | 14 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2005 | 3 | 15 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2005 | 3 | 16 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2005 | 3 | 17 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2005 | 3 | 18 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2005 | 3 | 19 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2005 | 3 | 20 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2005 | 3 | 21 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2005 | 3 | 22 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2005 | 3 | 23 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2005 | 3 | 24 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2005 | 3 | 25 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2005 | 3 | 26 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
2005 | 3 | 27 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2005 | 3 | 28 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2005 | 3 | 29 | 411.4286 | 25 | 386.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
2005 | 3 | 30 | 583.8367 | 25 | 558.8367 | 28.8323 | 139.3858 | 0.77441 | 28.0579 | 89.27% | 295.6673 | 277.9272 | 6670.2533
2005 | 3 | 31 | 675.2653 | 25 | 650.2653 | 28.6495 | 139.3858 | 0.77441 | 27.8751 | 89.27% | 293.7404 | 276.1159 | 6626.7823
2005 | 4 | 1 | 706.6122 | 25 | 681.6122 | 28.5868 | 139.3858 | 0.77441 | 27.8124 | 89.27% | 293.0797 | 275.4949 | 6611.878
2005 | 4 | 2 | 720.9796 | 25 | 695.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
2005 | 4 | 3 | 3657.1429 | 25 | 3632.1429 | 22.6857 | 0 | 0 | 22.6857 | 0% | 0 | 0 | 0
2005 | 4 | 4 | 3461.2245 | 25 | 3436.2245 | 23.0776 | 0 | 0 | 23.0776 | 0% | 0 | 0 | 0
2005 | 4 | 5 | 1658.7755 | 25 | 1633.7755 | 26.6824 | 139.3858 | 0.77441 | 25.908 | 89.27% | 273.0124 | 256.6316 | 6159.1594
2005 | 4 | 6 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
2005 | 4 | 7 | 1502.0408 | 25 | 1477.0408 | 26.9959 | 139.3858 | 0.77441 | 26.2215 | 89.27% | 276.3156 | 259.7367 | 6233.681
2005 | 4 | 8 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
2005 | 4 | 9 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
2005 | 4 | 10 | 1102.3673 | 25 | 1077.3673 | 27.7953 | 139.3858 | 0.77441 | 27.0209 | 89.27% | 284.739 | 267.6546 | 6423.711
2005 | 4 | 11 | 1018.7755 | 25 | 993.7755 | 27.9624 | 139.3858 | 0.77441 | 27.188 | 89.27% | 286.5007 | 269.3107 | 6463.4559
2005 | 4 | 12 | 751.0204 | 25 | 726.0204 | 28.498 | 139.3858 | 0.77441 | 27.7235 | 89.27% | 292.1438 | 274.6151 | 6590.7636
2005 | 4 | 13 | 569.4694 | 25 | 544.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
2005 | 4 | 14 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
2005 | 4 | 15 | 510.6939 | 25 | 485.6939 | 28.9786 | 139.3858 | 0.77441 | 28.2042 | 89.27% | 297.2088 | 279.3763 | 6705.03
2005 | 4 | 16 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
2005 | 4 | 17 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
2005 | 4 | 18 | 502.8571 | 25 | 477.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
2005 | 4 | 19 | 453.2245 | 25 | 428.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
2005 | 4 | 20 | 425.7959 | 25 | 400.7959 | 29.1484 | 139.3858 | 0.77441 | 28.374 | 89.27% | 298.998 | 281.0582 | 6745.3959
2005 | 4 | 21 | 815.0204 | 25 | 790.0204 | 28.37 | 139.3858 | 0.77441 | 27.5955 | 89.27% | 290.7949 | 273.3472 | 6560.3339
2005 | 4 | 22 | 556.4082 | 25 | 531.4082 | 28.8872 | 139.3858 | 0.77441 | 28.1128 | 89.27% | 296.2453 | 278.4706 | 6683.2945
2005 | 4 | 23 | 457.1429 | 25 | 432.1429 | 29.0857 | 139.3858 | 0.77441 | 28.3113 | 89.27% | 298.3374 | 280.4371 | 6730.4915
2005 | 4 | 24 | 1071.0204 | 25 | 1046.0204 | 27.858 | 139.3858 | 0.77441 | 27.0835 | 89.27% | 285.3996 | 268.2756 | 6438.6154
2005 | 4 | 25 | 1776.3265 | 25 | 1751.3265 | 26.4473 | 139.3858 | 0.77441 | 25.6729 | 89.27% | 270.5349 | 254.3028 | 6103.2683
2005 | 4 | 26 | 1017.4694 | 25 | 992.4694 | 27.9651 | 139.3858 | 0.77441 | 27.1907 | 89.27% | 286.5282 | 269.3365 | 6464.0769
2005 | 4 | 27 | 739.2653 | 25 | 714.2653 | 28.5215 | 139.3858 | 0.77441 | 27.7471 | 89.27% | 292.3915 | 274.848 | 6596.3527
2005 | 4 | 28 | 2272.6531 | 25 | 2247.6531 | 25.4547 | 139.3858 | 0.77441 | 24.6803 | 89.27% | 260.0746 | 244.4701 | 5867.2833
2005 | 4 | 29 | 1737.1429 | 25 | 1712.1429 | 26.5257 | 139.3858 | 0.77441 | 25.7513 | 89.27% | 271.3608 | 255.0791 | 6121.8986
2005 | 4 | 30 | 982.2041 | 25 | 957.2041 | 28.0356 | 139.3858 | 0.77441 | 27.2612 | 89.27% | 287.2715 | 270.0352 | 6480.8443
2005 | 5 | 1 | 1060.5714 | 25 | 1035.5714 | 27.8789 | 139.3858 | 0.77441 | 27.1044 | 89.27% | 285.6198 | 268.4826 | 6443.5835
2005 | 5 | 2 | 784.9796 | 25 | 759.9796 | 28.43 | 139.3858 | 0.77441 | 27.6556 | 89.27% | 291.4281 | 273.9424 | 6574.6172
2005 | 5 | 3 | 566.8571 | 25 | 541.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
2005 | 5 | 4 | 453.2245 | 25 | 428.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
2005 | 5 | 5 | 378.7755 | 25 | 353.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
2005 | 5 | 6 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2005 | 5 | 7 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2005 | 5 | 8 | 411.4286 | 25 | 386.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
2005 | 5 | 9 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
2005 | 5 | 10 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2005 | 5 | 11 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2005 | 5 | 12 | 256 | 25 | 231 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2005 | 5 | 13 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2005 | 5 | 14 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2005 | 5 | 15 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2005 | 5 | 16 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
2005 | 5 | 17 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2005 | 5 | 18 | 253.3878 | 25 | 228.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2005 | 5 | 19 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2005 | 5 | 20 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2005 | 5 | 21 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2005 | 5 | 22 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
2005 | 5 | 23 | 761.4694 | 25 | 736.4694 | 28.4771 | 139.3858 | 0.77441 | 27.7027 | 89.27% | 291.9236 | 274.4081 | 6585.7955
2005 | 5 | 24 | 1554.2857 | 25 | 1529.2857 | 26.8914 | 139.3858 | 0.77441 | 26.117 | 89.27% | 275.2146 | 258.7017 | 6208.8405
2005 | 5 | 25 | 956.0816 | 25 | 931.0816 | 28.0878 | 139.3858 | 0.77441 | 27.3134 | 89.27% | 287.822 | 270.5527 | 6493.2645
2005 | 5 | 26 | 974.3673 | 25 | 949.3673 | 28.0513 | 139.3858 | 0.77441 | 27.2769 | 89.27% | 287.4366 | 270.1904 | 6484.5703
2005 | 5 | 27 | 1319.1837 | 25 | 1294.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
2005 | 5 | 28 | 867.2653 | 25 | 842.2653 | 28.2655 | 139.3858 | 0.77441 | 27.4911 | 89.27% | 289.6939 | 272.3122 | 6535.4934
2005 | 5 | 29 | 617.7959 | 25 | 592.7959 | 28.7644 | 139.3858 | 0.77441 | 27.99 | 89.27% | 294.9515 | 277.2545 | 6654.1069
2005 | 5 | 30 | 493.7143 | 25 | 468.7143 | 29.0126 | 139.3858 | 0.77441 | 28.2382 | 89.27% | 297.5666 | 279.7126 | 6713.1032
2005 | 5 | 31 | 543.3469 | 25 | 518.3469 | 28.9133 | 139.3858 | 0.77441 | 28.1389 | 89.27% | 296.5206 | 278.7294 | 6689.5047
2005 | 6 | 1 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
2005 | 6 | 2 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
2005 | 6 | 3 | 275.5918 | 25 | 250.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
2005 | 6 | 4 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2005 | 6 | 5 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2005 | 6 | 6 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2005 | 6 | 7 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2005 | 6 | 8 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
2005 | 6 | 9 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2005 | 6 | 10 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2005 | 6 | 11 | 180.2449 | 25 | 155.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2005 | 6 | 12 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2005 | 6 | 13 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2005 | 6 | 14 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
2005 | 6 | 15 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
2005 | 6 | 16 | 943.0204 | 25 | 918.0204 | 28.114 | 139.3858 | 0.77441 | 27.3395 | 89.27% | 288.0973 | 270.8114 | 6499.4746
2005 | 6 | 17 | 954.7755 | 25 | 929.7755 | 28.0904 | 139.3858 | 0.77441 | 27.316 | 89.27% | 287.8495 | 270.5786 | 6493.8855
2005 | 6 | 18 | 862.0408 | 25 | 837.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
2005 | 6 | 19 | 613.8776 | 25 | 588.8776 | 28.7722 | 139.3858 | 0.77441 | 27.9978 | 89.27% | 295.0341 | 277.3321 | 6655.97
2005 | 6 | 20 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
2005 | 6 | 21 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
2005 | 6 | 22 | 266.449 | 25 | 241.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
2005 | 6 | 23 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2005 | 6 | 24 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2005 | 6 | 25 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2005 | 6 | 26 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2005 | 6 | 27 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2005 | 6 | 28 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2005 | 6 | 29 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2005 | 6 | 30 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2005 | 7 | 1 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2005 | 7 | 2 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2005 | 7 | 3 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2005 | 7 | 4 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2005 | 7 | 5 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2005 | 7 | 6 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2005 | 7 | 7 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2005 | 7 | 8 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2005 | 7 | 9 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2005 | 7 | 10 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2005 | 7 | 11 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2005 | 7 | 12 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2005 | 7 | 13 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2005 | 7 | 14 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2005 | 7 | 15 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2005 | 7 | 16 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2005 | 7 | 17 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2005 | 7 | 18 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2005 | 7 | 19 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2005 | 7 | 20 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2005 | 7 | 21 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2005 | 7 | 22 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2005 | 7 | 23 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2005 | 7 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2005 | 7 | 25 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2005 | 7 | 26 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2005 | 7 | 27 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2005 | 7 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2005 | 7 | 29 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2005 | 7 | 30 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2005 | 7 | 31 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
2005 | 8 | 1 | 11.102 | 5 | 6.102 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
2005 | 8 | 2 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
2005 | 8 | 3 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
2005 | 8 | 4 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
2005 | 8 | 5 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
2005 | 8 | 6 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2005 | 8 | 7 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
2005 | 8 | 8 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
2005 | 8 | 9 | 9.1429 | 5 | 4.1429 | 29.9817 | 0 | 0 | 29.9817 | 0% | 0 | 0 | 0
2005 | 8 | 10 | 8.3592 | 5 | 3.3592 | 29.9833 | 0 | 0 | 29.9833 | 0% | 0 | 0 | 0
2005 | 8 | 11 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
2005 | 8 | 12 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
2005 | 8 | 13 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
2005 | 8 | 14 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
2005 | 8 | 15 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
2005 | 8 | 16 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2005 | 8 | 17 | 9.5347 | 5 | 4.5347 | 29.9809 | 0 | 0 | 29.9809 | 0% | 0 | 0 | 0
2005 | 8 | 18 | 7.0531 | 5 | 2.0531 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
2005 | 8 | 19 | 6.2694 | 5 | 1.2694 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
2005 | 8 | 20 | 6.0082 | 5 | 1.0082 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
2005 | 8 | 21 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
2005 | 8 | 22 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2005 | 8 | 23 | 11.8857 | 5 | 6.8857 | 29.9762 | 6.8857 | 0.0018899 | 29.9743 | 40.05% | 7.0004 | 6.5804 | 157.9297
2005 | 8 | 24 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
2005 | 8 | 25 | 7.7061 | 5 | 2.7061 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
2005 | 8 | 26 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
2005 | 8 | 27 | 5.8776 | 5 | 0.87755 | 29.9882 | 0 | 0 | 29.9882 | 0% | 0 | 0 | 0
2005 | 8 | 28 | 5.3551 | 5 | 0.3551 | 29.9893 | 0 | 0 | 29.9893 | 0% | 0 | 0 | 0
2005 | 8 | 29 | 6.4 | 5 | 1.4 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
2005 | 8 | 30 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2005 | 8 | 31 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2005 | 9 | 1 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2005 | 9 | 2 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
2005 | 9 | 3 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2005 | 9 | 4 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2005 | 9 | 5 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2005 | 9 | 6 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2005 | 9 | 7 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2005 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2005 | 9 | 9 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2005 | 9 | 10 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
2005 | 9 | 11 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
2005 | 9 | 12 | 9.6653 | 15 | 0 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
2005 | 9 | 13 | 8.4898 | 15 | 0 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
2005 | 9 | 14 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2005 | 9 | 15 | 10.449 | 15 | 0 | 29.9791 | 0 | 0 | 29.9791 | 0% | 0 | 0 | 0
2005 | 9 | 16 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2005 | 9 | 17 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2005 | 9 | 18 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2005 | 9 | 19 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2005 | 9 | 20 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2005 | 9 | 21 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2005 | 9 | 22 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2005 | 9 | 23 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2005 | 9 | 24 | 10.1878 | 15 | 0 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
2005 | 9 | 25 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2005 | 9 | 26 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2005 | 9 | 27 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2005 | 9 | 28 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2005 | 9 | 29 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2005 | 9 | 30 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2005 | 10 | 1 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2005 | 10 | 2 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2005 | 10 | 3 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2005 | 10 | 4 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2005 | 10 | 5 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2005 | 10 | 6 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2005 | 10 | 7 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2005 | 10 | 8 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2005 | 10 | 9 | 1030.5306 | 15 | 1015.5306 | 27.9389 | 139.3858 | 0.77441 | 27.1645 | 89.27% | 286.253 | 269.0778 | 6457.8668
2005 | 10 | 10 | 835.9184 | 15 | 820.9184 | 28.3282 | 139.3858 | 0.77441 | 27.5538 | 89.27% | 290.3545 | 272.9332 | 6550.3977
2005 | 10 | 11 | 402.2857 | 15 | 387.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
2005 | 10 | 12 | 253.3878 | 15 | 238.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2005 | 10 | 13 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2005 | 10 | 14 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2005 | 10 | 15 | 803.2653 | 15 | 788.2653 | 28.3935 | 139.3858 | 0.77441 | 27.6191 | 89.27% | 291.0427 | 273.5801 | 6565.9231
2005 | 10 | 16 | 1789.3878 | 15 | 1774.3878 | 26.4212 | 139.3858 | 0.77441 | 25.6468 | 89.27% | 270.2597 | 254.0441 | 6097.0581
2005 | 10 | 17 | 865.9592 | 15 | 850.9592 | 28.2681 | 139.3858 | 0.77441 | 27.4937 | 89.27% | 289.7214 | 272.3381 | 6536.1144
2005 | 10 | 18 | 492.4082 | 15 | 477.4082 | 29.0152 | 139.3858 | 0.77441 | 28.2408 | 89.27% | 297.5942 | 279.7385 | 6713.7242
2005 | 10 | 19 | 344.8163 | 15 | 329.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
2005 | 10 | 20 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2005 | 10 | 21 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2005 | 10 | 22 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2005 | 10 | 23 | 378.7755 | 15 | 363.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
2005 | 10 | 24 | 544.6531 | 15 | 529.6531 | 28.9107 | 139.3858 | 0.77441 | 28.1363 | 89.27% | 296.4931 | 278.7035 | 6688.8837
2005 | 10 | 25 | 778.449 | 15 | 763.449 | 28.4431 | 139.3858 | 0.77441 | 27.6687 | 89.27% | 291.5657 | 274.0718 | 6577.7223
2005 | 10 | 26 | 2155.102 | 15 | 2140.102 | 25.6898 | 139.3858 | 0.77441 | 24.9154 | 89.27% | 262.5521 | 246.7989 | 5923.1744
2005 | 10 | 27 | 1281.3061 | 15 | 1266.3061 | 27.4374 | 139.3858 | 0.77441 | 26.663 | 89.27% | 280.9677 | 264.1097 | 6338.6322
2005 | 10 | 28 | 717.0612 | 15 | 702.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
2005 | 10 | 29 | 488.4898 | 15 | 473.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
2005 | 10 | 30 | 382.6939 | 15 | 367.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
2005 | 10 | 31 | 327.8367 | 15 | 312.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
2005 | 11 | 1 | 288.6531 | 15 | 273.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
2005 | 11 | 2 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2005 | 11 | 3 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2005 | 11 | 4 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2005 | 11 | 5 | 180.2449 | 15 | 165.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2005 | 11 | 6 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2005 | 11 | 7 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2005 | 11 | 8 | 254.6939 | 15 | 239.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2005 | 11 | 9 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2005 | 11 | 10 | 498.9388 | 15 | 483.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
2005 | 11 | 11 | 491.102 | 15 | 476.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
2005 | 11 | 12 | 344.8163 | 15 | 329.8163 | 29.3104 | 139.3858 | 0.77441 | 28.536 | 89.27% | 300.7047 | 282.6624 | 6783.8987
2005 | 11 | 13 | 282.1224 | 15 | 267.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
2005 | 11 | 14 | 261.2245 | 15 | 246.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
2005 | 11 | 15 | 253.3878 | 15 | 238.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2005 | 11 | 16 | 459.7551 | 15 | 444.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
2005 | 11 | 17 | 1216 | 15 | 1201 | 27.568 | 139.3858 | 0.77441 | 26.7936 | 89.27% | 282.3441 | 265.4035 | 6369.6829
2005 | 11 | 18 | 786.2857 | 15 | 771.2857 | 28.4274 | 139.3858 | 0.77441 | 27.653 | 89.27% | 291.4005 | 273.9165 | 6573.9962
2005 | 11 | 19 | 475.4286 | 15 | 460.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
2005 | 11 | 20 | 364.4082 | 15 | 349.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
2005 | 11 | 21 | 313.4694 | 15 | 298.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2005 | 11 | 22 | 468.898 | 15 | 453.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
2005 | 11 | 23 | 1195.102 | 15 | 1180.102 | 27.6098 | 139.3858 | 0.77441 | 26.8354 | 89.27% | 282.7845 | 265.8175 | 6379.6191
2005 | 11 | 24 | 626.9388 | 15 | 611.9388 | 28.7461 | 139.3858 | 0.77441 | 27.9717 | 89.27% | 294.7589 | 277.0733 | 6649.7598
2005 | 11 | 25 | 440.1633 | 15 | 425.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
2005 | 11 | 26 | 336.9796 | 15 | 321.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2005 | 11 | 27 | 295.1837 | 15 | 280.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
2005 | 11 | 28 | 276.898 | 15 | 261.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2005 | 11 | 29 | 335.6735 | 15 | 320.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
2005 | 11 | 30 | 800.6531 | 15 | 785.6531 | 28.3987 | 139.3858 | 0.77441 | 27.6243 | 89.27% | 291.0977 | 273.6319 | 6567.1651
2005 | 12 | 1 | 1106.2857 | 5 | 1101.2857 | 27.7874 | 139.3858 | 0.77441 | 27.013 | 89.27% | 284.6564 | 267.577 | 6421.848
2005 | 12 | 2 | 650.449 | 5 | 645.449 | 28.6991 | 139.3858 | 0.77441 | 27.9247 | 89.27% | 294.2634 | 276.6076 | 6638.5816
2005 | 12 | 3 | 462.3673 | 5 | 457.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
2005 | 12 | 4 | 356.5714 | 5 | 351.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
2005 | 12 | 5 | 303.0204 | 5 | 298.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
2005 | 12 | 6 | 262.5306 | 5 | 257.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2005 | 12 | 7 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2005 | 12 | 8 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2005 | 12 | 9 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2005 | 12 | 10 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2005 | 12 | 11 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2005 | 12 | 12 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2005 | 12 | 13 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2005 | 12 | 14 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2005 | 12 | 15 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2005 | 12 | 16 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2005 | 12 | 17 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2005 | 12 | 18 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2005 | 12 | 19 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2005 | 12 | 20 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2005 | 12 | 21 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2005 | 12 | 22 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2005 | 12 | 23 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2005 | 12 | 24 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2005 | 12 | 25 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2005 | 12 | 26 | 303.0204 | 5 | 298.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
2005 | 12 | 27 | 381.3878 | 5 | 376.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
2005 | 12 | 28 | 278.2041 | 5 | 273.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
2005 | 12 | 29 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2005 | 12 | 30 | 560.3265 | 5 | 555.3265 | 28.8793 | 139.3858 | 0.77441 | 28.1049 | 89.27% | 296.1627 | 278.393 | 6681.4315
2005 | 12 | 31 | 408.8163 | 5 | 403.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
2006 | 1 | 1 | 296.4898 | 5 | 291.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2006 | 1 | 2 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2006 | 1 | 3 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2006 | 1 | 4 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2006 | 1 | 5 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
2006 | 1 | 6 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2006 | 1 | 7 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2006 | 1 | 8 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2006 | 1 | 9 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2006 | 1 | 10 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2006 | 1 | 11 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2006 | 1 | 12 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2006 | 1 | 13 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2006 | 1 | 14 | 579.9184 | 5 | 574.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
2006 | 1 | 15 | 1306.1224 | 5 | 1301.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
2006 | 1 | 16 | 542.0408 | 5 | 537.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
2006 | 1 | 17 | 374.8571 | 5 | 369.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
2006 | 1 | 18 | 595.5918 | 5 | 590.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
2006 | 1 | 19 | 1567.3469 | 5 | 1562.3469 | 26.8653 | 139.3858 | 0.77441 | 26.0909 | 89.27% | 274.9393 | 258.4429 | 6202.6304
2006 | 1 | 20 | 737.9592 | 5 | 732.9592 | 28.5241 | 139.3858 | 0.77441 | 27.7497 | 89.27% | 292.419 | 274.8739 | 6596.9737
2006 | 1 | 21 | 505.4694 | 5 | 500.4694 | 28.9891 | 139.3858 | 0.77441 | 28.2147 | 89.27% | 297.3189 | 279.4798 | 6707.5141
2006 | 1 | 22 | 425.7959 | 5 | 420.7959 | 29.1484 | 139.3858 | 0.77441 | 28.374 | 89.27% | 298.998 | 281.0582 | 6745.3959
2006 | 1 | 23 | 327.8367 | 5 | 322.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
2006 | 1 | 24 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
2006 | 1 | 25 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
2006 | 1 | 26 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2006 | 1 | 27 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2006 | 1 | 28 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2006 | 1 | 29 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2006 | 1 | 30 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2006 | 1 | 31 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2006 | 2 | 1 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2006 | 2 | 2 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2006 | 2 | 3 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2006 | 2 | 4 | 518.5306 | 5 | 513.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
2006 | 2 | 5 | 1043.5918 | 5 | 1038.5918 | 27.9128 | 139.3858 | 0.77441 | 27.1384 | 89.27% | 285.9777 | 268.819 | 6451.6566
2006 | 2 | 6 | 1034.449 | 5 | 1029.449 | 27.9311 | 139.3858 | 0.77441 | 27.1567 | 89.27% | 286.1704 | 269.0002 | 6456.0037
2006 | 2 | 7 | 542.0408 | 5 | 537.0408 | 28.9159 | 139.3858 | 0.77441 | 28.1415 | 89.27% | 296.5481 | 278.7552 | 6690.1257
2006 | 2 | 8 | 367.0204 | 5 | 362.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
2006 | 2 | 9 | 269.0612 | 5 | 264.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
2006 | 2 | 10 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2006 | 2 | 11 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2006 | 2 | 12 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2006 | 2 | 13 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2006 | 2 | 14 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2006 | 2 | 15 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2006 | 2 | 16 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2006 | 2 | 17 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2006 | 2 | 18 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2006 | 2 | 19 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2006 | 2 | 20 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2006 | 2 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2006 | 2 | 22 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2006 | 2 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2006 | 2 | 24 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2006 | 2 | 25 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2006 | 2 | 26 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2006 | 2 | 27 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2006 | 2 | 28 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2006 | 3 | 1 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2006 | 3 | 2 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2006 | 3 | 3 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2006 | 3 | 4 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2006 | 3 | 5 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2006 | 3 | 6 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2006 | 3 | 7 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2006 | 3 | 8 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2006 | 3 | 9 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2006 | 3 | 10 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2006 | 3 | 11 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2006 | 3 | 12 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
2006 | 3 | 13 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
2006 | 3 | 14 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
2006 | 3 | 15 | 402.2857 | 25 | 377.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
2006 | 3 | 16 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2006 | 3 | 17 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2006 | 3 | 18 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2006 | 3 | 19 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2006 | 3 | 20 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2006 | 3 | 21 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2006 | 3 | 22 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2006 | 3 | 23 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2006 | 3 | 24 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2006 | 3 | 25 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2006 | 3 | 26 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2006 | 3 | 27 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
2006 | 3 | 28 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
2006 | 3 | 29 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2006 | 3 | 30 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2006 | 3 | 31 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2006 | 4 | 1 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2006 | 4 | 2 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2006 | 4 | 3 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2006 | 4 | 4 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2006 | 4 | 5 | 402.2857 | 25 | 377.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
2006 | 4 | 6 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
2006 | 4 | 7 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
2006 | 4 | 8 | 320 | 25 | 295 | 29.36 | 139.3858 | 0.77441 | 28.5856 | 89.27% | 301.2277 | 283.1541 | 6795.6979
2006 | 4 | 9 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
2006 | 4 | 10 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2006 | 4 | 11 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2006 | 4 | 12 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2006 | 4 | 13 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2006 | 4 | 14 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2006 | 4 | 15 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2006 | 4 | 16 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2006 | 4 | 17 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2006 | 4 | 18 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2006 | 4 | 19 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2006 | 4 | 20 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2006 | 4 | 21 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2006 | 4 | 22 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2006 | 4 | 23 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2006 | 4 | 24 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2006 | 4 | 25 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2006 | 4 | 26 | 133.2245 | 25 | 108.2245 | 29.7336 | 108.2245 | 0.46686 | 29.2667 | 91.77% | 246.1635 | 231.3936 | 5553.4476
2006 | 4 | 27 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2006 | 4 | 28 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2006 | 4 | 29 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2006 | 4 | 30 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2006 | 5 | 1 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2006 | 5 | 2 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
2006 | 5 | 3 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
2006 | 5 | 4 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2006 | 5 | 5 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2006 | 5 | 6 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2006 | 5 | 7 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
2006 | 5 | 8 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2006 | 5 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2006 | 5 | 10 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2006 | 5 | 11 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
2006 | 5 | 12 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
2006 | 5 | 13 | 1606.5306 | 25 | 1581.5306 | 26.7869 | 139.3858 | 0.77441 | 26.0125 | 89.27% | 274.1135 | 257.6667 | 6184
2006 | 5 | 14 | 1099.7551 | 25 | 1074.7551 | 27.8005 | 139.3858 | 0.77441 | 27.0261 | 89.27% | 284.794 | 267.7064 | 6424.9531
2006 | 5 | 15 | 573.3878 | 25 | 548.3878 | 28.8532 | 139.3858 | 0.77441 | 28.0788 | 89.27% | 295.8875 | 278.1342 | 6675.2214
2006 | 5 | 16 | 715.7551 | 25 | 690.7551 | 28.5685 | 139.3858 | 0.77441 | 27.7941 | 89.27% | 292.887 | 275.3138 | 6607.5309
2006 | 5 | 17 | 983.5102 | 25 | 958.5102 | 28.033 | 139.3858 | 0.77441 | 27.2586 | 89.27% | 287.2439 | 270.0093 | 6480.2232
2006 | 5 | 18 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
2006 | 5 | 19 | 579.9184 | 25 | 554.9184 | 28.8402 | 139.3858 | 0.77441 | 28.0658 | 89.27% | 295.7498 | 278.0048 | 6672.1163
2006 | 5 | 20 | 765.3878 | 25 | 740.3878 | 28.4692 | 139.3858 | 0.77441 | 27.6948 | 89.27% | 291.841 | 274.3305 | 6583.9324
2006 | 5 | 21 | 500.2449 | 25 | 475.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
2006 | 5 | 22 | 386.6122 | 25 | 361.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
2006 | 5 | 23 | 308.2449 | 25 | 283.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2006 | 5 | 24 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2006 | 5 | 25 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2006 | 5 | 26 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2006 | 5 | 27 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2006 | 5 | 28 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2006 | 5 | 29 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2006 | 5 | 30 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2006 | 5 | 31 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2006 | 6 | 1 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
2006 | 6 | 2 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2006 | 6 | 3 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2006 | 6 | 4 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2006 | 6 | 5 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2006 | 6 | 6 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2006 | 6 | 7 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2006 | 6 | 8 | 504.1633 | 25 | 479.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
2006 | 6 | 9 | 681.7959 | 25 | 656.7959 | 28.6364 | 139.3858 | 0.77441 | 27.862 | 89.27% | 293.6027 | 275.9866 | 6623.6773
2006 | 6 | 10 | 991.3469 | 25 | 966.3469 | 28.0173 | 139.3858 | 0.77441 | 27.2429 | 89.27% | 287.0788 | 269.854 | 6476.4972
2006 | 6 | 11 | 1138.9388 | 25 | 1113.9388 | 27.7221 | 139.3858 | 0.77441 | 26.9477 | 89.27% | 283.9682 | 266.9301 | 6406.3227
2006 | 6 | 12 | 587.7551 | 25 | 562.7551 | 28.8245 | 139.3858 | 0.77441 | 28.0501 | 89.27% | 295.5847 | 277.8496 | 6668.3902
2006 | 6 | 13 | 391.8367 | 25 | 366.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
2006 | 6 | 14 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
2006 | 6 | 15 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
2006 | 6 | 16 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2006 | 6 | 17 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
2006 | 6 | 18 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
2006 | 6 | 19 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2006 | 6 | 20 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
2006 | 6 | 21 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2006 | 6 | 22 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
2006 | 6 | 23 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2006 | 6 | 24 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2006 | 6 | 25 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2006 | 6 | 26 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2006 | 6 | 27 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
2006 | 6 | 28 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
2006 | 6 | 29 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
2006 | 6 | 30 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
2006 | 7 | 1 | 248.1633 | 5 | 243.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2006 | 7 | 2 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2006 | 7 | 3 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2006 | 7 | 4 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2006 | 7 | 5 | 377.4694 | 5 | 372.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
2006 | 7 | 6 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2006 | 7 | 7 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2006 | 7 | 8 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2006 | 7 | 9 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2006 | 7 | 10 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2006 | 7 | 11 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2006 | 7 | 12 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2006 | 7 | 13 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2006 | 7 | 14 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2006 | 7 | 15 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2006 | 7 | 16 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2006 | 7 | 17 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2006 | 7 | 18 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2006 | 7 | 19 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2006 | 7 | 20 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2006 | 7 | 21 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2006 | 7 | 22 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2006 | 7 | 23 | 451.9184 | 5 | 446.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
2006 | 7 | 24 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2006 | 7 | 25 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
2006 | 7 | 26 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2006 | 7 | 27 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2006 | 7 | 28 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2006 | 7 | 29 | 583.8367 | 5 | 578.8367 | 28.8323 | 139.3858 | 0.77441 | 28.0579 | 89.27% | 295.6673 | 277.9272 | 6670.2533
2006 | 7 | 30 | 271.6735 | 5 | 266.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
2006 | 7 | 31 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2006 | 8 | 1 | 223.3469 | 5 | 218.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2006 | 8 | 2 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2006 | 8 | 3 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2006 | 8 | 4 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2006 | 8 | 5 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2006 | 8 | 6 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2006 | 8 | 7 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2006 | 8 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2006 | 8 | 9 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2006 | 8 | 10 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2006 | 8 | 11 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2006 | 8 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2006 | 8 | 13 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2006 | 8 | 14 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2006 | 8 | 15 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2006 | 8 | 16 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2006 | 8 | 17 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2006 | 8 | 18 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2006 | 8 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2006 | 8 | 20 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2006 | 8 | 21 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2006 | 8 | 22 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2006 | 8 | 23 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2006 | 8 | 24 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2006 | 8 | 25 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2006 | 8 | 26 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2006 | 8 | 27 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2006 | 8 | 28 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2006 | 8 | 29 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2006 | 8 | 30 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2006 | 8 | 31 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2006 | 9 | 1 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2006 | 9 | 2 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2006 | 9 | 3 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2006 | 9 | 4 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2006 | 9 | 5 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2006 | 9 | 6 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
2006 | 9 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2006 | 9 | 8 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2006 | 9 | 9 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2006 | 9 | 10 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2006 | 9 | 11 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2006 | 9 | 12 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2006 | 9 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2006 | 9 | 14 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2006 | 9 | 15 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2006 | 9 | 16 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2006 | 9 | 17 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2006 | 9 | 18 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2006 | 9 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2006 | 9 | 20 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2006 | 9 | 21 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2006 | 9 | 22 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2006 | 9 | 23 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2006 | 9 | 24 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2006 | 9 | 25 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2006 | 9 | 26 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2006 | 9 | 27 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2006 | 9 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2006 | 9 | 29 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2006 | 9 | 30 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2006 | 10 | 1 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2006 | 10 | 2 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2006 | 10 | 3 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2006 | 10 | 4 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2006 | 10 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2006 | 10 | 6 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2006 | 10 | 7 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2006 | 10 | 8 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2006 | 10 | 9 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2006 | 10 | 10 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2006 | 10 | 11 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2006 | 10 | 12 | 346.1224 | 15 | 331.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2006 | 10 | 13 | 323.9184 | 15 | 308.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2006 | 10 | 14 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2006 | 10 | 15 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
2006 | 10 | 16 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
2006 | 10 | 17 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2006 | 10 | 18 | 239.0204 | 15 | 224.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
2006 | 10 | 19 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2006 | 10 | 20 | 270.3673 | 15 | 255.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
2006 | 10 | 21 | 1319.1837 | 15 | 1304.1837 | 27.3616 | 139.3858 | 0.77441 | 26.5872 | 89.27% | 280.1695 | 263.3593 | 6320.6229
2006 | 10 | 22 | 595.5918 | 15 | 580.5918 | 28.8088 | 139.3858 | 0.77441 | 28.0344 | 89.27% | 295.4195 | 277.6943 | 6664.6641
2006 | 10 | 23 | 487.1837 | 15 | 472.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
2006 | 10 | 24 | 555.102 | 15 | 540.102 | 28.8898 | 139.3858 | 0.77441 | 28.1154 | 89.27% | 296.2729 | 278.4965 | 6683.9156
2006 | 10 | 25 | 360.4898 | 15 | 345.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
2006 | 10 | 26 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
2006 | 10 | 27 | 223.3469 | 15 | 208.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2006 | 10 | 28 | 566.8571 | 15 | 551.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
2006 | 10 | 29 | 2546.9388 | 15 | 2531.9388 | 24.9061 | 0 | 0 | 24.9061 | 0% | 0 | 0 | 0
2006 | 10 | 30 | 995.2653 | 15 | 980.2653 | 28.0095 | 139.3858 | 0.77441 | 27.2351 | 89.27% | 286.9962 | 269.7764 | 6474.6341
2006 | 10 | 31 | 539.4286 | 15 | 524.4286 | 28.9211 | 139.3858 | 0.77441 | 28.1467 | 89.27% | 296.6032 | 278.807 | 6691.3677
2006 | 11 | 1 | 395.7551 | 15 | 380.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
2006 | 11 | 2 | 391.8367 | 15 | 376.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
2006 | 11 | 3 | 382.6939 | 15 | 367.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
2006 | 11 | 4 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2006 | 11 | 5 | 257.3061 | 15 | 242.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2006 | 11 | 6 | 233.7959 | 15 | 218.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2006 | 11 | 7 | 212.898 | 15 | 197.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2006 | 11 | 8 | 210.2857 | 15 | 195.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2006 | 11 | 9 | 786.2857 | 15 | 771.2857 | 28.4274 | 139.3858 | 0.77441 | 27.653 | 89.27% | 291.4005 | 273.9165 | 6573.9962
2006 | 11 | 10 | 606.0408 | 15 | 591.0408 | 28.7879 | 139.3858 | 0.77441 | 28.0135 | 89.27% | 295.1993 | 277.4873 | 6659.696
2006 | 11 | 11 | 391.8367 | 15 | 376.8367 | 29.2163 | 139.3858 | 0.77441 | 28.4419 | 89.27% | 299.7137 | 281.7309 | 6761.5422
2006 | 11 | 12 | 333.0612 | 15 | 318.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
2006 | 11 | 13 | 498.9388 | 15 | 483.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
2006 | 11 | 14 | 752.3265 | 15 | 737.3265 | 28.4953 | 139.3858 | 0.77441 | 27.7209 | 89.27% | 292.1162 | 274.5893 | 6590.1426
2006 | 11 | 15 | 871.1837 | 15 | 856.1837 | 28.2576 | 139.3858 | 0.77441 | 27.4832 | 89.27% | 289.6113 | 272.2346 | 6533.6304
2006 | 11 | 16 | 555.102 | 15 | 540.102 | 28.8898 | 139.3858 | 0.77441 | 28.1154 | 89.27% | 296.2729 | 278.4965 | 6683.9156
2006 | 11 | 17 | 1306.1224 | 15 | 1291.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
2006 | 11 | 18 | 1184.6531 | 15 | 1169.6531 | 27.6307 | 139.3858 | 0.77441 | 26.8563 | 89.27% | 283.0048 | 266.0245 | 6384.5872
2006 | 11 | 19 | 641.3061 | 15 | 626.3061 | 28.7174 | 139.3858 | 0.77441 | 27.943 | 89.27% | 294.4561 | 276.7887 | 6642.9287
2006 | 11 | 20 | 461.0612 | 15 | 446.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
2006 | 11 | 21 | 364.4082 | 15 | 349.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
2006 | 11 | 22 | 308.2449 | 15 | 293.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2006 | 11 | 23 | 275.5918 | 15 | 260.5918 | 29.4488 | 139.3858 | 0.77441 | 28.6744 | 89.27% | 302.1637 | 284.0338 | 6816.8124
2006 | 11 | 24 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2006 | 11 | 25 | 231.1837 | 15 | 216.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2006 | 11 | 26 | 214.2041 | 15 | 199.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
2006 | 11 | 27 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2006 | 11 | 28 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2006 | 11 | 29 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2006 | 11 | 30 | 203.7551 | 15 | 188.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2006 | 12 | 1 | 267.7551 | 5 | 262.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
2006 | 12 | 2 | 784.9796 | 5 | 779.9796 | 28.43 | 139.3858 | 0.77441 | 27.6556 | 89.27% | 291.4281 | 273.9424 | 6574.6172
2006 | 12 | 3 | 470.2041 | 5 | 465.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
2006 | 12 | 4 | 339.5918 | 5 | 334.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
2006 | 12 | 5 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2006 | 12 | 6 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2006 | 12 | 7 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2006 | 12 | 8 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2006 | 12 | 9 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2006 | 12 | 10 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2006 | 12 | 11 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2006 | 12 | 12 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2006 | 12 | 13 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2006 | 12 | 14 | 225.9592 | 5 | 220.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2006 | 12 | 15 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2006 | 12 | 16 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2006 | 12 | 17 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2006 | 12 | 18 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2006 | 12 | 19 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
2006 | 12 | 20 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
2006 | 12 | 21 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2006 | 12 | 22 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2006 | 12 | 23 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2006 | 12 | 24 | 407.5102 | 5 | 402.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
2006 | 12 | 25 | 288.6531 | 5 | 283.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
2006 | 12 | 26 | 258.6122 | 5 | 253.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2006 | 12 | 27 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2006 | 12 | 28 | 223.3469 | 5 | 218.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2006 | 12 | 29 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2006 | 12 | 30 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2006 | 12 | 31 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2007 | 1 | 1 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2007 | 1 | 2 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2007 | 1 | 3 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2007 | 1 | 4 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
2007 | 1 | 5 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2007 | 1 | 6 | 252.0816 | 5 | 247.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2007 | 1 | 7 | 322.6122 | 5 | 317.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
2007 | 1 | 8 | 293.8776 | 5 | 288.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
2007 | 1 | 9 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2007 | 1 | 10 | 270.3673 | 5 | 265.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
2007 | 1 | 11 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2007 | 1 | 12 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2007 | 1 | 13 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
2007 | 1 | 14 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2007 | 1 | 15 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2007 | 1 | 16 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2007 | 1 | 17 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2007 | 1 | 18 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2007 | 1 | 19 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2007 | 1 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2007 | 1 | 21 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2007 | 1 | 22 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2007 | 1 | 23 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2007 | 1 | 24 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2007 | 1 | 25 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2007 | 1 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2007 | 1 | 27 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2007 | 1 | 28 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2007 | 1 | 29 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2007 | 1 | 30 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2007 | 1 | 31 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2007 | 2 | 1 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2007 | 2 | 2 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2007 | 2 | 3 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2007 | 2 | 4 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2007 | 2 | 5 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2007 | 2 | 6 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2007 | 2 | 7 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2007 | 2 | 8 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2007 | 2 | 9 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2007 | 2 | 10 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2007 | 2 | 11 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2007 | 2 | 12 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2007 | 2 | 13 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2007 | 2 | 14 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2007 | 2 | 15 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2007 | 2 | 16 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2007 | 2 | 17 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2007 | 2 | 18 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2007 | 2 | 19 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2007 | 2 | 20 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2007 | 2 | 21 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2007 | 2 | 22 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2007 | 2 | 23 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2007 | 2 | 24 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2007 | 2 | 25 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2007 | 2 | 26 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2007 | 2 | 27 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2007 | 2 | 28 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2007 | 3 | 1 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2007 | 3 | 2 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
2007 | 3 | 3 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2007 | 3 | 4 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2007 | 3 | 5 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2007 | 3 | 6 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2007 | 3 | 7 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2007 | 3 | 8 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
2007 | 3 | 9 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
2007 | 3 | 10 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2007 | 3 | 11 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2007 | 3 | 12 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2007 | 3 | 13 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2007 | 3 | 14 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2007 | 3 | 15 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2007 | 3 | 16 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2007 | 3 | 17 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2007 | 3 | 18 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2007 | 3 | 19 | 154.1224 | 25 | 129.1224 | 29.6918 | 129.1224 | 0.66457 | 29.0272 | 90.74% | 288.0243 | 270.7429 | 6497.829
2007 | 3 | 20 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
2007 | 3 | 21 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2007 | 3 | 22 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2007 | 3 | 23 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2007 | 3 | 24 | 360.4898 | 25 | 335.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
2007 | 3 | 25 | 340.898 | 25 | 315.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
2007 | 3 | 26 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
2007 | 3 | 27 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2007 | 3 | 28 | 549.8776 | 25 | 524.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
2007 | 3 | 29 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
2007 | 3 | 30 | 408.8163 | 25 | 383.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
2007 | 3 | 31 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
2007 | 4 | 1 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
2007 | 4 | 2 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
2007 | 4 | 3 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
2007 | 4 | 4 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
2007 | 4 | 5 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
2007 | 4 | 6 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
2007 | 4 | 7 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2007 | 4 | 8 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2007 | 4 | 9 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2007 | 4 | 10 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2007 | 4 | 11 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2007 | 4 | 12 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2007 | 4 | 13 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2007 | 4 | 14 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2007 | 4 | 15 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
2007 | 4 | 16 | 1515.102 | 25 | 1490.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
2007 | 4 | 17 | 3082.449 | 25 | 3057.449 | 23.8351 | 0 | 0 | 23.8351 | 0% | 0 | 0 | 0
2007 | 4 | 18 | 2220.4082 | 25 | 2195.4082 | 25.5592 | 139.3858 | 0.77441 | 24.7848 | 89.27% | 261.1757 | 245.5052 | 5892.1238
2007 | 4 | 19 | 1893.8776 | 25 | 1868.8776 | 26.2122 | 139.3858 | 0.77441 | 25.4378 | 89.27% | 268.0575 | 251.974 | 6047.3771
2007 | 4 | 20 | 1711.0204 | 25 | 1686.0204 | 26.578 | 139.3858 | 0.77441 | 25.8035 | 89.27% | 271.9113 | 255.5966 | 6134.3189
2007 | 4 | 21 | 1619.5918 | 25 | 1594.5918 | 26.7608 | 139.3858 | 0.77441 | 25.9864 | 89.27% | 273.8382 | 257.4079 | 6177.7898
2007 | 4 | 22 | 1593.4694 | 25 | 1568.4694 | 26.8131 | 139.3858 | 0.77441 | 26.0387 | 89.27% | 274.3887 | 257.9254 | 6190.2101
2007 | 4 | 23 | 1436.7347 | 25 | 1411.7347 | 27.1265 | 139.3858 | 0.77441 | 26.3521 | 89.27% | 277.692 | 261.0305 | 6264.7317
2007 | 4 | 24 | 1462.8571 | 25 | 1437.8571 | 27.0743 | 139.3858 | 0.77441 | 26.2999 | 89.27% | 277.1415 | 260.513 | 6252.3114
2007 | 4 | 25 | 1038.3673 | 25 | 1013.3673 | 27.9233 | 139.3858 | 0.77441 | 27.1489 | 89.27% | 286.0878 | 268.9225 | 6454.1407
2007 | 4 | 26 | 671.3469 | 25 | 646.3469 | 28.6573 | 139.3858 | 0.77441 | 27.8829 | 89.27% | 293.8229 | 276.1936 | 6628.6454
2007 | 4 | 27 | 527.6735 | 25 | 502.6735 | 28.9447 | 139.3858 | 0.77441 | 28.1702 | 89.27% | 296.8509 | 279.0399 | 6696.9568
2007 | 4 | 28 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
2007 | 4 | 29 | 559.0204 | 25 | 534.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
2007 | 4 | 30 | 603.4286 | 25 | 578.4286 | 28.7931 | 139.3858 | 0.77441 | 28.0187 | 89.27% | 295.2543 | 277.5391 | 6660.9381
2007 | 5 | 1 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
2007 | 5 | 2 | 436.2449 | 25 | 411.2449 | 29.1275 | 139.3858 | 0.77441 | 28.3531 | 89.27% | 298.7778 | 280.8512 | 6740.4278
2007 | 5 | 3 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
2007 | 5 | 4 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2007 | 5 | 5 | 261.2245 | 25 | 236.2245 | 29.4776 | 139.3858 | 0.77441 | 28.7031 | 89.27% | 302.4665 | 284.3185 | 6823.6435
2007 | 5 | 6 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2007 | 5 | 7 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2007 | 5 | 8 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2007 | 5 | 9 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2007 | 5 | 10 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2007 | 5 | 11 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2007 | 5 | 12 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
2007 | 5 | 13 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
2007 | 5 | 14 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2007 | 5 | 15 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2007 | 5 | 16 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2007 | 5 | 17 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2007 | 5 | 18 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2007 | 5 | 19 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
2007 | 5 | 20 | 292.5714 | 25 | 267.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
2007 | 5 | 21 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
2007 | 5 | 22 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2007 | 5 | 23 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2007 | 5 | 24 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
2007 | 5 | 25 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2007 | 5 | 26 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2007 | 5 | 27 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2007 | 5 | 28 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2007 | 5 | 29 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2007 | 5 | 30 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2007 | 5 | 31 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2007 | 6 | 1 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2007 | 6 | 2 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2007 | 6 | 3 | 167.1837 | 25 | 142.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2007 | 6 | 4 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2007 | 6 | 5 | 1017.4694 | 25 | 992.4694 | 27.9651 | 139.3858 | 0.77441 | 27.1907 | 89.27% | 286.5282 | 269.3365 | 6464.0769
2007 | 6 | 6 | 577.3061 | 25 | 552.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
2007 | 6 | 7 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
2007 | 6 | 8 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2007 | 6 | 9 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2007 | 6 | 10 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2007 | 6 | 11 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2007 | 6 | 12 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2007 | 6 | 13 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2007 | 6 | 14 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2007 | 6 | 15 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2007 | 6 | 16 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2007 | 6 | 17 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2007 | 6 | 18 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2007 | 6 | 19 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2007 | 6 | 20 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2007 | 6 | 21 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
2007 | 6 | 22 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
2007 | 6 | 23 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2007 | 6 | 24 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2007 | 6 | 25 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2007 | 6 | 26 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2007 | 6 | 27 | 31.3469 | 25 | 6.3469 | 29.9373 | 0 | 0 | 29.9373 | 0% | 0 | 0 | 0
2007 | 6 | 28 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
2007 | 6 | 29 | 41.7959 | 25 | 16.7959 | 29.9164 | 16.7959 | 0.011245 | 29.9052 | 70.08% | 29.8104 | 28.0218 | 672.5224
2007 | 6 | 30 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2007 | 7 | 1 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2007 | 7 | 2 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2007 | 7 | 3 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2007 | 7 | 4 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2007 | 7 | 5 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2007 | 7 | 6 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2007 | 7 | 7 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2007 | 7 | 8 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2007 | 7 | 9 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2007 | 7 | 10 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2007 | 7 | 11 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2007 | 7 | 12 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2007 | 7 | 13 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2007 | 7 | 14 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2007 | 7 | 15 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2007 | 7 | 16 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2007 | 7 | 17 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2007 | 7 | 18 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2007 | 7 | 19 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2007 | 7 | 20 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2007 | 7 | 21 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2007 | 7 | 22 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2007 | 7 | 23 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2007 | 7 | 24 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2007 | 7 | 25 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2007 | 7 | 26 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2007 | 7 | 27 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2007 | 7 | 28 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2007 | 7 | 29 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2007 | 7 | 30 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2007 | 7 | 31 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
2007 | 8 | 1 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
2007 | 8 | 2 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
2007 | 8 | 3 | 9.2735 | 5 | 4.2735 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2007 | 8 | 4 | 8.6204 | 5 | 3.6204 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
2007 | 8 | 5 | 8.2286 | 5 | 3.2286 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2007 | 8 | 6 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
2007 | 8 | 7 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2007 | 8 | 8 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2007 | 8 | 9 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2007 | 8 | 10 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2007 | 8 | 11 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2007 | 8 | 12 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
2007 | 8 | 13 | 10.5796 | 5 | 5.5796 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
2007 | 8 | 14 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
2007 | 8 | 15 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
2007 | 8 | 16 | 7.9673 | 5 | 2.9673 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
2007 | 8 | 17 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
2007 | 8 | 18 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2007 | 8 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2007 | 8 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2007 | 8 | 21 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
2007 | 8 | 22 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
2007 | 8 | 23 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
2007 | 8 | 24 | 8.098 | 5 | 3.098 | 29.9838 | 0 | 0 | 29.9838 | 0% | 0 | 0 | 0
2007 | 8 | 25 | 8.8816 | 5 | 3.8816 | 29.9822 | 0 | 0 | 29.9822 | 0% | 0 | 0 | 0
2007 | 8 | 26 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2007 | 8 | 27 | 8.4898 | 5 | 3.4898 | 29.983 | 0 | 0 | 29.983 | 0% | 0 | 0 | 0
2007 | 8 | 28 | 7.5755 | 5 | 2.5755 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
2007 | 8 | 29 | 6.6612 | 5 | 1.6612 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
2007 | 8 | 30 | 6.7918 | 5 | 1.7918 | 29.9864 | 0 | 0 | 29.9864 | 0% | 0 | 0 | 0
2007 | 8 | 31 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2007 | 9 | 1 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2007 | 9 | 2 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2007 | 9 | 3 | 12.1469 | 15 | 0 | 29.9757 | 0 | 0 | 29.9757 | 0% | 0 | 0 | 0
2007 | 9 | 4 | 9.4041 | 15 | 0 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
2007 | 9 | 5 | 7.9673 | 15 | 0 | 29.9841 | 0 | 0 | 29.9841 | 0% | 0 | 0 | 0
2007 | 9 | 6 | 6.9224 | 15 | 0 | 29.9862 | 0 | 0 | 29.9862 | 0% | 0 | 0 | 0
2007 | 9 | 7 | 6.2694 | 15 | 0 | 29.9875 | 0 | 0 | 29.9875 | 0% | 0 | 0 | 0
2007 | 9 | 8 | 6.0082 | 15 | 0 | 29.988 | 0 | 0 | 29.988 | 0% | 0 | 0 | 0
2007 | 9 | 9 | 6.4 | 15 | 0 | 29.9872 | 0 | 0 | 29.9872 | 0% | 0 | 0 | 0
2007 | 9 | 10 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2007 | 9 | 11 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2007 | 9 | 12 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2007 | 9 | 13 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2007 | 9 | 14 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2007 | 9 | 15 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2007 | 9 | 16 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2007 | 9 | 17 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2007 | 9 | 18 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2007 | 9 | 19 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
2007 | 9 | 20 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
2007 | 9 | 21 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2007 | 9 | 22 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2007 | 9 | 23 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
2007 | 9 | 24 | 7.0531 | 15 | 0 | 29.9859 | 0 | 0 | 29.9859 | 0% | 0 | 0 | 0
2007 | 9 | 25 | 6.6612 | 15 | 0 | 29.9867 | 0 | 0 | 29.9867 | 0% | 0 | 0 | 0
2007 | 9 | 26 | 6.5306 | 15 | 0 | 29.9869 | 0 | 0 | 29.9869 | 0% | 0 | 0 | 0
2007 | 9 | 27 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
2007 | 9 | 28 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2007 | 9 | 29 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2007 | 9 | 30 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2007 | 10 | 1 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
2007 | 10 | 2 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
2007 | 10 | 3 | 10.0571 | 15 | 0 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
2007 | 10 | 4 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2007 | 10 | 5 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2007 | 10 | 6 | 9.2735 | 15 | 0 | 29.9815 | 0 | 0 | 29.9815 | 0% | 0 | 0 | 0
2007 | 10 | 7 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2007 | 10 | 8 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2007 | 10 | 9 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2007 | 10 | 10 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2007 | 10 | 11 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2007 | 10 | 12 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
2007 | 10 | 13 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2007 | 10 | 14 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
2007 | 10 | 15 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2007 | 10 | 16 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2007 | 10 | 17 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2007 | 10 | 18 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2007 | 10 | 19 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2007 | 10 | 20 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2007 | 10 | 21 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
2007 | 10 | 22 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
2007 | 10 | 23 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2007 | 10 | 24 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2007 | 10 | 25 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2007 | 10 | 26 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2007 | 10 | 27 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2007 | 10 | 28 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
2007 | 10 | 29 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
2007 | 10 | 30 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2007 | 10 | 31 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2007 | 11 | 1 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2007 | 11 | 2 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2007 | 11 | 3 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2007 | 11 | 4 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
2007 | 11 | 5 | 190.6939 | 15 | 175.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2007 | 11 | 6 | 292.5714 | 15 | 277.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
2007 | 11 | 7 | 455.8367 | 15 | 440.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
2007 | 11 | 8 | 266.449 | 15 | 251.449 | 29.4671 | 139.3858 | 0.77441 | 28.6927 | 89.27% | 302.3564 | 284.215 | 6821.1595
2007 | 11 | 9 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2007 | 11 | 10 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
2007 | 11 | 11 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
2007 | 11 | 12 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2007 | 11 | 13 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2007 | 11 | 14 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2007 | 11 | 15 | 374.8571 | 15 | 359.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
2007 | 11 | 16 | 1397.551 | 15 | 1382.551 | 27.2049 | 139.3858 | 0.77441 | 26.4305 | 89.27% | 278.5178 | 261.8068 | 6283.3621
2007 | 11 | 17 | 774.5306 | 15 | 759.5306 | 28.4509 | 139.3858 | 0.77441 | 27.6765 | 89.27% | 291.6483 | 274.1494 | 6579.5853
2007 | 11 | 18 | 429.7143 | 15 | 414.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
2007 | 11 | 19 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2007 | 11 | 20 | 244.2449 | 15 | 229.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
2007 | 11 | 21 | 211.5918 | 15 | 196.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2007 | 11 | 22 | 246.8571 | 15 | 231.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2007 | 11 | 23 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
2007 | 11 | 24 | 223.3469 | 15 | 208.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2007 | 11 | 25 | 177.6327 | 15 | 162.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2007 | 11 | 26 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2007 | 11 | 27 | 334.3673 | 15 | 319.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
2007 | 11 | 28 | 310.8571 | 15 | 295.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2007 | 11 | 29 | 241.6327 | 15 | 226.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2007 | 11 | 30 | 201.1429 | 15 | 186.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2007 | 12 | 1 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2007 | 12 | 2 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2007 | 12 | 3 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2007 | 12 | 4 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2007 | 12 | 5 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2007 | 12 | 6 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2007 | 12 | 7 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2007 | 12 | 8 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2007 | 12 | 9 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2007 | 12 | 10 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2007 | 12 | 11 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2007 | 12 | 12 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2007 | 12 | 13 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2007 | 12 | 14 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2007 | 12 | 15 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2007 | 12 | 16 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2007 | 12 | 17 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2007 | 12 | 18 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2007 | 12 | 19 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2007 | 12 | 20 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2007 | 12 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2007 | 12 | 22 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2007 | 12 | 23 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2007 | 12 | 24 | 483.2653 | 5 | 478.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
2007 | 12 | 25 | 502.8571 | 5 | 497.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
2007 | 12 | 26 | 336.9796 | 5 | 331.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2007 | 12 | 27 | 262.5306 | 5 | 257.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2007 | 12 | 28 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2007 | 12 | 29 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2007 | 12 | 30 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2007 | 12 | 31 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2008 | 1 | 1 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2008 | 1 | 2 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
2008 | 1 | 3 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2008 | 1 | 4 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2008 | 1 | 5 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2008 | 1 | 6 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2008 | 1 | 7 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
2008 | 1 | 8 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2008 | 1 | 9 | 299.102 | 5 | 294.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2008 | 1 | 10 | 444.0816 | 5 | 439.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
2008 | 1 | 11 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2008 | 1 | 12 | 364.4082 | 5 | 359.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
2008 | 1 | 13 | 305.6327 | 5 | 300.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
2008 | 1 | 14 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2008 | 1 | 15 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2008 | 1 | 16 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2008 | 1 | 17 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2008 | 1 | 18 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2008 | 1 | 19 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2008 | 1 | 20 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2008 | 1 | 21 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2008 | 1 | 22 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2008 | 1 | 23 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2008 | 1 | 24 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2008 | 1 | 25 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2008 | 1 | 26 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2008 | 1 | 27 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2008 | 1 | 28 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2008 | 1 | 29 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2008 | 1 | 30 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2008 | 1 | 31 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2008 | 2 | 1 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2008 | 2 | 2 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2008 | 2 | 3 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2008 | 2 | 4 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2008 | 2 | 5 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
2008 | 2 | 6 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2008 | 2 | 7 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2008 | 2 | 8 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
2008 | 2 | 9 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2008 | 2 | 10 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
2008 | 2 | 11 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2008 | 2 | 12 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2008 | 2 | 13 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2008 | 2 | 14 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2008 | 2 | 15 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2008 | 2 | 16 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
2008 | 2 | 17 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
2008 | 2 | 18 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2008 | 2 | 19 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2008 | 2 | 20 | 292.5714 | 5 | 287.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
2008 | 2 | 21 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2008 | 2 | 22 | 199.8367 | 5 | 194.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2008 | 2 | 23 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2008 | 2 | 24 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2008 | 2 | 25 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2008 | 2 | 26 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2008 | 2 | 27 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2008 | 2 | 28 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2008 | 2 | 29 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2008 | 3 | 1 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
2008 | 3 | 2 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
2008 | 3 | 3 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2008 | 3 | 4 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2008 | 3 | 5 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
2008 | 3 | 6 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
2008 | 3 | 7 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2008 | 3 | 8 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2008 | 3 | 9 | 723.5918 | 25 | 698.5918 | 28.5528 | 139.3858 | 0.77441 | 27.7784 | 89.27% | 292.7218 | 275.1585 | 6603.8049
2008 | 3 | 10 | 680.4898 | 25 | 655.4898 | 28.639 | 139.3858 | 0.77441 | 27.8646 | 89.27% | 293.6302 | 276.0124 | 6624.2983
2008 | 3 | 11 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
2008 | 3 | 12 | 364.4082 | 25 | 339.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
2008 | 3 | 13 | 304.3265 | 25 | 279.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
2008 | 3 | 14 | 270.3673 | 25 | 245.3673 | 29.4593 | 139.3858 | 0.77441 | 28.6849 | 89.27% | 302.2738 | 284.1374 | 6819.2964
2008 | 3 | 15 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
2008 | 3 | 16 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2008 | 3 | 17 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
2008 | 3 | 18 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2008 | 3 | 19 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2008 | 3 | 20 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2008 | 3 | 21 | 326.5306 | 25 | 301.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
2008 | 3 | 22 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2008 | 3 | 23 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2008 | 3 | 24 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
2008 | 3 | 25 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2008 | 3 | 26 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2008 | 3 | 27 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2008 | 3 | 28 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2008 | 3 | 29 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2008 | 3 | 30 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2008 | 3 | 31 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2008 | 4 | 1 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2008 | 4 | 2 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
2008 | 4 | 3 | 475.4286 | 25 | 450.4286 | 29.0491 | 139.3858 | 0.77441 | 28.2747 | 89.27% | 297.952 | 280.0749 | 6721.7974
2008 | 4 | 4 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
2008 | 4 | 5 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
2008 | 4 | 6 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
2008 | 4 | 7 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
2008 | 4 | 8 | 617.7959 | 25 | 592.7959 | 28.7644 | 139.3858 | 0.77441 | 27.99 | 89.27% | 294.9515 | 277.2545 | 6654.1069
2008 | 4 | 9 | 732.7347 | 25 | 707.7347 | 28.5345 | 139.3858 | 0.77441 | 27.7601 | 89.27% | 292.5292 | 274.9774 | 6599.4578
2008 | 4 | 10 | 974.3673 | 25 | 949.3673 | 28.0513 | 139.3858 | 0.77441 | 27.2769 | 89.27% | 287.4366 | 270.1904 | 6484.5703
2008 | 4 | 11 | 1273.4694 | 25 | 1248.4694 | 27.4531 | 139.3858 | 0.77441 | 26.6787 | 89.27% | 281.1329 | 264.2649 | 6342.3583
2008 | 4 | 12 | 1358.3673 | 25 | 1333.3673 | 27.2833 | 139.3858 | 0.77441 | 26.5089 | 89.27% | 279.3436 | 262.583 | 6301.9925
2008 | 4 | 13 | 1397.551 | 25 | 1372.551 | 27.2049 | 139.3858 | 0.77441 | 26.4305 | 89.27% | 278.5178 | 261.8068 | 6283.3621
2008 | 4 | 14 | 952.1633 | 25 | 927.1633 | 28.0957 | 139.3858 | 0.77441 | 27.3213 | 89.27% | 287.9046 | 270.6303 | 6495.1276
2008 | 4 | 15 | 875.102 | 25 | 850.102 | 28.2498 | 139.3858 | 0.77441 | 27.4754 | 89.27% | 289.5287 | 272.157 | 6531.7673
2008 | 4 | 16 | 961.3061 | 25 | 936.3061 | 28.0774 | 139.3858 | 0.77441 | 27.303 | 89.27% | 287.7119 | 270.4492 | 6490.7805
2008 | 4 | 17 | 1182.0408 | 25 | 1157.0408 | 27.6359 | 139.3858 | 0.77441 | 26.8615 | 89.27% | 283.0598 | 266.0762 | 6385.8292
2008 | 4 | 18 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
2008 | 4 | 19 | 1580.4082 | 25 | 1555.4082 | 26.8392 | 139.3858 | 0.77441 | 26.0648 | 89.27% | 274.664 | 258.1842 | 6196.4202
2008 | 4 | 20 | 1462.8571 | 25 | 1437.8571 | 27.0743 | 139.3858 | 0.77441 | 26.2999 | 89.27% | 277.1415 | 260.513 | 6252.3114
2008 | 4 | 21 | 1242.1224 | 25 | 1217.1224 | 27.5158 | 139.3858 | 0.77441 | 26.7413 | 89.27% | 281.7936 | 264.8859 | 6357.2626
2008 | 4 | 22 | 1114.1224 | 25 | 1089.1224 | 27.7718 | 139.3858 | 0.77441 | 26.9973 | 89.27% | 284.4912 | 267.4217 | 6418.1219
2008 | 4 | 23 | 967.8367 | 25 | 942.8367 | 28.0643 | 139.3858 | 0.77441 | 27.2899 | 89.27% | 287.5743 | 270.3198 | 6487.6754
2008 | 4 | 24 | 842.449 | 25 | 817.449 | 28.3151 | 139.3858 | 0.77441 | 27.5407 | 89.27% | 290.2169 | 272.8039 | 6547.2927
2008 | 4 | 25 | 596.898 | 25 | 571.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
2008 | 4 | 26 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
2008 | 4 | 27 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2008 | 4 | 28 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
2008 | 4 | 29 | 2089.7959 | 25 | 2064.7959 | 25.8204 | 139.3858 | 0.77441 | 25.046 | 89.27% | 263.9284 | 248.0927 | 5954.2251
2008 | 4 | 30 | 2298.7755 | 25 | 2273.7755 | 25.4024 | 139.3858 | 0.77441 | 24.628 | 89.27% | 259.5241 | 243.9526 | 5854.863
2008 | 5 | 1 | 1040.9796 | 25 | 1015.9796 | 27.918 | 139.3858 | 0.77441 | 27.1436 | 89.27% | 286.0327 | 268.8708 | 6452.8987
2008 | 5 | 2 | 630.8571 | 25 | 605.8571 | 28.7383 | 139.3858 | 0.77441 | 27.9639 | 89.27% | 294.6763 | 276.9957 | 6647.8968
2008 | 5 | 3 | 480.6531 | 25 | 455.6531 | 29.0387 | 139.3858 | 0.77441 | 28.2643 | 89.27% | 297.8419 | 279.9714 | 6719.3133
2008 | 5 | 4 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
2008 | 5 | 5 | 515.9184 | 25 | 490.9184 | 28.9682 | 139.3858 | 0.77441 | 28.1938 | 89.27% | 297.0987 | 279.2727 | 6702.5459
2008 | 5 | 6 | 404.898 | 25 | 379.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
2008 | 5 | 7 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
2008 | 5 | 8 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2008 | 5 | 9 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2008 | 5 | 10 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2008 | 5 | 11 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2008 | 5 | 12 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2008 | 5 | 13 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2008 | 5 | 14 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
2008 | 5 | 15 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2008 | 5 | 16 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2008 | 5 | 17 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2008 | 5 | 18 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2008 | 5 | 19 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2008 | 5 | 20 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2008 | 5 | 21 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2008 | 5 | 22 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2008 | 5 | 23 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2008 | 5 | 24 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2008 | 5 | 25 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2008 | 5 | 26 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2008 | 5 | 27 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2008 | 5 | 28 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2008 | 5 | 29 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2008 | 5 | 30 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2008 | 5 | 31 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2008 | 6 | 1 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2008 | 6 | 2 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2008 | 6 | 3 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2008 | 6 | 4 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2008 | 6 | 5 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2008 | 6 | 6 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2008 | 6 | 7 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2008 | 6 | 8 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2008 | 6 | 9 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2008 | 6 | 10 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2008 | 6 | 11 | 411.4286 | 25 | 386.4286 | 29.1771 | 139.3858 | 0.77441 | 28.4027 | 89.27% | 299.3008 | 281.3428 | 6752.227
2008 | 6 | 12 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2008 | 6 | 13 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2008 | 6 | 14 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2008 | 6 | 15 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2008 | 6 | 16 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2008 | 6 | 17 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2008 | 6 | 18 | 186.7755 | 25 | 161.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2008 | 6 | 19 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
2008 | 6 | 20 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
2008 | 6 | 21 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2008 | 6 | 22 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2008 | 6 | 23 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2008 | 6 | 24 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2008 | 6 | 25 | 142.3673 | 25 | 117.3673 | 29.7153 | 117.3673 | 0.54907 | 29.1662 | 91.43% | 265.0571 | 249.1537 | 5979.688
2008 | 6 | 26 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2008 | 6 | 27 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2008 | 6 | 28 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2008 | 6 | 29 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2008 | 6 | 30 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2008 | 7 | 1 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2008 | 7 | 2 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2008 | 7 | 3 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2008 | 7 | 4 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2008 | 7 | 5 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2008 | 7 | 6 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2008 | 7 | 7 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2008 | 7 | 8 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2008 | 7 | 9 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2008 | 7 | 10 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2008 | 7 | 11 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2008 | 7 | 12 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2008 | 7 | 13 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2008 | 7 | 14 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2008 | 7 | 15 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2008 | 7 | 16 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2008 | 7 | 17 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2008 | 7 | 18 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2008 | 7 | 19 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2008 | 7 | 20 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2008 | 7 | 21 | 353.9592 | 5 | 348.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
2008 | 7 | 22 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2008 | 7 | 23 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2008 | 7 | 24 | 429.7143 | 5 | 424.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
2008 | 7 | 25 | 1345.3061 | 5 | 1340.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
2008 | 7 | 26 | 523.7551 | 5 | 518.7551 | 28.9525 | 139.3858 | 0.77441 | 28.1781 | 89.27% | 296.9335 | 279.1175 | 6698.8199
2008 | 7 | 27 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2008 | 7 | 28 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2008 | 7 | 29 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2008 | 7 | 30 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2008 | 7 | 31 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2008 | 8 | 1 | 1216 | 5 | 1211 | 27.568 | 139.3858 | 0.77441 | 26.7936 | 89.27% | 282.3441 | 265.4035 | 6369.6829
2008 | 8 | 2 | 839.8367 | 5 | 834.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
2008 | 8 | 3 | 577.3061 | 5 | 572.3061 | 28.8454 | 139.3858 | 0.77441 | 28.071 | 89.27% | 295.8049 | 278.0566 | 6673.3583
2008 | 8 | 4 | 428.4082 | 5 | 423.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
2008 | 8 | 5 | 386.6122 | 5 | 381.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
2008 | 8 | 6 | 453.2245 | 5 | 448.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
2008 | 8 | 7 | 1276.0816 | 5 | 1271.0816 | 27.4478 | 139.3858 | 0.77441 | 26.6734 | 89.27% | 281.0778 | 264.2132 | 6341.1163
2008 | 8 | 8 | 1449.7959 | 5 | 1444.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
2008 | 8 | 9 | 1264.3265 | 5 | 1259.3265 | 27.4713 | 139.3858 | 0.77441 | 26.6969 | 89.27% | 281.3256 | 264.4461 | 6346.7054
2008 | 8 | 10 | 740.5714 | 5 | 735.5714 | 28.5189 | 139.3858 | 0.77441 | 27.7444 | 89.27% | 292.364 | 274.8222 | 6595.7317
2008 | 8 | 11 | 474.1224 | 5 | 469.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
2008 | 8 | 12 | 369.6327 | 5 | 364.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2008 | 8 | 13 | 429.7143 | 5 | 424.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
2008 | 8 | 14 | 292.5714 | 5 | 287.5714 | 29.4149 | 139.3858 | 0.77441 | 28.6404 | 89.27% | 301.8058 | 283.6975 | 6808.7392
2008 | 8 | 15 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2008 | 8 | 16 | 219.4286 | 5 | 214.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2008 | 8 | 17 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2008 | 8 | 18 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2008 | 8 | 19 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2008 | 8 | 20 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2008 | 8 | 21 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2008 | 8 | 22 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2008 | 8 | 23 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2008 | 8 | 24 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2008 | 8 | 25 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2008 | 8 | 26 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2008 | 8 | 27 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2008 | 8 | 28 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2008 | 8 | 29 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2008 | 8 | 30 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2008 | 8 | 31 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2008 | 9 | 1 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
2008 | 9 | 2 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2008 | 9 | 3 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2008 | 9 | 4 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2008 | 9 | 5 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2008 | 9 | 6 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2008 | 9 | 7 | 560.3265 | 15 | 545.3265 | 28.8793 | 139.3858 | 0.77441 | 28.1049 | 89.27% | 296.1627 | 278.393 | 6681.4315
2008 | 9 | 8 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2008 | 9 | 9 | 219.4286 | 15 | 204.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2008 | 9 | 10 | 250.7755 | 15 | 235.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2008 | 9 | 11 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
2008 | 9 | 12 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
2008 | 9 | 13 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2008 | 9 | 14 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
2008 | 9 | 15 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
2008 | 9 | 16 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2008 | 9 | 17 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2008 | 9 | 18 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2008 | 9 | 19 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2008 | 9 | 20 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2008 | 9 | 21 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2008 | 9 | 22 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2008 | 9 | 23 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2008 | 9 | 24 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
2008 | 9 | 25 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
2008 | 9 | 26 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
2008 | 9 | 27 | 288.6531 | 15 | 273.6531 | 29.4227 | 139.3858 | 0.77441 | 28.6483 | 89.27% | 301.8884 | 283.7751 | 6810.6022
2008 | 9 | 28 | 667.4286 | 15 | 652.4286 | 28.6651 | 139.3858 | 0.77441 | 27.8907 | 89.27% | 293.9055 | 276.2712 | 6630.5084
2008 | 9 | 29 | 782.3673 | 15 | 767.3673 | 28.4353 | 139.3858 | 0.77441 | 27.6609 | 89.27% | 291.4831 | 273.9941 | 6575.8593
2008 | 9 | 30 | 407.5102 | 15 | 392.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
2008 | 10 | 1 | 312.1633 | 15 | 297.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
2008 | 10 | 2 | 545.9592 | 15 | 530.9592 | 28.9081 | 139.3858 | 0.77441 | 28.1337 | 89.27% | 296.4655 | 278.6776 | 6688.2626
2008 | 10 | 3 | 356.5714 | 15 | 341.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
2008 | 10 | 4 | 254.6939 | 15 | 239.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2008 | 10 | 5 | 194.6122 | 15 | 179.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2008 | 10 | 6 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
2008 | 10 | 7 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
2008 | 10 | 8 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
2008 | 10 | 9 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2008 | 10 | 10 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
2008 | 10 | 11 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2008 | 10 | 12 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
2008 | 10 | 13 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2008 | 10 | 14 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2008 | 10 | 15 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2008 | 10 | 16 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2008 | 10 | 17 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2008 | 10 | 18 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2008 | 10 | 19 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2008 | 10 | 20 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2008 | 10 | 21 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2008 | 10 | 22 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2008 | 10 | 23 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2008 | 10 | 24 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2008 | 10 | 25 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2008 | 10 | 26 | 820.2449 | 15 | 805.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
2008 | 10 | 27 | 596.898 | 15 | 581.898 | 28.8062 | 139.3858 | 0.77441 | 28.0318 | 89.27% | 295.392 | 277.6685 | 6664.0431
2008 | 10 | 28 | 357.8776 | 15 | 342.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
2008 | 10 | 29 | 385.3061 | 15 | 370.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
2008 | 10 | 30 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
2008 | 10 | 31 | 231.1837 | 15 | 216.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2008 | 11 | 1 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2008 | 11 | 2 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2008 | 11 | 3 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
2008 | 11 | 4 | 131.9184 | 15 | 116.9184 | 29.7362 | 116.9184 | 0.54488 | 29.1913 | 91.43% | 264.2703 | 248.4141 | 5961.9376
2008 | 11 | 5 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
2008 | 11 | 6 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
2008 | 11 | 7 | 249.4694 | 15 | 234.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
2008 | 11 | 8 | 254.6939 | 15 | 239.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2008 | 11 | 9 | 423.1837 | 15 | 408.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
2008 | 11 | 10 | 342.2041 | 15 | 327.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
2008 | 11 | 11 | 267.7551 | 15 | 252.7551 | 29.4645 | 139.3858 | 0.77441 | 28.6901 | 89.27% | 302.3288 | 284.1891 | 6820.5384
2008 | 11 | 12 | 219.4286 | 15 | 204.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2008 | 11 | 13 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2008 | 11 | 14 | 348.7347 | 15 | 333.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
2008 | 11 | 15 | 586.449 | 15 | 571.449 | 28.8271 | 139.3858 | 0.77441 | 28.0527 | 89.27% | 295.6122 | 277.8755 | 6669.0112
2008 | 11 | 16 | 820.2449 | 15 | 805.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
2008 | 11 | 17 | 569.4694 | 15 | 554.4694 | 28.8611 | 139.3858 | 0.77441 | 28.0867 | 89.27% | 295.9701 | 278.2119 | 6677.0844
2008 | 11 | 18 | 384 | 15 | 369 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
2008 | 11 | 19 | 299.102 | 15 | 284.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2008 | 11 | 20 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
2008 | 11 | 21 | 206.3673 | 15 | 191.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2008 | 11 | 22 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2008 | 11 | 23 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
2008 | 11 | 24 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
2008 | 11 | 25 | 318.6939 | 15 | 303.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2008 | 11 | 26 | 2795.102 | 15 | 2780.102 | 24.4098 | 0 | 0 | 24.4098 | 0% | 0 | 0 | 0
2008 | 11 | 27 | 1397.551 | 15 | 1382.551 | 27.2049 | 139.3858 | 0.77441 | 26.4305 | 89.27% | 278.5178 | 261.8068 | 6283.3621
2008 | 11 | 28 | 761.4694 | 15 | 746.4694 | 28.4771 | 139.3858 | 0.77441 | 27.7027 | 89.27% | 291.9236 | 274.4081 | 6585.7955
2008 | 11 | 29 | 518.5306 | 15 | 503.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
2008 | 11 | 30 | 393.1429 | 15 | 378.1429 | 29.2137 | 139.3858 | 0.77441 | 28.4393 | 89.27% | 299.6862 | 281.705 | 6760.9212
2008 | 12 | 1 | 374.8571 | 5 | 369.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
2008 | 12 | 2 | 364.4082 | 5 | 359.4082 | 29.2712 | 139.3858 | 0.77441 | 28.4968 | 89.27% | 300.2918 | 282.2743 | 6774.5835
2008 | 12 | 3 | 317.3878 | 5 | 312.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
2008 | 12 | 4 | 280.8163 | 5 | 275.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
2008 | 12 | 5 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2008 | 12 | 6 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2008 | 12 | 7 | 208.9796 | 5 | 203.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
2008 | 12 | 8 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2008 | 12 | 9 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2008 | 12 | 10 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2008 | 12 | 11 | 340.898 | 5 | 335.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
2008 | 12 | 12 | 1246.0408 | 5 | 1241.0408 | 27.5079 | 139.3858 | 0.77441 | 26.7335 | 89.27% | 281.711 | 264.8083 | 6355.3996
2008 | 12 | 13 | 1515.102 | 5 | 1510.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
2008 | 12 | 14 | 821.551 | 5 | 816.551 | 28.3569 | 139.3858 | 0.77441 | 27.5825 | 89.27% | 290.6573 | 273.2179 | 6557.2289
2008 | 12 | 15 | 476.7347 | 5 | 471.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
2008 | 12 | 16 | 604.7347 | 5 | 599.7347 | 28.7905 | 139.3858 | 0.77441 | 28.0161 | 89.27% | 295.2268 | 277.5132 | 6660.3171
2008 | 12 | 17 | 440.1633 | 5 | 435.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
2008 | 12 | 18 | 376.1633 | 5 | 371.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
2008 | 12 | 19 | 310.8571 | 5 | 305.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2008 | 12 | 20 | 271.6735 | 5 | 266.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
2008 | 12 | 21 | 239.0204 | 5 | 234.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
2008 | 12 | 22 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2008 | 12 | 23 | 233.7959 | 5 | 228.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2008 | 12 | 24 | 232.4898 | 5 | 227.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2008 | 12 | 25 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2008 | 12 | 26 | 237.7143 | 5 | 232.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2008 | 12 | 27 | 225.9592 | 5 | 220.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2008 | 12 | 28 | 223.3469 | 5 | 218.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2008 | 12 | 29 | 263.8367 | 5 | 258.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
2008 | 12 | 30 | 244.2449 | 5 | 239.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
2008 | 12 | 31 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2009 | 1 | 1 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2009 | 1 | 2 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2009 | 1 | 3 | 158.0408 | 5 | 153.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2009 | 1 | 4 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2009 | 1 | 5 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2009 | 1 | 6 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2009 | 1 | 7 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2009 | 1 | 8 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2009 | 1 | 9 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2009 | 1 | 10 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2009 | 1 | 11 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2009 | 1 | 12 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2009 | 1 | 13 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2009 | 1 | 14 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2009 | 1 | 15 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2009 | 1 | 16 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2009 | 1 | 17 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2009 | 1 | 18 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2009 | 1 | 19 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2009 | 1 | 20 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2009 | 1 | 21 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2009 | 1 | 22 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2009 | 1 | 23 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2009 | 1 | 24 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2009 | 1 | 25 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2009 | 1 | 26 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2009 | 1 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2009 | 1 | 28 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2009 | 1 | 29 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2009 | 1 | 30 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2009 | 1 | 31 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2009 | 2 | 1 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2009 | 2 | 2 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2009 | 2 | 3 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2009 | 2 | 4 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2009 | 2 | 5 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2009 | 2 | 6 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2009 | 2 | 7 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2009 | 2 | 8 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2009 | 2 | 9 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2009 | 2 | 10 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2009 | 2 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2009 | 2 | 12 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2009 | 2 | 13 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2009 | 2 | 14 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2009 | 2 | 15 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2009 | 2 | 16 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2009 | 2 | 17 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2009 | 2 | 18 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2009 | 2 | 19 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2009 | 2 | 20 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2009 | 2 | 21 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2009 | 2 | 22 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2009 | 2 | 23 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2009 | 2 | 24 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2009 | 2 | 25 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2009 | 2 | 26 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2009 | 2 | 27 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2009 | 2 | 28 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2009 | 3 | 1 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2009 | 3 | 2 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2009 | 3 | 3 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2009 | 3 | 4 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2009 | 3 | 5 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2009 | 3 | 6 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2009 | 3 | 7 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2009 | 3 | 8 | 205.0612 | 25 | 180.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2009 | 3 | 9 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2009 | 3 | 10 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2009 | 3 | 11 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2009 | 3 | 12 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2009 | 3 | 13 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2009 | 3 | 14 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2009 | 3 | 15 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2009 | 3 | 16 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2009 | 3 | 17 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2009 | 3 | 18 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2009 | 3 | 19 | 227.2653 | 25 | 202.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2009 | 3 | 20 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
2009 | 3 | 21 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2009 | 3 | 22 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2009 | 3 | 23 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
2009 | 3 | 24 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2009 | 3 | 25 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2009 | 3 | 26 | 223.3469 | 25 | 198.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2009 | 3 | 27 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2009 | 3 | 28 | 440.1633 | 25 | 415.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
2009 | 3 | 29 | 488.4898 | 25 | 463.4898 | 29.023 | 139.3858 | 0.77441 | 28.2486 | 89.27% | 297.6767 | 279.8161 | 6715.5872
2009 | 3 | 30 | 945.6327 | 25 | 920.6327 | 28.1087 | 139.3858 | 0.77441 | 27.3343 | 89.27% | 288.0422 | 270.7597 | 6498.2326
2009 | 3 | 31 | 824.1633 | 25 | 799.1633 | 28.3517 | 139.3858 | 0.77441 | 27.5773 | 89.27% | 290.6023 | 273.1661 | 6555.9868
2009 | 4 | 1 | 710.5306 | 25 | 685.5306 | 28.5789 | 139.3858 | 0.77441 | 27.8045 | 89.27% | 292.9971 | 275.4173 | 6610.015
2009 | 4 | 2 | 641.3061 | 25 | 616.3061 | 28.7174 | 139.3858 | 0.77441 | 27.943 | 89.27% | 294.4561 | 276.7887 | 6642.9287
2009 | 4 | 3 | 863.3469 | 25 | 838.3469 | 28.2733 | 139.3858 | 0.77441 | 27.4989 | 89.27% | 289.7764 | 272.3899 | 6537.3564
2009 | 4 | 4 | 1593.4694 | 25 | 1568.4694 | 26.8131 | 139.3858 | 0.77441 | 26.0387 | 89.27% | 274.3887 | 257.9254 | 6190.2101
2009 | 4 | 5 | 1256.4898 | 25 | 1231.4898 | 27.487 | 139.3858 | 0.77441 | 26.7126 | 89.27% | 281.4908 | 264.6013 | 6350.4315
2009 | 4 | 6 | 1055.3469 | 25 | 1030.3469 | 27.8893 | 139.3858 | 0.77441 | 27.1149 | 89.27% | 285.7299 | 268.5861 | 6446.0675
2009 | 4 | 7 | 1906.9388 | 25 | 1881.9388 | 26.1861 | 139.3858 | 0.77441 | 25.4117 | 89.27% | 267.7822 | 251.7153 | 6041.1669
2009 | 4 | 8 | 1204.2449 | 25 | 1179.2449 | 27.5915 | 139.3858 | 0.77441 | 26.8171 | 89.27% | 282.5918 | 265.6363 | 6375.272
2009 | 4 | 9 | 740.5714 | 25 | 715.5714 | 28.5189 | 139.3858 | 0.77441 | 27.7444 | 89.27% | 292.364 | 274.8222 | 6595.7317
2009 | 4 | 10 | 590.3673 | 25 | 565.3673 | 28.8193 | 139.3858 | 0.77441 | 28.0449 | 89.27% | 295.5296 | 277.7978 | 6667.1482
2009 | 4 | 11 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
2009 | 4 | 12 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
2009 | 4 | 13 | 368.3265 | 25 | 343.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
2009 | 4 | 14 | 327.8367 | 25 | 302.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
2009 | 4 | 15 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
2009 | 4 | 16 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
2009 | 4 | 17 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
2009 | 4 | 18 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2009 | 4 | 19 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2009 | 4 | 20 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2009 | 4 | 21 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
2009 | 4 | 22 | 768 | 25 | 743 | 28.464 | 139.3858 | 0.77441 | 27.6896 | 89.27% | 291.7859 | 274.2788 | 6582.6904
2009 | 4 | 23 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
2009 | 4 | 24 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
2009 | 4 | 25 | 357.8776 | 25 | 332.8776 | 29.2842 | 139.3858 | 0.77441 | 28.5098 | 89.27% | 300.4295 | 282.4037 | 6777.6885
2009 | 4 | 26 | 295.1837 | 25 | 270.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
2009 | 4 | 27 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2009 | 4 | 28 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2009 | 4 | 29 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2009 | 4 | 30 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2009 | 5 | 1 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2009 | 5 | 2 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2009 | 5 | 3 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
2009 | 5 | 4 | 141.0612 | 25 | 116.0612 | 29.7179 | 116.0612 | 0.53692 | 29.181 | 91.43% | 262.2401 | 246.5057 | 5916.1365
2009 | 5 | 5 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2009 | 5 | 6 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2009 | 5 | 7 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2009 | 5 | 8 | 246.8571 | 25 | 221.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2009 | 5 | 9 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2009 | 5 | 10 | 462.3673 | 25 | 437.3673 | 29.0753 | 139.3858 | 0.77441 | 28.3009 | 89.27% | 298.2273 | 280.3336 | 6728.0075
2009 | 5 | 11 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
2009 | 5 | 12 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2009 | 5 | 13 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2009 | 5 | 14 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2009 | 5 | 15 | 150.2041 | 25 | 125.2041 | 29.6996 | 125.2041 | 0.62484 | 29.0747 | 90.74% | 279.7415 | 262.957 | 6310.9681
2009 | 5 | 16 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2009 | 5 | 17 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2009 | 5 | 18 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2009 | 5 | 19 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2009 | 5 | 20 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2009 | 5 | 21 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2009 | 5 | 22 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2009 | 5 | 23 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2009 | 5 | 24 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2009 | 5 | 25 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2009 | 5 | 26 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2009 | 5 | 27 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2009 | 5 | 28 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2009 | 5 | 29 | 206.3673 | 25 | 181.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2009 | 5 | 30 | 232.4898 | 25 | 207.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2009 | 5 | 31 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
2009 | 6 | 1 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
2009 | 6 | 2 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2009 | 6 | 3 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2009 | 6 | 4 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2009 | 6 | 5 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2009 | 6 | 6 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2009 | 6 | 7 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2009 | 6 | 8 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2009 | 6 | 9 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2009 | 6 | 10 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2009 | 6 | 11 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2009 | 6 | 12 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
2009 | 6 | 13 | 417.9592 | 25 | 392.9592 | 29.1641 | 139.3858 | 0.77441 | 28.3897 | 89.27% | 299.1632 | 281.2134 | 6749.1219
2009 | 6 | 14 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2009 | 6 | 15 | 461.0612 | 25 | 436.0612 | 29.0779 | 139.3858 | 0.77441 | 28.3035 | 89.27% | 298.2548 | 280.3595 | 6728.6285
2009 | 6 | 16 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
2009 | 6 | 17 | 222.0408 | 25 | 197.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2009 | 6 | 18 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
2009 | 6 | 19 | 859.4286 | 25 | 834.4286 | 28.2811 | 139.3858 | 0.77441 | 27.5067 | 89.27% | 289.859 | 272.4675 | 6539.2195
2009 | 6 | 20 | 1290.449 | 25 | 1265.449 | 27.4191 | 139.3858 | 0.77441 | 26.6447 | 89.27% | 280.7751 | 263.9285 | 6334.2851
2009 | 6 | 21 | 621.7143 | 25 | 596.7143 | 28.7566 | 139.3858 | 0.77441 | 27.9822 | 89.27% | 294.869 | 277.1768 | 6652.2439
2009 | 6 | 22 | 433.6327 | 25 | 408.6327 | 29.1327 | 139.3858 | 0.77441 | 28.3583 | 89.27% | 298.8329 | 280.9029 | 6741.6698
2009 | 6 | 23 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
2009 | 6 | 24 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2009 | 6 | 25 | 374.8571 | 25 | 349.8571 | 29.2503 | 139.3858 | 0.77441 | 28.4759 | 89.27% | 300.0716 | 282.0673 | 6769.6154
2009 | 6 | 26 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2009 | 6 | 27 | 1111.5102 | 25 | 1086.5102 | 27.777 | 139.3858 | 0.77441 | 27.0026 | 89.27% | 284.5463 | 267.4735 | 6419.3639
2009 | 6 | 28 | 915.5918 | 25 | 890.5918 | 28.1688 | 139.3858 | 0.77441 | 27.3944 | 89.27% | 288.6754 | 271.3548 | 6512.5159
2009 | 6 | 29 | 1554.2857 | 25 | 1529.2857 | 26.8914 | 139.3858 | 0.77441 | 26.117 | 89.27% | 275.2146 | 258.7017 | 6208.8405
2009 | 6 | 30 | 1263.0204 | 25 | 1238.0204 | 27.474 | 139.3858 | 0.77441 | 26.6995 | 89.27% | 281.3531 | 264.4719 | 6347.3264
2009 | 7 | 1 | 735.3469 | 5 | 730.3469 | 28.5293 | 139.3858 | 0.77441 | 27.7549 | 89.27% | 292.4741 | 274.9257 | 6598.2157
2009 | 7 | 2 | 659.5918 | 5 | 654.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
2009 | 7 | 3 | 1193.7959 | 5 | 1188.7959 | 27.6124 | 139.3858 | 0.77441 | 26.838 | 89.27% | 282.8121 | 265.8433 | 6380.2401
2009 | 7 | 4 | 1306.1224 | 5 | 1301.1224 | 27.3878 | 139.3858 | 0.77441 | 26.6133 | 89.27% | 280.4447 | 263.618 | 6326.833
2009 | 7 | 5 | 724.898 | 5 | 719.898 | 28.5502 | 139.3858 | 0.77441 | 27.7758 | 89.27% | 292.6943 | 275.1327 | 6603.1838
2009 | 7 | 6 | 441.4694 | 5 | 436.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
2009 | 7 | 7 | 360.4898 | 5 | 355.4898 | 29.279 | 139.3858 | 0.77441 | 28.5046 | 89.27% | 300.3744 | 282.3519 | 6776.4465
2009 | 7 | 8 | 790.2041 | 5 | 785.2041 | 28.4196 | 139.3858 | 0.77441 | 27.6452 | 89.27% | 291.318 | 273.8389 | 6572.1332
2009 | 7 | 9 | 992.6531 | 5 | 987.6531 | 28.0147 | 139.3858 | 0.77441 | 27.2403 | 89.27% | 287.0512 | 269.8282 | 6475.8761
2009 | 7 | 10 | 526.3673 | 5 | 521.3673 | 28.9473 | 139.3858 | 0.77441 | 28.1729 | 89.27% | 296.8785 | 279.0657 | 6697.5778
2009 | 7 | 11 | 356.5714 | 5 | 351.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
2009 | 7 | 12 | 287.3469 | 5 | 282.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2009 | 7 | 13 | 241.6327 | 5 | 236.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2009 | 7 | 14 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2009 | 7 | 15 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2009 | 7 | 16 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
2009 | 7 | 17 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
2009 | 7 | 18 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2009 | 7 | 19 | 181.551 | 5 | 176.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2009 | 7 | 20 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2009 | 7 | 21 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2009 | 7 | 22 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2009 | 7 | 23 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2009 | 7 | 24 | 385.3061 | 5 | 380.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
2009 | 7 | 25 | 549.8776 | 5 | 544.8776 | 28.9002 | 139.3858 | 0.77441 | 28.1258 | 89.27% | 296.383 | 278.6 | 6686.3996
2009 | 7 | 26 | 323.9184 | 5 | 318.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2009 | 7 | 27 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2009 | 7 | 28 | 216.8163 | 5 | 211.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2009 | 7 | 29 | 163.2653 | 5 | 158.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2009 | 7 | 30 | 604.7347 | 5 | 599.7347 | 28.7905 | 139.3858 | 0.77441 | 28.0161 | 89.27% | 295.2268 | 277.5132 | 6660.3171
2009 | 7 | 31 | 623.0204 | 5 | 618.0204 | 28.754 | 139.3858 | 0.77441 | 27.9795 | 89.27% | 294.8414 | 277.151 | 6651.6229
2009 | 8 | 1 | 805.8776 | 5 | 800.8776 | 28.3882 | 139.3858 | 0.77441 | 27.6138 | 89.27% | 290.9876 | 273.5284 | 6564.681
2009 | 8 | 2 | 421.8776 | 5 | 416.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
2009 | 8 | 3 | 535.5102 | 5 | 530.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
2009 | 8 | 4 | 369.6327 | 5 | 364.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2009 | 8 | 5 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
2009 | 8 | 6 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2009 | 8 | 7 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2009 | 8 | 8 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2009 | 8 | 9 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2009 | 8 | 10 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2009 | 8 | 11 | 133.2245 | 5 | 128.2245 | 29.7336 | 128.2245 | 0.65535 | 29.0782 | 90.74% | 286.5239 | 269.3325 | 6463.9797
2009 | 8 | 12 | 244.2449 | 5 | 239.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
2009 | 8 | 13 | 334.3673 | 5 | 329.3673 | 29.3313 | 139.3858 | 0.77441 | 28.5569 | 89.27% | 300.9249 | 282.8694 | 6788.8668
2009 | 8 | 14 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2009 | 8 | 15 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2009 | 8 | 16 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2009 | 8 | 17 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2009 | 8 | 18 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2009 | 8 | 19 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2009 | 8 | 20 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2009 | 8 | 21 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2009 | 8 | 22 | 736.6531 | 5 | 731.6531 | 28.5267 | 139.3858 | 0.77441 | 27.7523 | 89.27% | 292.4466 | 274.8998 | 6597.5947
2009 | 8 | 23 | 495.0204 | 5 | 490.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
2009 | 8 | 24 | 476.7347 | 5 | 471.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
2009 | 8 | 25 | 368.3265 | 5 | 363.3265 | 29.2633 | 139.3858 | 0.77441 | 28.4889 | 89.27% | 300.2092 | 282.1967 | 6772.7204
2009 | 8 | 26 | 254.6939 | 5 | 249.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2009 | 8 | 27 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2009 | 8 | 28 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2009 | 8 | 29 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2009 | 8 | 30 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2009 | 8 | 31 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2009 | 9 | 1 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
2009 | 9 | 2 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2009 | 9 | 3 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
2009 | 9 | 4 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
2009 | 9 | 5 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2009 | 9 | 6 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2009 | 9 | 7 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2009 | 9 | 8 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2009 | 9 | 9 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2009 | 9 | 10 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
2009 | 9 | 11 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2009 | 9 | 12 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2009 | 9 | 13 | 44.4082 | 15 | 29.4082 | 29.9112 | 29.4082 | 0.034472 | 29.8767 | 80.09% | 59.594 | 56.0184 | 1344.441
2009 | 9 | 14 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
2009 | 9 | 15 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2009 | 9 | 16 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2009 | 9 | 17 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2009 | 9 | 18 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2009 | 9 | 19 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2009 | 9 | 20 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2009 | 9 | 21 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2009 | 9 | 22 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2009 | 9 | 23 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2009 | 9 | 24 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2009 | 9 | 25 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2009 | 9 | 26 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2009 | 9 | 27 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2009 | 9 | 28 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2009 | 9 | 29 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
2009 | 9 | 30 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2009 | 10 | 1 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2009 | 10 | 2 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2009 | 10 | 3 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
2009 | 10 | 4 | 404.898 | 15 | 389.898 | 29.1902 | 139.3858 | 0.77441 | 28.4158 | 89.27% | 299.4385 | 281.4722 | 6755.3321
2009 | 10 | 5 | 245.551 | 15 | 230.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
2009 | 10 | 6 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2009 | 10 | 7 | 189.3878 | 15 | 174.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2009 | 10 | 8 | 256 | 15 | 241 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2009 | 10 | 9 | 173.7143 | 15 | 158.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2009 | 10 | 10 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
2009 | 10 | 11 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
2009 | 10 | 12 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
2009 | 10 | 13 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2009 | 10 | 14 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
2009 | 10 | 15 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
2009 | 10 | 16 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2009 | 10 | 17 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2009 | 10 | 18 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2009 | 10 | 19 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2009 | 10 | 20 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2009 | 10 | 21 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2009 | 10 | 22 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
2009 | 10 | 23 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2009 | 10 | 24 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2009 | 10 | 25 | 970.449 | 15 | 955.449 | 28.0591 | 139.3858 | 0.77441 | 27.2847 | 89.27% | 287.5192 | 270.2681 | 6486.4334
2009 | 10 | 26 | 484.5714 | 15 | 469.5714 | 29.0309 | 139.3858 | 0.77441 | 28.2564 | 89.27% | 297.7593 | 279.8938 | 6717.4503
2009 | 10 | 27 | 305.6327 | 15 | 290.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
2009 | 10 | 28 | 236.4082 | 15 | 221.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2009 | 10 | 29 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2009 | 10 | 30 | 158.0408 | 15 | 143.0408 | 29.6839 | 139.3858 | 0.77441 | 28.9095 | 89.27% | 304.6411 | 286.3626 | 6872.7036
2009 | 10 | 31 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
2009 | 11 | 1 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2009 | 11 | 2 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2009 | 11 | 3 | 163.2653 | 15 | 148.2653 | 29.6735 | 139.3858 | 0.77441 | 28.8991 | 89.27% | 304.531 | 286.2591 | 6870.2195
2009 | 11 | 4 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
2009 | 11 | 5 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
2009 | 11 | 6 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
2009 | 11 | 7 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
2009 | 11 | 8 | 107.102 | 15 | 92.102 | 29.7858 | 92.102 | 0.33812 | 29.4477 | 92.2% | 211.7751 | 199.0686 | 4777.6456
2009 | 11 | 9 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2009 | 11 | 10 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2009 | 11 | 11 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2009 | 11 | 12 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
2009 | 11 | 13 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2009 | 11 | 14 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
2009 | 11 | 15 | 1332.2449 | 15 | 1317.2449 | 27.3355 | 139.3858 | 0.77441 | 26.5611 | 89.27% | 279.8942 | 263.1005 | 6314.4127
2009 | 11 | 16 | 717.0612 | 15 | 702.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
2009 | 11 | 17 | 407.5102 | 15 | 392.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
2009 | 11 | 18 | 303.0204 | 15 | 288.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
2009 | 11 | 19 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2009 | 11 | 20 | 444.0816 | 15 | 429.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
2009 | 11 | 21 | 609.9592 | 15 | 594.9592 | 28.7801 | 139.3858 | 0.77441 | 28.0057 | 89.27% | 295.1167 | 277.4097 | 6657.833
2009 | 11 | 22 | 382.6939 | 15 | 367.6939 | 29.2346 | 139.3858 | 0.77441 | 28.4602 | 89.27% | 299.9064 | 281.9121 | 6765.8893
2009 | 11 | 23 | 297.7959 | 15 | 282.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
2009 | 11 | 24 | 254.6939 | 15 | 239.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2009 | 11 | 25 | 225.9592 | 15 | 210.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2009 | 11 | 26 | 216.8163 | 15 | 201.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2009 | 11 | 27 | 280.8163 | 15 | 265.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
2009 | 11 | 28 | 997.8776 | 15 | 982.8776 | 28.0042 | 139.3858 | 0.77441 | 27.2298 | 89.27% | 286.9411 | 269.7247 | 6473.3921
2009 | 11 | 29 | 583.8367 | 15 | 568.8367 | 28.8323 | 139.3858 | 0.77441 | 28.0579 | 89.27% | 295.6673 | 277.9272 | 6670.2533
2009 | 11 | 30 | 400.9796 | 15 | 385.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
2009 | 12 | 1 | 329.1429 | 5 | 324.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
2009 | 12 | 2 | 278.2041 | 5 | 273.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
2009 | 12 | 3 | 808.4898 | 5 | 803.4898 | 28.383 | 139.3858 | 0.77441 | 27.6086 | 89.27% | 290.9326 | 273.4766 | 6563.439
2009 | 12 | 4 | 933.8776 | 5 | 928.8776 | 28.1322 | 139.3858 | 0.77441 | 27.3578 | 89.27% | 288.29 | 270.9926 | 6503.8217
2009 | 12 | 5 | 495.0204 | 5 | 490.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
2009 | 12 | 6 | 384 | 5 | 379 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
2009 | 12 | 7 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
2009 | 12 | 8 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2009 | 12 | 9 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2009 | 12 | 10 | 233.7959 | 5 | 228.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2009 | 12 | 11 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2009 | 12 | 12 | 171.102 | 5 | 166.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2009 | 12 | 13 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2009 | 12 | 14 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2009 | 12 | 15 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2009 | 12 | 16 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2009 | 12 | 17 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2009 | 12 | 18 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2009 | 12 | 19 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2009 | 12 | 20 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2009 | 12 | 21 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2009 | 12 | 22 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2009 | 12 | 23 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2009 | 12 | 24 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2009 | 12 | 25 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2009 | 12 | 26 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2009 | 12 | 27 | 331.7551 | 5 | 326.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
2009 | 12 | 28 | 919.5102 | 5 | 914.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
2009 | 12 | 29 | 485.8776 | 5 | 480.8776 | 29.0282 | 139.3858 | 0.77441 | 28.2538 | 89.27% | 297.7318 | 279.8679 | 6716.8293
2009 | 12 | 30 | 301.7143 | 5 | 296.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2009 | 12 | 31 | 265.1429 | 5 | 260.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2010 | 1 | 1 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2010 | 1 | 2 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2010 | 1 | 3 | 202.449 | 5 | 197.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2010 | 1 | 4 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2010 | 1 | 5 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2010 | 1 | 6 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2010 | 1 | 7 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2010 | 1 | 8 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2010 | 1 | 9 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2010 | 1 | 10 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2010 | 1 | 11 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2010 | 1 | 12 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2010 | 1 | 13 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2010 | 1 | 14 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2010 | 1 | 15 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2010 | 1 | 16 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2010 | 1 | 17 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2010 | 1 | 18 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2010 | 1 | 19 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2010 | 1 | 20 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2010 | 1 | 21 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2010 | 1 | 22 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2010 | 1 | 23 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2010 | 1 | 24 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2010 | 1 | 25 | 223.3469 | 5 | 218.3469 | 29.5533 | 139.3858 | 0.77441 | 28.7789 | 89.27% | 303.2648 | 285.0689 | 6841.6529
2010 | 1 | 26 | 1684.898 | 5 | 1679.898 | 26.6302 | 139.3858 | 0.77441 | 25.8558 | 89.27% | 272.4618 | 256.1141 | 6146.7392
2010 | 1 | 27 | 988.7347 | 5 | 983.7347 | 28.0225 | 139.3858 | 0.77441 | 27.2481 | 89.27% | 287.1338 | 269.9058 | 6477.7392
2010 | 1 | 28 | 548.5714 | 5 | 543.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
2010 | 1 | 29 | 309.551 | 5 | 304.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
2010 | 1 | 30 | 239.0204 | 5 | 234.0204 | 29.522 | 139.3858 | 0.77441 | 28.7475 | 89.27% | 302.9344 | 284.7584 | 6834.2007
2010 | 1 | 31 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2010 | 2 | 1 | 184.1633 | 5 | 179.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2010 | 2 | 2 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2010 | 2 | 3 | 151.5102 | 5 | 146.5102 | 29.697 | 139.3858 | 0.77441 | 28.9226 | 89.27% | 304.7788 | 286.492 | 6875.8086
2010 | 2 | 4 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2010 | 2 | 5 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2010 | 2 | 6 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2010 | 2 | 7 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2010 | 2 | 8 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2010 | 2 | 9 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2010 | 2 | 10 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2010 | 2 | 11 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2010 | 2 | 12 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2010 | 2 | 13 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2010 | 2 | 14 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2010 | 2 | 15 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2010 | 2 | 16 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2010 | 2 | 17 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2010 | 2 | 18 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2010 | 2 | 19 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2010 | 2 | 20 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2010 | 2 | 21 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2010 | 2 | 22 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2010 | 2 | 23 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2010 | 2 | 24 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2010 | 2 | 25 | 186.7755 | 5 | 181.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2010 | 2 | 26 | 1039.6735 | 5 | 1034.6735 | 27.9207 | 139.3858 | 0.77441 | 27.1462 | 89.27% | 286.0603 | 268.8967 | 6453.5197
2010 | 2 | 27 | 882.9388 | 5 | 877.9388 | 28.2341 | 139.3858 | 0.77441 | 27.4597 | 89.27% | 289.3635 | 272.0017 | 6528.0413
2010 | 2 | 28 | 559.0204 | 5 | 554.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
2010 | 3 | 1 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
2010 | 3 | 2 | 440.1633 | 25 | 415.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
2010 | 3 | 3 | 384 | 25 | 359 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
2010 | 3 | 4 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2010 | 3 | 5 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
2010 | 3 | 6 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2010 | 3 | 7 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2010 | 3 | 8 | 329.1429 | 25 | 304.1429 | 29.3417 | 139.3858 | 0.77441 | 28.5673 | 89.27% | 301.0351 | 282.973 | 6791.3508
2010 | 3 | 9 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
2010 | 3 | 10 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2010 | 3 | 11 | 293.8776 | 25 | 268.8776 | 29.4122 | 139.3858 | 0.77441 | 28.6378 | 89.27% | 301.7783 | 283.6716 | 6808.1182
2010 | 3 | 12 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
2010 | 3 | 13 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
2010 | 3 | 14 | 322.6122 | 25 | 297.6122 | 29.3548 | 139.3858 | 0.77441 | 28.5804 | 89.27% | 301.1727 | 283.1023 | 6794.4559
2010 | 3 | 15 | 884.2449 | 25 | 859.2449 | 28.2315 | 139.3858 | 0.77441 | 27.4571 | 89.27% | 289.336 | 271.9758 | 6527.4202
2010 | 3 | 16 | 719.6735 | 25 | 694.6735 | 28.5607 | 139.3858 | 0.77441 | 27.7862 | 89.27% | 292.8044 | 275.2362 | 6605.6679
2010 | 3 | 17 | 633.4694 | 25 | 608.4694 | 28.7331 | 139.3858 | 0.77441 | 27.9587 | 89.27% | 294.6212 | 276.9439 | 6646.6548
2010 | 3 | 18 | 689.6327 | 25 | 664.6327 | 28.6207 | 139.3858 | 0.77441 | 27.8463 | 89.27% | 293.4376 | 275.8313 | 6619.9512
2010 | 3 | 19 | 784.9796 | 25 | 759.9796 | 28.43 | 139.3858 | 0.77441 | 27.6556 | 89.27% | 291.4281 | 273.9424 | 6574.6172
2010 | 3 | 20 | 820.2449 | 25 | 795.2449 | 28.3595 | 139.3858 | 0.77441 | 27.5851 | 89.27% | 290.6848 | 273.2437 | 6557.8499
2010 | 3 | 21 | 809.7959 | 25 | 784.7959 | 28.3804 | 139.3858 | 0.77441 | 27.606 | 89.27% | 290.9051 | 273.4507 | 6562.818
2010 | 3 | 22 | 561.6327 | 25 | 536.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
2010 | 3 | 23 | 1247.3469 | 25 | 1222.3469 | 27.5053 | 139.3858 | 0.77441 | 26.7309 | 89.27% | 281.6834 | 264.7824 | 6354.7786
2010 | 3 | 24 | 2573.0612 | 25 | 2548.0612 | 24.8539 | 0 | 0 | 24.8539 | 0% | 0 | 0 | 0
2010 | 3 | 25 | 1345.3061 | 25 | 1320.3061 | 27.3094 | 139.3858 | 0.77441 | 26.535 | 89.27% | 279.6189 | 262.8418 | 6308.2026
2010 | 3 | 26 | 839.8367 | 25 | 814.8367 | 28.3203 | 139.3858 | 0.77441 | 27.5459 | 89.27% | 290.2719 | 272.8556 | 6548.5347
2010 | 3 | 27 | 564.2449 | 25 | 539.2449 | 28.8715 | 139.3858 | 0.77441 | 28.0971 | 89.27% | 296.0802 | 278.3154 | 6679.5685
2010 | 3 | 28 | 444.0816 | 25 | 419.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
2010 | 3 | 29 | 969.1429 | 25 | 944.1429 | 28.0617 | 139.3858 | 0.77441 | 27.2873 | 89.27% | 287.5467 | 270.2939 | 6487.0544
2010 | 3 | 30 | 1880.8163 | 25 | 1855.8163 | 26.2384 | 139.3858 | 0.77441 | 25.464 | 89.27% | 268.3328 | 252.2328 | 6053.5872
2010 | 3 | 31 | 1906.9388 | 25 | 1881.9388 | 26.1861 | 139.3858 | 0.77441 | 25.4117 | 89.27% | 267.7822 | 251.7153 | 6041.1669
2010 | 4 | 1 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
2010 | 4 | 2 | 889.4694 | 25 | 864.4694 | 28.2211 | 139.3858 | 0.77441 | 27.4467 | 89.27% | 289.2259 | 271.8723 | 6524.9362
2010 | 4 | 3 | 653.0612 | 25 | 628.0612 | 28.6939 | 139.3858 | 0.77441 | 27.9195 | 89.27% | 294.2083 | 276.5558 | 6637.3396
2010 | 4 | 4 | 506.7755 | 25 | 481.7755 | 28.9864 | 139.3858 | 0.77441 | 28.212 | 89.27% | 297.2914 | 279.4539 | 6706.893
2010 | 4 | 5 | 408.8163 | 25 | 383.8163 | 29.1824 | 139.3858 | 0.77441 | 28.408 | 89.27% | 299.3559 | 281.3945 | 6753.469
2010 | 4 | 6 | 347.4286 | 25 | 322.4286 | 29.3051 | 139.3858 | 0.77441 | 28.5307 | 89.27% | 300.6497 | 282.6107 | 6782.6566
2010 | 4 | 7 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
2010 | 4 | 8 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
2010 | 4 | 9 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
2010 | 4 | 10 | 620.4082 | 25 | 595.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
2010 | 4 | 11 | 437.551 | 25 | 412.551 | 29.1249 | 139.3858 | 0.77441 | 28.3505 | 89.27% | 298.7503 | 280.8253 | 6739.8067
2010 | 4 | 12 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2010 | 4 | 13 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2010 | 4 | 14 | 250.7755 | 25 | 225.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2010 | 4 | 15 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2010 | 4 | 16 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2010 | 4 | 17 | 321.3061 | 25 | 296.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
2010 | 4 | 18 | 373.551 | 25 | 348.551 | 29.2529 | 139.3858 | 0.77441 | 28.4785 | 89.27% | 300.0991 | 282.0932 | 6770.2364
2010 | 4 | 19 | 381.3878 | 25 | 356.3878 | 29.2372 | 139.3858 | 0.77441 | 28.4628 | 89.27% | 299.934 | 281.9379 | 6766.5103
2010 | 4 | 20 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
2010 | 4 | 21 | 276.898 | 25 | 251.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2010 | 4 | 22 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2010 | 4 | 23 | 283.4286 | 25 | 258.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2010 | 4 | 24 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2010 | 4 | 25 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2010 | 4 | 26 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2010 | 4 | 27 | 168.4898 | 25 | 143.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2010 | 4 | 28 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
2010 | 4 | 29 | 592.9796 | 25 | 567.9796 | 28.814 | 139.3858 | 0.77441 | 28.0396 | 89.27% | 295.4746 | 277.7461 | 6665.9062
2010 | 4 | 30 | 395.7551 | 25 | 370.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
2010 | 5 | 1 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2010 | 5 | 2 | 254.6939 | 25 | 229.6939 | 29.4906 | 139.3858 | 0.77441 | 28.7162 | 89.27% | 302.6041 | 284.4479 | 6826.7486
2010 | 5 | 3 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2010 | 5 | 4 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2010 | 5 | 5 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2010 | 5 | 6 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2010 | 5 | 7 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2010 | 5 | 8 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2010 | 5 | 9 | 394.449 | 25 | 369.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
2010 | 5 | 10 | 287.3469 | 25 | 262.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2010 | 5 | 11 | 228.5714 | 25 | 203.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2010 | 5 | 12 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2010 | 5 | 13 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
2010 | 5 | 14 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
2010 | 5 | 15 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2010 | 5 | 16 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2010 | 5 | 17 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2010 | 5 | 18 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2010 | 5 | 19 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2010 | 5 | 20 | 161.9592 | 25 | 136.9592 | 29.6761 | 136.9592 | 0.74768 | 28.9284 | 90.08% | 302.2509 | 284.1159 | 6818.7805
2010 | 5 | 21 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2010 | 5 | 22 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2010 | 5 | 23 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2010 | 5 | 24 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2010 | 5 | 25 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2010 | 5 | 26 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2010 | 5 | 27 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2010 | 5 | 28 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
2010 | 5 | 29 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2010 | 5 | 30 | 39.1837 | 25 | 14.1837 | 29.9216 | 14.1837 | 0.0080188 | 29.9136 | 70.08% | 25.1811 | 23.6703 | 568.0865
2010 | 5 | 31 | 35.2653 | 25 | 10.2653 | 29.9295 | 10.2653 | 0.0042003 | 29.9253 | 40.05% | 10.4192 | 9.7941 | 235.0581
2010 | 6 | 1 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2010 | 6 | 2 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
2010 | 6 | 3 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
2010 | 6 | 4 | 37.8776 | 25 | 12.8776 | 29.9242 | 12.8776 | 0.00661 | 29.9176 | 40.05% | 13.0673 | 12.2833 | 294.7989
2010 | 6 | 5 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2010 | 6 | 6 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
2010 | 6 | 7 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2010 | 6 | 8 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2010 | 6 | 9 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2010 | 6 | 10 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2010 | 6 | 11 | 109.7143 | 25 | 84.7143 | 29.7806 | 84.7143 | 0.28605 | 29.4945 | 92.11% | 194.9074 | 183.213 | 4397.1116
2010 | 6 | 12 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2010 | 6 | 13 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2010 | 6 | 14 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2010 | 6 | 15 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2010 | 6 | 16 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2010 | 6 | 17 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2010 | 6 | 18 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2010 | 6 | 19 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2010 | 6 | 20 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2010 | 6 | 21 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2010 | 6 | 22 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2010 | 6 | 23 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2010 | 6 | 24 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2010 | 6 | 25 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2010 | 6 | 26 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2010 | 6 | 27 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2010 | 6 | 28 | 122.7755 | 25 | 97.7755 | 29.7544 | 97.7755 | 0.38106 | 29.3734 | 92.08% | 223.9614 | 210.5237 | 5052.5684
2010 | 6 | 29 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
2010 | 6 | 30 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2010 | 7 | 1 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2010 | 7 | 2 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2010 | 7 | 3 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2010 | 7 | 4 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2010 | 7 | 5 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2010 | 7 | 6 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2010 | 7 | 7 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2010 | 7 | 8 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2010 | 7 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2010 | 7 | 10 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2010 | 7 | 11 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2010 | 7 | 12 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2010 | 7 | 13 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2010 | 7 | 14 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2010 | 7 | 15 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2010 | 7 | 16 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2010 | 7 | 17 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2010 | 7 | 18 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2010 | 7 | 19 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2010 | 7 | 20 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2010 | 7 | 21 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2010 | 7 | 22 | 224.6531 | 5 | 219.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2010 | 7 | 23 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2010 | 7 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2010 | 7 | 25 | 52.2449 | 5 | 47.2449 | 29.8955 | 47.2449 | 0.08897 | 29.8065 | 88.6% | 105.6632 | 99.3234 | 2383.7623
2010 | 7 | 26 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2010 | 7 | 27 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2010 | 7 | 28 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2010 | 7 | 29 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2010 | 7 | 30 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2010 | 7 | 31 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2010 | 8 | 1 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2010 | 8 | 2 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
2010 | 8 | 3 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
2010 | 8 | 4 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2010 | 8 | 5 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2010 | 8 | 6 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2010 | 8 | 7 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2010 | 8 | 8 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2010 | 8 | 9 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2010 | 8 | 10 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2010 | 8 | 11 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2010 | 8 | 12 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2010 | 8 | 13 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
2010 | 8 | 14 | 11.3633 | 5 | 6.3633 | 29.9773 | 6.3633 | 0.001614 | 29.9757 | 40.05% | 6.4696 | 6.0814 | 145.9533
2010 | 8 | 15 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
2010 | 8 | 16 | 10.3184 | 5 | 5.3184 | 29.9794 | 0 | 0 | 29.9794 | 0% | 0 | 0 | 0
2010 | 8 | 17 | 12.2776 | 5 | 7.2776 | 29.9754 | 7.2776 | 0.0021111 | 29.9733 | 40.05% | 7.3985 | 6.9546 | 166.9112
2010 | 8 | 18 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
2010 | 8 | 19 | 10.1878 | 5 | 5.1878 | 29.9796 | 0 | 0 | 29.9796 | 0% | 0 | 0 | 0
2010 | 8 | 20 | 9.4041 | 5 | 4.4041 | 29.9812 | 0 | 0 | 29.9812 | 0% | 0 | 0 | 0
2010 | 8 | 21 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2010 | 8 | 22 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2010 | 8 | 23 | 10.0571 | 5 | 5.0571 | 29.9799 | 0 | 0 | 29.9799 | 0% | 0 | 0 | 0
2010 | 8 | 24 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
2010 | 8 | 25 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2010 | 8 | 26 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2010 | 8 | 27 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2010 | 8 | 28 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2010 | 8 | 29 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2010 | 8 | 30 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2010 | 8 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2010 | 9 | 1 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2010 | 9 | 2 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2010 | 9 | 3 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2010 | 9 | 4 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2010 | 9 | 5 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2010 | 9 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2010 | 9 | 7 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2010 | 9 | 8 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2010 | 9 | 9 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2010 | 9 | 10 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2010 | 9 | 11 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2010 | 9 | 12 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
2010 | 9 | 13 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
2010 | 9 | 14 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
2010 | 9 | 15 | 11.2327 | 15 | 0 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
2010 | 9 | 16 | 10.7102 | 15 | 0 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
2010 | 9 | 17 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2010 | 9 | 18 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2010 | 9 | 19 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2010 | 9 | 20 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2010 | 9 | 21 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2010 | 9 | 22 | 12.6694 | 15 | 0 | 29.9747 | 0 | 0 | 29.9747 | 0% | 0 | 0 | 0
2010 | 9 | 23 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
2010 | 9 | 24 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2010 | 9 | 25 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2010 | 9 | 26 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2010 | 9 | 27 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2010 | 9 | 28 | 22.2041 | 15 | 7.2041 | 29.9556 | 7.2041 | 0.0020687 | 29.9535 | 40.05% | 7.319 | 6.8799 | 165.117
2010 | 9 | 29 | 31.3469 | 15 | 16.3469 | 29.9373 | 16.3469 | 0.010651 | 29.9267 | 70.08% | 29.0344 | 27.2923 | 655.0153
2010 | 9 | 30 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2010 | 10 | 1 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
2010 | 10 | 2 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2010 | 10 | 3 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
2010 | 10 | 4 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2010 | 10 | 5 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2010 | 10 | 6 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2010 | 10 | 7 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
2010 | 10 | 8 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
2010 | 10 | 9 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2010 | 10 | 10 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2010 | 10 | 11 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2010 | 10 | 12 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2010 | 10 | 13 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2010 | 10 | 14 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
2010 | 10 | 15 | 308.2449 | 15 | 293.2449 | 29.3835 | 139.3858 | 0.77441 | 28.6091 | 89.27% | 301.4755 | 283.387 | 6801.287
2010 | 10 | 16 | 502.8571 | 15 | 487.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
2010 | 10 | 17 | 263.8367 | 15 | 248.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
2010 | 10 | 18 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2010 | 10 | 19 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
2010 | 10 | 20 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2010 | 10 | 21 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
2010 | 10 | 22 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2010 | 10 | 23 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
2010 | 10 | 24 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2010 | 10 | 25 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2010 | 10 | 26 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
2010 | 10 | 27 | 227.2653 | 15 | 212.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2010 | 10 | 28 | 365.7143 | 15 | 350.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
2010 | 10 | 29 | 229.8776 | 15 | 214.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2010 | 10 | 30 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2010 | 10 | 31 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
2010 | 11 | 1 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
2010 | 11 | 2 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2010 | 11 | 3 | 86.2041 | 15 | 71.2041 | 29.8276 | 71.2041 | 0.20209 | 29.6255 | 91.6% | 163.6401 | 153.8217 | 3691.7207
2010 | 11 | 4 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
2010 | 11 | 5 | 522.449 | 15 | 507.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
2010 | 11 | 6 | 547.2653 | 15 | 532.2653 | 28.9055 | 139.3858 | 0.77441 | 28.1311 | 89.27% | 296.438 | 278.6517 | 6687.6416
2010 | 11 | 7 | 301.7143 | 15 | 286.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2010 | 11 | 8 | 489.7959 | 15 | 474.7959 | 29.0204 | 139.3858 | 0.77441 | 28.246 | 89.27% | 297.6492 | 279.7903 | 6714.9662
2010 | 11 | 9 | 566.8571 | 15 | 551.8571 | 28.8663 | 139.3858 | 0.77441 | 28.0919 | 89.27% | 296.0251 | 278.2636 | 6678.3264
2010 | 11 | 10 | 479.3469 | 15 | 464.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
2010 | 11 | 11 | 321.3061 | 15 | 306.3061 | 29.3574 | 139.3858 | 0.77441 | 28.583 | 89.27% | 301.2002 | 283.1282 | 6795.0769
2010 | 11 | 12 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2010 | 11 | 13 | 195.9184 | 15 | 180.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2010 | 11 | 14 | 172.4082 | 15 | 157.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2010 | 11 | 15 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
2010 | 11 | 16 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
2010 | 11 | 17 | 410.1224 | 15 | 395.1224 | 29.1798 | 139.3858 | 0.77441 | 28.4053 | 89.27% | 299.3284 | 281.3687 | 6752.848
2010 | 11 | 18 | 615.1837 | 15 | 600.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
2010 | 11 | 19 | 338.2857 | 15 | 323.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
2010 | 11 | 20 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2010 | 11 | 21 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2010 | 11 | 22 | 168.4898 | 15 | 153.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2010 | 11 | 23 | 161.9592 | 15 | 146.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2010 | 11 | 24 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2010 | 11 | 25 | 135.8367 | 15 | 120.8367 | 29.7283 | 120.8367 | 0.58201 | 29.1463 | 91.08% | 271.6623 | 255.3625 | 6128.7005
2010 | 11 | 26 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
2010 | 11 | 27 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
2010 | 11 | 28 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
2010 | 11 | 29 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2010 | 11 | 30 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2010 | 12 | 1 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2010 | 12 | 2 | 953.4694 | 5 | 948.4694 | 28.0931 | 139.3858 | 0.77441 | 27.3187 | 89.27% | 287.8771 | 270.6044 | 6494.5065
2010 | 12 | 3 | 590.3673 | 5 | 585.3673 | 28.8193 | 139.3858 | 0.77441 | 28.0449 | 89.27% | 295.5296 | 277.7978 | 6667.1482
2010 | 12 | 4 | 372.2449 | 5 | 367.2449 | 29.2555 | 139.3858 | 0.77441 | 28.4811 | 89.27% | 300.1267 | 282.1191 | 6770.8574
2010 | 12 | 5 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
2010 | 12 | 6 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2010 | 12 | 7 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2010 | 12 | 8 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
2010 | 12 | 9 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2010 | 12 | 10 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2010 | 12 | 11 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2010 | 12 | 12 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
2010 | 12 | 13 | 2977.9592 | 5 | 2972.9592 | 24.0441 | 0 | 0 | 24.0441 | 0% | 0 | 0 | 0
2010 | 12 | 14 | 1959.1837 | 5 | 1954.1837 | 26.0816 | 139.3858 | 0.77441 | 25.3072 | 89.27% | 266.6811 | 250.6803 | 6016.3264
2010 | 12 | 15 | 996.5714 | 5 | 991.5714 | 28.0069 | 139.3858 | 0.77441 | 27.2324 | 89.27% | 286.9687 | 269.7505 | 6474.0131
2010 | 12 | 16 | 576 | 5 | 571 | 28.848 | 139.3858 | 0.77441 | 28.0736 | 89.27% | 295.8324 | 278.0825 | 6673.9793
2010 | 12 | 17 | 398.3673 | 5 | 393.3673 | 29.2033 | 139.3858 | 0.77441 | 28.4289 | 89.27% | 299.5761 | 281.6015 | 6758.4371
2010 | 12 | 18 | 297.7959 | 5 | 292.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
2010 | 12 | 19 | 259.9184 | 5 | 254.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2010 | 12 | 20 | 227.2653 | 5 | 222.2653 | 29.5455 | 139.3858 | 0.77441 | 28.7711 | 89.27% | 303.1822 | 284.9912 | 6839.7899
2010 | 12 | 21 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2010 | 12 | 22 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2010 | 12 | 23 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2010 | 12 | 24 | 175.0204 | 5 | 170.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2010 | 12 | 25 | 164.5714 | 5 | 159.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2010 | 12 | 26 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2010 | 12 | 27 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2010 | 12 | 28 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2010 | 12 | 29 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2010 | 12 | 30 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2010 | 12 | 31 | 125.3878 | 5 | 120.3878 | 29.7492 | 120.3878 | 0.57769 | 29.1715 | 91.08% | 270.887 | 254.6338 | 6111.2112
2011 | 1 | 1 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2011 | 1 | 2 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2011 | 1 | 3 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2011 | 1 | 4 | 172.4082 | 5 | 167.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2011 | 1 | 5 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
2011 | 1 | 6 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2011 | 1 | 7 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2011 | 1 | 8 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2011 | 1 | 9 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2011 | 1 | 10 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2011 | 1 | 11 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2011 | 1 | 12 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2011 | 1 | 13 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2011 | 1 | 14 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2011 | 1 | 15 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2011 | 1 | 16 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2011 | 1 | 17 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2011 | 1 | 18 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2011 | 1 | 19 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2011 | 1 | 20 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2011 | 1 | 21 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2011 | 1 | 22 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2011 | 1 | 23 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2011 | 1 | 24 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2011 | 1 | 25 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2011 | 1 | 26 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2011 | 1 | 27 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2011 | 1 | 28 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2011 | 1 | 29 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2011 | 1 | 30 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2011 | 1 | 31 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2011 | 2 | 1 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2011 | 2 | 2 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2011 | 2 | 3 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2011 | 2 | 4 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2011 | 2 | 5 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2011 | 2 | 6 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2011 | 2 | 7 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2011 | 2 | 8 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2011 | 2 | 9 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2011 | 2 | 10 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2011 | 2 | 11 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2011 | 2 | 12 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2011 | 2 | 13 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2011 | 2 | 14 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2011 | 2 | 15 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2011 | 2 | 16 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2011 | 2 | 17 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2011 | 2 | 18 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2011 | 2 | 19 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2011 | 2 | 20 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2011 | 2 | 21 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2011 | 2 | 22 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2011 | 2 | 23 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2011 | 2 | 24 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2011 | 2 | 25 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2011 | 2 | 26 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2011 | 2 | 27 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2011 | 2 | 28 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2011 | 3 | 1 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2011 | 3 | 2 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2011 | 3 | 3 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2011 | 3 | 4 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2011 | 3 | 5 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2011 | 3 | 6 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2011 | 3 | 7 | 902.5306 | 25 | 877.5306 | 28.1949 | 139.3858 | 0.77441 | 27.4205 | 89.27% | 288.9506 | 271.6136 | 6518.7261
2011 | 3 | 8 | 1247.3469 | 25 | 1222.3469 | 27.5053 | 139.3858 | 0.77441 | 26.7309 | 89.27% | 281.6834 | 264.7824 | 6354.7786
2011 | 3 | 9 | 756.2449 | 25 | 731.2449 | 28.4875 | 139.3858 | 0.77441 | 27.7131 | 89.27% | 292.0337 | 274.5116 | 6588.2795
2011 | 3 | 10 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
2011 | 3 | 11 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
2011 | 3 | 12 | 943.0204 | 25 | 918.0204 | 28.114 | 139.3858 | 0.77441 | 27.3395 | 89.27% | 288.0973 | 270.8114 | 6499.4746
2011 | 3 | 13 | 828.0816 | 25 | 803.0816 | 28.3438 | 139.3858 | 0.77441 | 27.5694 | 89.27% | 290.5197 | 273.0885 | 6554.1238
2011 | 3 | 14 | 632.1633 | 25 | 607.1633 | 28.7357 | 139.3858 | 0.77441 | 27.9613 | 89.27% | 294.6487 | 276.9698 | 6647.2758
2011 | 3 | 15 | 483.2653 | 25 | 458.2653 | 29.0335 | 139.3858 | 0.77441 | 28.2591 | 89.27% | 297.7868 | 279.9196 | 6718.0713
2011 | 3 | 16 | 416.6531 | 25 | 391.6531 | 29.1667 | 139.3858 | 0.77441 | 28.3923 | 89.27% | 299.1907 | 281.2393 | 6749.7429
2011 | 3 | 17 | 384 | 25 | 359 | 29.232 | 139.3858 | 0.77441 | 28.4576 | 89.27% | 299.8789 | 281.8862 | 6765.2683
2011 | 3 | 18 | 585.1429 | 25 | 560.1429 | 28.8297 | 139.3858 | 0.77441 | 28.0553 | 89.27% | 295.6397 | 277.9013 | 6669.6323
2011 | 3 | 19 | 1007.0204 | 25 | 982.0204 | 27.986 | 139.3858 | 0.77441 | 27.2115 | 89.27% | 286.7484 | 269.5435 | 6469.045
2011 | 3 | 20 | 679.1837 | 25 | 654.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
2011 | 3 | 21 | 522.449 | 25 | 497.449 | 28.9551 | 139.3858 | 0.77441 | 28.1807 | 89.27% | 296.961 | 279.1434 | 6699.4409
2011 | 3 | 22 | 429.7143 | 25 | 404.7143 | 29.1406 | 139.3858 | 0.77441 | 28.3662 | 89.27% | 298.9155 | 280.9805 | 6743.5328
2011 | 3 | 23 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
2011 | 3 | 24 | 303.0204 | 25 | 278.0204 | 29.394 | 139.3858 | 0.77441 | 28.6195 | 89.27% | 301.5856 | 283.4905 | 6803.7711
2011 | 3 | 25 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2011 | 3 | 26 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2011 | 3 | 27 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2011 | 3 | 28 | 198.5306 | 25 | 173.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2011 | 3 | 29 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2011 | 3 | 30 | 197.2245 | 25 | 172.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2011 | 3 | 31 | 231.1837 | 25 | 206.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2011 | 4 | 1 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
2011 | 4 | 2 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2011 | 4 | 3 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
2011 | 4 | 4 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2011 | 4 | 5 | 389.2245 | 25 | 364.2245 | 29.2216 | 139.3858 | 0.77441 | 28.4471 | 89.27% | 299.7688 | 281.7827 | 6762.7842
2011 | 4 | 6 | 432.3265 | 25 | 407.3265 | 29.1353 | 139.3858 | 0.77441 | 28.3609 | 89.27% | 298.8604 | 280.9288 | 6742.2908
2011 | 4 | 7 | 400.9796 | 25 | 375.9796 | 29.198 | 139.3858 | 0.77441 | 28.4236 | 89.27% | 299.5211 | 281.5498 | 6757.1951
2011 | 4 | 8 | 428.4082 | 25 | 403.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
2011 | 4 | 9 | 501.551 | 25 | 476.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
2011 | 4 | 10 | 687.0204 | 25 | 662.0204 | 28.626 | 139.3858 | 0.77441 | 27.8515 | 89.27% | 293.4926 | 275.8831 | 6621.1932
2011 | 4 | 11 | 1371.4286 | 25 | 1346.4286 | 27.2571 | 139.3858 | 0.77441 | 26.4827 | 89.27% | 279.0684 | 262.3243 | 6295.7823
2011 | 4 | 12 | 1737.1429 | 25 | 1712.1429 | 26.5257 | 139.3858 | 0.77441 | 25.7513 | 89.27% | 271.3608 | 255.0791 | 6121.8986
2011 | 4 | 13 | 1462.8571 | 25 | 1437.8571 | 27.0743 | 139.3858 | 0.77441 | 26.2999 | 89.27% | 277.1415 | 260.513 | 6252.3114
2011 | 4 | 14 | 1567.3469 | 25 | 1542.3469 | 26.8653 | 139.3858 | 0.77441 | 26.0909 | 89.27% | 274.9393 | 258.4429 | 6202.6304
2011 | 4 | 15 | 1155.9184 | 25 | 1130.9184 | 27.6882 | 139.3858 | 0.77441 | 26.9138 | 89.27% | 283.6104 | 266.5937 | 6398.2495
2011 | 4 | 16 | 760.1633 | 25 | 735.1633 | 28.4797 | 139.3858 | 0.77441 | 27.7053 | 89.27% | 291.9511 | 274.434 | 6586.4165
2011 | 4 | 17 | 2181.2245 | 25 | 2156.2245 | 25.6376 | 139.3858 | 0.77441 | 24.8631 | 89.27% | 262.0015 | 246.2814 | 5910.7542
2011 | 4 | 18 | 1867.7551 | 25 | 1842.7551 | 26.2645 | 139.3858 | 0.77441 | 25.4901 | 89.27% | 268.608 | 252.4916 | 6059.7973
2011 | 4 | 19 | 1009.6327 | 25 | 984.6327 | 27.9807 | 139.3858 | 0.77441 | 27.2063 | 89.27% | 286.6934 | 269.4918 | 6467.803
2011 | 4 | 20 | 771.9184 | 25 | 746.9184 | 28.4562 | 139.3858 | 0.77441 | 27.6818 | 89.27% | 291.7033 | 274.2011 | 6580.8274
2011 | 4 | 21 | 634.7755 | 25 | 609.7755 | 28.7304 | 139.3858 | 0.77441 | 27.956 | 89.27% | 294.5937 | 276.9181 | 6646.0338
2011 | 4 | 22 | 487.1837 | 25 | 462.1837 | 29.0256 | 139.3858 | 0.77441 | 28.2512 | 89.27% | 297.7043 | 279.842 | 6716.2082
2011 | 4 | 23 | 438.8571 | 25 | 413.8571 | 29.1223 | 139.3858 | 0.77441 | 28.3479 | 89.27% | 298.7228 | 280.7994 | 6739.1857
2011 | 4 | 24 | 514.6122 | 25 | 489.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
2011 | 4 | 25 | 450.6122 | 25 | 425.6122 | 29.0988 | 139.3858 | 0.77441 | 28.3244 | 89.27% | 298.475 | 280.5665 | 6733.5966
2011 | 4 | 26 | 643.9184 | 25 | 618.9184 | 28.7122 | 139.3858 | 0.77441 | 27.9378 | 89.27% | 294.401 | 276.7369 | 6641.6867
2011 | 4 | 27 | 679.1837 | 25 | 654.1837 | 28.6416 | 139.3858 | 0.77441 | 27.8672 | 89.27% | 293.6578 | 276.0383 | 6624.9193
2011 | 4 | 28 | 525.0612 | 25 | 500.0612 | 28.9499 | 139.3858 | 0.77441 | 28.1755 | 89.27% | 296.906 | 279.0916 | 6698.1989
2011 | 4 | 29 | 527.6735 | 25 | 502.6735 | 28.9447 | 139.3858 | 0.77441 | 28.1702 | 89.27% | 296.8509 | 279.0399 | 6696.9568
2011 | 4 | 30 | 415.3469 | 25 | 390.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
2011 | 5 | 1 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2011 | 5 | 2 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
2011 | 5 | 3 | 236.4082 | 25 | 211.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2011 | 5 | 4 | 242.9388 | 25 | 217.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2011 | 5 | 5 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
2011 | 5 | 6 | 286.0408 | 25 | 261.0408 | 29.4279 | 139.3858 | 0.77441 | 28.6535 | 89.27% | 301.9435 | 283.8268 | 6811.8443
2011 | 5 | 7 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2011 | 5 | 8 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2011 | 5 | 9 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2011 | 5 | 10 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
2011 | 5 | 11 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
2011 | 5 | 12 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2011 | 5 | 13 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2011 | 5 | 14 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2011 | 5 | 15 | 291.2653 | 25 | 266.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
2011 | 5 | 16 | 979.5918 | 25 | 954.5918 | 28.0408 | 139.3858 | 0.77441 | 27.2664 | 89.27% | 287.3265 | 270.0869 | 6482.0863
2011 | 5 | 17 | 632.1633 | 25 | 607.1633 | 28.7357 | 139.3858 | 0.77441 | 27.9613 | 89.27% | 294.6487 | 276.9698 | 6647.2758
2011 | 5 | 18 | 459.7551 | 25 | 434.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
2011 | 5 | 19 | 548.5714 | 25 | 523.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
2011 | 5 | 20 | 701.3878 | 25 | 676.3878 | 28.5972 | 139.3858 | 0.77441 | 27.8228 | 89.27% | 293.1898 | 275.5984 | 6614.3621
2011 | 5 | 21 | 527.6735 | 25 | 502.6735 | 28.9447 | 139.3858 | 0.77441 | 28.1702 | 89.27% | 296.8509 | 279.0399 | 6696.9568
2011 | 5 | 22 | 468.898 | 25 | 443.898 | 29.0622 | 139.3858 | 0.77441 | 28.2878 | 89.27% | 298.0896 | 280.2043 | 6724.9024
2011 | 5 | 23 | 416.6531 | 25 | 391.6531 | 29.1667 | 139.3858 | 0.77441 | 28.3923 | 89.27% | 299.1907 | 281.2393 | 6749.7429
2011 | 5 | 24 | 416.6531 | 25 | 391.6531 | 29.1667 | 139.3858 | 0.77441 | 28.3923 | 89.27% | 299.1907 | 281.2393 | 6749.7429
2011 | 5 | 25 | 339.5918 | 25 | 314.5918 | 29.3208 | 139.3858 | 0.77441 | 28.5464 | 89.27% | 300.8148 | 282.7659 | 6786.3827
2011 | 5 | 26 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2011 | 5 | 27 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2011 | 5 | 28 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2011 | 5 | 29 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2011 | 5 | 30 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2011 | 5 | 31 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2011 | 6 | 1 | 135.8367 | 25 | 110.8367 | 29.7283 | 110.8367 | 0.48967 | 29.2387 | 91.77% | 251.8637 | 236.7519 | 5682.0448
2011 | 6 | 2 | 120.1633 | 25 | 95.1633 | 29.7597 | 95.1633 | 0.36097 | 29.3987 | 92.2% | 218.45 | 205.343 | 4928.2322
2011 | 6 | 3 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2011 | 6 | 4 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2011 | 6 | 5 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2011 | 6 | 6 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2011 | 6 | 7 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2011 | 6 | 8 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2011 | 6 | 9 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2011 | 6 | 10 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2011 | 6 | 11 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2011 | 6 | 12 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2011 | 6 | 13 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2011 | 6 | 14 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2011 | 6 | 15 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2011 | 6 | 16 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2011 | 6 | 17 | 45.7143 | 25 | 20.7143 | 29.9086 | 20.7143 | 0.017103 | 29.8915 | 70.08% | 36.7481 | 34.5432 | 829.0373
2011 | 6 | 18 | 50.9388 | 25 | 25.9388 | 29.8981 | 25.9388 | 0.026818 | 29.8713 | 80.09% | 52.554 | 49.4007 | 1185.6178
2011 | 6 | 19 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2011 | 6 | 20 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2011 | 6 | 21 | 36.5714 | 25 | 11.5714 | 29.9269 | 11.5714 | 0.0053371 | 29.9215 | 40.05% | 11.7435 | 11.0389 | 264.9329
2011 | 6 | 22 | 32.6531 | 25 | 7.6531 | 29.9347 | 7.6531 | 0.0023346 | 29.9324 | 40.05% | 7.7697 | 7.3035 | 175.2837
2011 | 6 | 23 | 33.9592 | 25 | 8.9592 | 29.9321 | 8.9592 | 0.0031994 | 29.9289 | 40.05% | 9.0946 | 8.549 | 205.1749
2011 | 6 | 24 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2011 | 6 | 25 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2011 | 6 | 26 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2011 | 6 | 27 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2011 | 6 | 28 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2011 | 6 | 29 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2011 | 6 | 30 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2011 | 7 | 1 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2011 | 7 | 2 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2011 | 7 | 3 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2011 | 7 | 4 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2011 | 7 | 5 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2011 | 7 | 6 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2011 | 7 | 7 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2011 | 7 | 8 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2011 | 7 | 9 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2011 | 7 | 10 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2011 | 7 | 11 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2011 | 7 | 12 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2011 | 7 | 13 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2011 | 7 | 14 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2011 | 7 | 15 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2011 | 7 | 16 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2011 | 7 | 17 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2011 | 7 | 18 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2011 | 7 | 19 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2011 | 7 | 20 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2011 | 7 | 21 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2011 | 7 | 22 | 12.5388 | 5 | 7.5388 | 29.9749 | 7.5388 | 0.0022654 | 29.9727 | 40.05% | 7.6639 | 7.2041 | 172.8985
2011 | 7 | 23 | 11.2327 | 5 | 6.2327 | 29.9775 | 0 | 0 | 29.9775 | 0% | 0 | 0 | 0
2011 | 7 | 24 | 9.9265 | 5 | 4.9265 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
2011 | 7 | 25 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2011 | 7 | 26 | 12.0163 | 5 | 7.0163 | 29.976 | 7.0163 | 0.0019622 | 29.974 | 40.05% | 7.1331 | 6.7052 | 160.9236
2011 | 7 | 27 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2011 | 7 | 28 | 39.1837 | 5 | 34.1837 | 29.9216 | 34.1837 | 0.046577 | 29.8751 | 80.09% | 69.2675 | 65.1114 | 1562.6744
2011 | 7 | 29 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2011 | 7 | 30 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2011 | 7 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2011 | 8 | 1 | 18.2857 | 5 | 13.2857 | 29.9634 | 13.2857 | 0.0070356 | 29.9564 | 40.05% | 13.499 | 12.689 | 304.5367
2011 | 8 | 2 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2011 | 8 | 3 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2011 | 8 | 4 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2011 | 8 | 5 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2011 | 8 | 6 | 12.9306 | 5 | 7.9306 | 29.9741 | 7.9306 | 0.002507 | 29.9716 | 40.05% | 8.062 | 7.5783 | 181.8789
2011 | 8 | 7 | 12.6694 | 5 | 7.6694 | 29.9747 | 7.6694 | 0.0023445 | 29.9723 | 40.05% | 7.7966 | 7.3288 | 175.8921
2011 | 8 | 8 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2011 | 8 | 9 | 13.0612 | 5 | 8.0612 | 29.9739 | 8.0612 | 0.0025902 | 29.9713 | 40.05% | 8.1947 | 7.703 | 184.8722
2011 | 8 | 10 | 11.7551 | 5 | 6.7551 | 29.9765 | 6.7551 | 0.0018189 | 29.9747 | 40.05% | 6.8677 | 6.4557 | 154.9357
2011 | 8 | 11 | 12.1469 | 5 | 7.1469 | 29.9757 | 7.1469 | 0.002036 | 29.9737 | 40.05% | 7.2658 | 6.8299 | 163.9175
2011 | 8 | 12 | 11.4939 | 5 | 6.4939 | 29.977 | 6.4939 | 0.0016809 | 29.9753 | 40.05% | 6.6023 | 6.2061 | 148.9475
2011 | 8 | 13 | 9.7959 | 5 | 4.7959 | 29.9804 | 0 | 0 | 29.9804 | 0% | 0 | 0 | 0
2011 | 8 | 14 | 8.751 | 5 | 3.751 | 29.9825 | 0 | 0 | 29.9825 | 0% | 0 | 0 | 0
2011 | 8 | 15 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2011 | 8 | 16 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2011 | 8 | 17 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2011 | 8 | 18 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2011 | 8 | 19 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2011 | 8 | 20 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2011 | 8 | 21 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2011 | 8 | 22 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2011 | 8 | 23 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2011 | 8 | 24 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2011 | 8 | 25 | 57.4694 | 5 | 52.4694 | 29.8851 | 52.4694 | 0.10974 | 29.7753 | 89.6% | 118.548 | 111.4351 | 2674.4426
2011 | 8 | 26 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2011 | 8 | 27 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2011 | 8 | 28 | 673.9592 | 5 | 668.9592 | 28.6521 | 139.3858 | 0.77441 | 27.8777 | 89.27% | 293.7679 | 276.1418 | 6627.4034
2011 | 8 | 29 | 1893.8776 | 5 | 1888.8776 | 26.2122 | 139.3858 | 0.77441 | 25.4378 | 89.27% | 268.0575 | 251.974 | 6047.3771
2011 | 8 | 30 | 684.4082 | 5 | 679.4082 | 28.6312 | 139.3858 | 0.77441 | 27.8568 | 89.27% | 293.5477 | 275.9348 | 6622.4353
2011 | 8 | 31 | 331.7551 | 5 | 326.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
2011 | 9 | 1 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2011 | 9 | 2 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2011 | 9 | 3 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2011 | 9 | 4 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
2011 | 9 | 5 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2011 | 9 | 6 | 182.8571 | 15 | 167.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2011 | 9 | 7 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2011 | 9 | 8 | 242.9388 | 15 | 227.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2011 | 9 | 9 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2011 | 9 | 10 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2011 | 9 | 11 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
2011 | 9 | 12 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2011 | 9 | 13 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2011 | 9 | 14 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2011 | 9 | 15 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2011 | 9 | 16 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2011 | 9 | 17 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2011 | 9 | 18 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2011 | 9 | 19 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2011 | 9 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2011 | 9 | 21 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2011 | 9 | 22 | 37.8776 | 15 | 22.8776 | 29.9242 | 22.8776 | 0.020862 | 29.9034 | 70.08% | 40.602 | 38.1659 | 915.9815
2011 | 9 | 23 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2011 | 9 | 24 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2011 | 9 | 25 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2011 | 9 | 26 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2011 | 9 | 27 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2011 | 9 | 28 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2011 | 9 | 29 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2011 | 9 | 30 | 407.5102 | 15 | 392.5102 | 29.185 | 139.3858 | 0.77441 | 28.4106 | 89.27% | 299.3834 | 281.4204 | 6754.09
2011 | 10 | 1 | 219.4286 | 15 | 204.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2011 | 10 | 2 | 342.2041 | 15 | 327.2041 | 29.3156 | 139.3858 | 0.77441 | 28.5412 | 89.27% | 300.7598 | 282.7142 | 6785.1407
2011 | 10 | 3 | 715.7551 | 15 | 700.7551 | 28.5685 | 139.3858 | 0.77441 | 27.7941 | 89.27% | 292.887 | 275.3138 | 6607.5309
2011 | 10 | 4 | 455.8367 | 15 | 440.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
2011 | 10 | 5 | 387.9184 | 15 | 372.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2011 | 10 | 6 | 259.9184 | 15 | 244.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2011 | 10 | 7 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2011 | 10 | 8 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
2011 | 10 | 9 | 122.7755 | 15 | 107.7755 | 29.7544 | 107.7755 | 0.46299 | 29.2915 | 91.77% | 245.3496 | 230.6287 | 5535.0881
2011 | 10 | 10 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
2011 | 10 | 11 | 90.1224 | 15 | 75.1224 | 29.8198 | 75.1224 | 0.22494 | 29.5948 | 91.6% | 172.4664 | 162.1184 | 3890.8415
2011 | 10 | 12 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2011 | 10 | 13 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2011 | 10 | 14 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
2011 | 10 | 15 | 717.0612 | 15 | 702.0612 | 28.5659 | 139.3858 | 0.77441 | 27.7915 | 89.27% | 292.8595 | 275.2879 | 6606.9099
2011 | 10 | 16 | 423.1837 | 15 | 408.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
2011 | 10 | 17 | 274.2857 | 15 | 259.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
2011 | 10 | 18 | 208.9796 | 15 | 193.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
2011 | 10 | 19 | 171.102 | 15 | 156.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2011 | 10 | 20 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2011 | 10 | 21 | 242.9388 | 15 | 227.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2011 | 10 | 22 | 198.5306 | 15 | 183.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2011 | 10 | 23 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2011 | 10 | 24 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
2011 | 10 | 25 | 134.5306 | 15 | 119.5306 | 29.7309 | 119.5306 | 0.5695 | 29.1614 | 91.43% | 269.8985 | 253.7046 | 6088.9105
2011 | 10 | 26 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
2011 | 10 | 27 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
2011 | 10 | 28 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2011 | 10 | 29 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
2011 | 10 | 30 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
2011 | 10 | 31 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2011 | 11 | 1 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
2011 | 11 | 2 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2011 | 11 | 3 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2011 | 11 | 4 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2011 | 11 | 5 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
2011 | 11 | 6 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
2011 | 11 | 7 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
2011 | 11 | 8 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
2011 | 11 | 9 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
2011 | 11 | 10 | 150.2041 | 15 | 135.2041 | 29.6996 | 135.2041 | 0.72864 | 28.971 | 90.08% | 298.8165 | 280.8875 | 6741.3004
2011 | 11 | 11 | 1042.2857 | 15 | 1027.2857 | 27.9154 | 139.3858 | 0.77441 | 27.141 | 89.27% | 286.0052 | 268.8449 | 6452.2776
2011 | 11 | 12 | 560.3265 | 15 | 545.3265 | 28.8793 | 139.3858 | 0.77441 | 28.1049 | 89.27% | 296.1627 | 278.393 | 6681.4315
2011 | 11 | 13 | 350.0408 | 15 | 335.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
2011 | 11 | 14 | 265.1429 | 15 | 250.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2011 | 11 | 15 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2011 | 11 | 16 | 192 | 15 | 177 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2011 | 11 | 17 | 202.449 | 15 | 187.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2011 | 11 | 18 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2011 | 11 | 19 | 156.7347 | 15 | 141.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
2011 | 11 | 20 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
2011 | 11 | 21 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
2011 | 11 | 22 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
2011 | 11 | 23 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
2011 | 11 | 24 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2011 | 11 | 25 | 133.2245 | 15 | 118.2245 | 29.7336 | 118.2245 | 0.55712 | 29.1764 | 91.43% | 267.0865 | 251.0613 | 6025.4721
2011 | 11 | 26 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
2011 | 11 | 27 | 186.7755 | 15 | 171.7755 | 29.6264 | 139.3858 | 0.77441 | 28.852 | 89.27% | 304.0355 | 285.7934 | 6859.0413
2011 | 11 | 28 | 237.7143 | 15 | 222.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2011 | 11 | 29 | 296.4898 | 15 | 281.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2011 | 11 | 30 | 966.5306 | 15 | 951.5306 | 28.0669 | 139.3858 | 0.77441 | 27.2925 | 89.27% | 287.6018 | 270.3457 | 6488.2964
2011 | 12 | 1 | 787.5918 | 5 | 782.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
2011 | 12 | 2 | 446.6939 | 5 | 441.6939 | 29.1066 | 139.3858 | 0.77441 | 28.3322 | 89.27% | 298.5576 | 280.6442 | 6735.4596
2011 | 12 | 3 | 325.2245 | 5 | 320.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
2011 | 12 | 4 | 257.3061 | 5 | 252.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2011 | 12 | 5 | 225.9592 | 5 | 220.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2011 | 12 | 6 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2011 | 12 | 7 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2011 | 12 | 8 | 561.6327 | 5 | 556.6327 | 28.8767 | 139.3858 | 0.77441 | 28.1023 | 89.27% | 296.1352 | 278.3671 | 6680.8105
2011 | 12 | 9 | 440.1633 | 5 | 435.1633 | 29.1197 | 139.3858 | 0.77441 | 28.3453 | 89.27% | 298.6952 | 280.7735 | 6738.5647
2011 | 12 | 10 | 325.2245 | 5 | 320.2245 | 29.3496 | 139.3858 | 0.77441 | 28.5751 | 89.27% | 301.1176 | 283.0506 | 6793.2139
2011 | 12 | 11 | 253.3878 | 5 | 248.3878 | 29.4932 | 139.3858 | 0.77441 | 28.7188 | 89.27% | 302.6316 | 284.4737 | 6827.3696
2011 | 12 | 12 | 211.5918 | 5 | 206.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2011 | 12 | 13 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2011 | 12 | 14 | 178.9388 | 5 | 173.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2011 | 12 | 15 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2011 | 12 | 16 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2011 | 12 | 17 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2011 | 12 | 18 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2011 | 12 | 19 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2011 | 12 | 20 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2011 | 12 | 21 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2011 | 12 | 22 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2011 | 12 | 23 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2011 | 12 | 24 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2011 | 12 | 25 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2011 | 12 | 26 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2011 | 12 | 27 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2011 | 12 | 28 | 707.9184 | 5 | 702.9184 | 28.5842 | 139.3858 | 0.77441 | 27.8098 | 89.27% | 293.0522 | 275.469 | 6611.257
2011 | 12 | 29 | 528.9796 | 5 | 523.9796 | 28.942 | 139.3858 | 0.77441 | 28.1676 | 89.27% | 296.8234 | 279.014 | 6696.3358
2011 | 12 | 30 | 318.6939 | 5 | 313.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2011 | 12 | 31 | 228.5714 | 5 | 223.5714 | 29.5429 | 139.3858 | 0.77441 | 28.7684 | 89.27% | 303.1546 | 284.9654 | 6839.1688
2012 | 1 | 1 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2012 | 1 | 2 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2012 | 1 | 3 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2012 | 1 | 4 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2012 | 1 | 5 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2012 | 1 | 6 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2012 | 1 | 7 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2012 | 1 | 8 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2012 | 1 | 9 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2012 | 1 | 10 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2012 | 1 | 11 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2012 | 1 | 12 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2012 | 1 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2012 | 1 | 14 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2012 | 1 | 15 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2012 | 1 | 16 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2012 | 1 | 17 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2012 | 1 | 18 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2012 | 1 | 19 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2012 | 1 | 20 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2012 | 1 | 21 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2012 | 1 | 22 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2012 | 1 | 23 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2012 | 1 | 24 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2012 | 1 | 25 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2012 | 1 | 26 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
2012 | 1 | 27 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2012 | 1 | 28 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2012 | 1 | 29 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2012 | 1 | 30 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2012 | 1 | 31 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2012 | 2 | 1 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2012 | 2 | 2 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2012 | 2 | 3 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2012 | 2 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2012 | 2 | 5 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2012 | 2 | 6 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2012 | 2 | 7 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2012 | 2 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2012 | 2 | 9 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2012 | 2 | 10 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2012 | 2 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2012 | 2 | 12 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2012 | 2 | 13 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2012 | 2 | 14 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2012 | 2 | 15 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2012 | 2 | 16 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2012 | 2 | 17 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2012 | 2 | 18 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2012 | 2 | 19 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2012 | 2 | 20 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2012 | 2 | 21 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2012 | 2 | 22 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2012 | 2 | 23 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2012 | 2 | 24 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2012 | 2 | 25 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2012 | 2 | 26 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2012 | 2 | 27 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2012 | 2 | 28 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2012 | 2 | 29 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2012 | 3 | 1 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2012 | 3 | 2 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2012 | 3 | 3 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2012 | 3 | 4 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2012 | 3 | 5 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2012 | 3 | 6 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2012 | 3 | 7 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2012 | 3 | 8 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2012 | 3 | 9 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
2012 | 3 | 10 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
2012 | 3 | 11 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2012 | 3 | 12 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2012 | 3 | 13 | 369.6327 | 25 | 344.6327 | 29.2607 | 139.3858 | 0.77441 | 28.4863 | 89.27% | 300.1817 | 282.1708 | 6772.0994
2012 | 3 | 14 | 495.0204 | 25 | 470.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
2012 | 3 | 15 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
2012 | 3 | 16 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2012 | 3 | 17 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
2012 | 3 | 18 | 472.8163 | 25 | 447.8163 | 29.0544 | 139.3858 | 0.77441 | 28.28 | 89.27% | 298.0071 | 280.1266 | 6723.0394
2012 | 3 | 19 | 659.5918 | 25 | 634.5918 | 28.6808 | 139.3858 | 0.77441 | 27.9064 | 89.27% | 294.0707 | 276.4264 | 6634.2345
2012 | 3 | 20 | 621.7143 | 25 | 596.7143 | 28.7566 | 139.3858 | 0.77441 | 27.9822 | 89.27% | 294.869 | 277.1768 | 6652.2439
2012 | 3 | 21 | 502.8571 | 25 | 477.8571 | 28.9943 | 139.3858 | 0.77441 | 28.2199 | 89.27% | 297.3739 | 279.5315 | 6708.7561
2012 | 3 | 22 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
2012 | 3 | 23 | 335.6735 | 25 | 310.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
2012 | 3 | 24 | 259.9184 | 25 | 234.9184 | 29.4802 | 139.3858 | 0.77441 | 28.7058 | 89.27% | 302.494 | 284.3444 | 6824.2645
2012 | 3 | 25 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2012 | 3 | 26 | 218.1224 | 25 | 193.1224 | 29.5638 | 139.3858 | 0.77441 | 28.7893 | 89.27% | 303.3749 | 285.1724 | 6844.1369
2012 | 3 | 27 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2012 | 3 | 28 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2012 | 3 | 29 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
2012 | 3 | 30 | 155.4286 | 25 | 130.4286 | 29.6891 | 130.4286 | 0.67808 | 29.0111 | 90.74% | 290.7762 | 273.3296 | 6559.9109
2012 | 3 | 31 | 152.8163 | 25 | 127.8163 | 29.6944 | 127.8163 | 0.65119 | 29.0432 | 90.74% | 285.2679 | 268.1518 | 6435.644
2012 | 4 | 1 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2012 | 4 | 2 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2012 | 4 | 3 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
2012 | 4 | 4 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2012 | 4 | 5 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2012 | 4 | 6 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2012 | 4 | 7 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2012 | 4 | 8 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2012 | 4 | 9 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2012 | 4 | 10 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2012 | 4 | 11 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2012 | 4 | 12 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2012 | 4 | 13 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2012 | 4 | 14 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2012 | 4 | 15 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2012 | 4 | 16 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2012 | 4 | 17 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2012 | 4 | 18 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2012 | 4 | 19 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2012 | 4 | 20 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2012 | 4 | 21 | 56.1633 | 25 | 31.1633 | 29.8877 | 31.1633 | 0.03871 | 29.849 | 80.09% | 63.092 | 59.3065 | 1423.3551
2012 | 4 | 22 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2012 | 4 | 23 | 527.6735 | 25 | 502.6735 | 28.9447 | 139.3858 | 0.77441 | 28.1702 | 89.27% | 296.8509 | 279.0399 | 6696.9568
2012 | 4 | 24 | 919.5102 | 25 | 894.5102 | 28.161 | 139.3858 | 0.77441 | 27.3866 | 89.27% | 288.5928 | 271.2772 | 6510.6529
2012 | 4 | 25 | 498.9388 | 25 | 473.9388 | 29.0021 | 139.3858 | 0.77441 | 28.2277 | 89.27% | 297.4565 | 279.6091 | 6710.6191
2012 | 4 | 26 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
2012 | 4 | 27 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
2012 | 4 | 28 | 333.0612 | 25 | 308.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
2012 | 4 | 29 | 240.3265 | 25 | 215.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2012 | 4 | 30 | 189.3878 | 25 | 164.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2012 | 5 | 1 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2012 | 5 | 2 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2012 | 5 | 3 | 233.7959 | 25 | 208.7959 | 29.5324 | 139.3858 | 0.77441 | 28.758 | 89.27% | 303.0445 | 284.8619 | 6836.6848
2012 | 5 | 4 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2012 | 5 | 5 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2012 | 5 | 6 | 245.551 | 25 | 220.551 | 29.5089 | 139.3858 | 0.77441 | 28.7345 | 89.27% | 302.7968 | 284.629 | 6831.0957
2012 | 5 | 7 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2012 | 5 | 8 | 194.6122 | 25 | 169.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2012 | 5 | 9 | 299.102 | 25 | 274.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2012 | 5 | 10 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
2012 | 5 | 11 | 390.5306 | 25 | 365.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
2012 | 5 | 12 | 269.0612 | 25 | 244.0612 | 29.4619 | 139.3858 | 0.77441 | 28.6875 | 89.27% | 302.3013 | 284.1632 | 6819.9174
2012 | 5 | 13 | 207.6735 | 25 | 182.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2012 | 5 | 14 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2012 | 5 | 15 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2012 | 5 | 16 | 272.9796 | 25 | 247.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2012 | 5 | 17 | 346.1224 | 25 | 321.1224 | 29.3078 | 139.3858 | 0.77441 | 28.5333 | 89.27% | 300.6772 | 282.6366 | 6783.2777
2012 | 5 | 18 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2012 | 5 | 19 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2012 | 5 | 20 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2012 | 5 | 21 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2012 | 5 | 22 | 113.6327 | 25 | 88.6327 | 29.7727 | 88.6327 | 0.31313 | 29.4596 | 92.22% | 203.9245 | 191.6891 | 4600.5374
2012 | 5 | 23 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2012 | 5 | 24 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2012 | 5 | 25 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2012 | 5 | 26 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2012 | 5 | 27 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2012 | 5 | 28 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2012 | 5 | 29 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2012 | 5 | 30 | 651.7551 | 25 | 626.7551 | 28.6965 | 139.3858 | 0.77441 | 27.9221 | 89.27% | 294.2358 | 276.5817 | 6637.9606
2012 | 5 | 31 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
2012 | 6 | 1 | 252.0816 | 25 | 227.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2012 | 6 | 2 | 211.5918 | 25 | 186.5918 | 29.5768 | 139.3858 | 0.77441 | 28.8024 | 89.27% | 303.5125 | 285.3018 | 6847.242
2012 | 6 | 3 | 4244.898 | 25 | 4219.898 | 21.5102 | 0 | 0 | 21.5102 | 0% | 0 | 0 | 0
2012 | 6 | 4 | 3108.5714 | 25 | 3083.5714 | 23.7829 | 0 | 0 | 23.7829 | 0% | 0 | 0 | 0
2012 | 6 | 5 | 1684.898 | 25 | 1659.898 | 26.6302 | 139.3858 | 0.77441 | 25.8558 | 89.27% | 272.4618 | 256.1141 | 6146.7392
2012 | 6 | 6 | 950.8571 | 25 | 925.8571 | 28.0983 | 139.3858 | 0.77441 | 27.3239 | 89.27% | 287.9321 | 270.6562 | 6495.7486
2012 | 6 | 7 | 647.8367 | 25 | 622.8367 | 28.7043 | 139.3858 | 0.77441 | 27.9299 | 89.27% | 294.3184 | 276.6593 | 6639.8236
2012 | 6 | 8 | 518.5306 | 25 | 493.5306 | 28.9629 | 139.3858 | 0.77441 | 28.1885 | 89.27% | 297.0436 | 279.221 | 6701.3039
2012 | 6 | 9 | 519.8367 | 25 | 494.8367 | 28.9603 | 139.3858 | 0.77441 | 28.1859 | 89.27% | 297.0161 | 279.1951 | 6700.6829
2012 | 6 | 10 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2012 | 6 | 11 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2012 | 6 | 12 | 210.2857 | 25 | 185.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2012 | 6 | 13 | 278.2041 | 25 | 253.2041 | 29.4436 | 139.3858 | 0.77441 | 28.6692 | 89.27% | 302.1086 | 283.9821 | 6815.5703
2012 | 6 | 14 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
2012 | 6 | 15 | 214.2041 | 25 | 189.2041 | 29.5716 | 139.3858 | 0.77441 | 28.7972 | 89.27% | 303.4574 | 285.25 | 6846
2012 | 6 | 16 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2012 | 6 | 17 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2012 | 6 | 18 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2012 | 6 | 19 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2012 | 6 | 20 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2012 | 6 | 21 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2012 | 6 | 22 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2012 | 6 | 23 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2012 | 6 | 24 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
2012 | 6 | 25 | 175.0204 | 25 | 150.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2012 | 6 | 26 | 600.8163 | 25 | 575.8163 | 28.7984 | 139.3858 | 0.77441 | 28.024 | 89.27% | 295.3094 | 277.5908 | 6662.1801
2012 | 6 | 27 | 658.2857 | 25 | 633.2857 | 28.6834 | 139.3858 | 0.77441 | 27.909 | 89.27% | 294.0982 | 276.4523 | 6634.8555
2012 | 6 | 28 | 367.0204 | 25 | 342.0204 | 29.266 | 139.3858 | 0.77441 | 28.4915 | 89.27% | 300.2368 | 282.2226 | 6773.3414
2012 | 6 | 29 | 248.1633 | 25 | 223.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2012 | 6 | 30 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2012 | 7 | 1 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2012 | 7 | 2 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2012 | 7 | 3 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2012 | 7 | 4 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2012 | 7 | 5 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2012 | 7 | 6 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2012 | 7 | 7 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2012 | 7 | 8 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2012 | 7 | 9 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2012 | 7 | 10 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2012 | 7 | 11 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2012 | 7 | 12 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2012 | 7 | 13 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2012 | 7 | 14 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2012 | 7 | 15 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2012 | 7 | 16 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2012 | 7 | 17 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2012 | 7 | 18 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2012 | 7 | 19 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2012 | 7 | 20 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2012 | 7 | 21 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2012 | 7 | 22 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2012 | 7 | 23 | 20.898 | 5 | 15.898 | 29.9582 | 15.898 | 0.010074 | 29.9481 | 70.08% | 28.2572 | 26.5618 | 637.482
2012 | 7 | 24 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2012 | 7 | 25 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2012 | 7 | 26 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2012 | 7 | 27 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2012 | 7 | 28 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2012 | 7 | 29 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2012 | 7 | 30 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2012 | 7 | 31 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2012 | 8 | 1 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2012 | 8 | 2 | 135.8367 | 5 | 130.8367 | 29.7283 | 130.8367 | 0.68233 | 29.046 | 90.74% | 292.0374 | 274.5151 | 6588.3632
2012 | 8 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2012 | 8 | 4 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2012 | 8 | 5 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2012 | 8 | 6 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2012 | 8 | 7 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2012 | 8 | 8 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2012 | 8 | 9 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2012 | 8 | 10 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2012 | 8 | 11 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2012 | 8 | 12 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2012 | 8 | 13 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2012 | 8 | 14 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2012 | 8 | 15 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2012 | 8 | 16 | 466.2857 | 5 | 461.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
2012 | 8 | 17 | 484.5714 | 5 | 479.5714 | 29.0309 | 139.3858 | 0.77441 | 28.2564 | 89.27% | 297.7593 | 279.8938 | 6717.4503
2012 | 8 | 18 | 252.0816 | 5 | 247.0816 | 29.4958 | 139.3858 | 0.77441 | 28.7214 | 89.27% | 302.6592 | 284.4996 | 6827.9906
2012 | 8 | 19 | 156.7347 | 5 | 151.7347 | 29.6865 | 139.3858 | 0.77441 | 28.9121 | 89.27% | 304.6686 | 286.3885 | 6873.3246
2012 | 8 | 20 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2012 | 8 | 21 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2012 | 8 | 22 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2012 | 8 | 23 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2012 | 8 | 24 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2012 | 8 | 25 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2012 | 8 | 26 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2012 | 8 | 27 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2012 | 8 | 28 | 49.6327 | 5 | 44.6327 | 29.9007 | 44.6327 | 0.079403 | 29.8213 | 87.1% | 98.1797 | 92.2889 | 2214.9332
2012 | 8 | 29 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2012 | 8 | 30 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2012 | 8 | 31 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2012 | 9 | 1 | 54.8571 | 15 | 39.8571 | 29.8903 | 39.8571 | 0.063321 | 29.827 | 87.1% | 87.6914 | 82.4299 | 1978.3181
2012 | 9 | 2 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2012 | 9 | 3 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
2012 | 9 | 4 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2012 | 9 | 5 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2012 | 9 | 6 | 178.9388 | 15 | 163.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2012 | 9 | 7 | 111.0204 | 15 | 96.0204 | 29.778 | 96.0204 | 0.3675 | 29.4105 | 92.2% | 220.5057 | 207.2754 | 4974.6093
2012 | 9 | 8 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2012 | 9 | 9 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
2012 | 9 | 10 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
2012 | 9 | 11 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2012 | 9 | 12 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2012 | 9 | 13 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2012 | 9 | 14 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2012 | 9 | 15 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2012 | 9 | 16 | 30.0408 | 15 | 15.0408 | 29.9399 | 15.0408 | 0.0090173 | 29.9309 | 70.08% | 26.7183 | 25.1152 | 602.765
2012 | 9 | 17 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2012 | 9 | 18 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2012 | 9 | 19 | 559.0204 | 15 | 544.0204 | 28.882 | 139.3858 | 0.77441 | 28.1075 | 89.27% | 296.1903 | 278.4189 | 6682.0525
2012 | 9 | 20 | 310.8571 | 15 | 295.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2012 | 9 | 21 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2012 | 9 | 22 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
2012 | 9 | 23 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
2012 | 9 | 24 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
2012 | 9 | 25 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2012 | 9 | 26 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2012 | 9 | 27 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2012 | 9 | 28 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2012 | 9 | 29 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
2012 | 9 | 30 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
2012 | 10 | 1 | 224.6531 | 15 | 209.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2012 | 10 | 2 | 152.8163 | 15 | 137.8163 | 29.6944 | 137.8163 | 0.75707 | 28.9373 | 90.08% | 304.2361 | 285.9819 | 6863.5655
2012 | 10 | 3 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
2012 | 10 | 4 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2012 | 10 | 5 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
2012 | 10 | 6 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
2012 | 10 | 7 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2012 | 10 | 8 | 144.9796 | 15 | 129.9796 | 29.71 | 129.9796 | 0.67342 | 29.0366 | 90.74% | 290.0305 | 272.6287 | 6543.0887
2012 | 10 | 9 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
2012 | 10 | 10 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2012 | 10 | 11 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2012 | 10 | 12 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
2012 | 10 | 13 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
2012 | 10 | 14 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2012 | 10 | 15 | 103.1837 | 15 | 88.1837 | 29.7936 | 88.1837 | 0.30996 | 29.4837 | 92.22% | 203.0572 | 190.8738 | 4580.9715
2012 | 10 | 16 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2012 | 10 | 17 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2012 | 10 | 18 | 114.9388 | 15 | 99.9388 | 29.7701 | 99.9388 | 0.39811 | 29.372 | 92.08% | 228.9058 | 215.1714 | 5164.1138
2012 | 10 | 19 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2012 | 10 | 20 | 723.5918 | 15 | 708.5918 | 28.5528 | 139.3858 | 0.77441 | 27.7784 | 89.27% | 292.7218 | 275.1585 | 6603.8049
2012 | 10 | 21 | 532.898 | 15 | 517.898 | 28.9342 | 139.3858 | 0.77441 | 28.1598 | 89.27% | 296.7408 | 278.9364 | 6694.4728
2012 | 10 | 22 | 309.551 | 15 | 294.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
2012 | 10 | 23 | 222.0408 | 15 | 207.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2012 | 10 | 24 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2012 | 10 | 25 | 146.2857 | 15 | 131.2857 | 29.7074 | 131.2857 | 0.68702 | 29.0204 | 90.74% | 292.7814 | 275.2145 | 6605.1477
2012 | 10 | 26 | 129.3061 | 15 | 114.3061 | 29.7414 | 114.3061 | 0.5208 | 29.2206 | 91.43% | 258.6252 | 243.1077 | 5834.5837
2012 | 10 | 27 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
2012 | 10 | 28 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
2012 | 10 | 29 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
2012 | 10 | 30 | 1187.2653 | 15 | 1172.2653 | 27.6255 | 139.3858 | 0.77441 | 26.8511 | 89.27% | 282.9497 | 265.9727 | 6383.3452
2012 | 10 | 31 | 1115.4286 | 15 | 1100.4286 | 27.7691 | 139.3858 | 0.77441 | 26.9947 | 89.27% | 284.4637 | 267.3959 | 6417.5009
2012 | 11 | 1 | 690.9388 | 15 | 675.9388 | 28.6181 | 139.3858 | 0.77441 | 27.8437 | 89.27% | 293.41 | 275.8054 | 6619.3302
2012 | 11 | 2 | 442.7755 | 15 | 427.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
2012 | 11 | 3 | 318.6939 | 15 | 303.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2012 | 11 | 4 | 246.8571 | 15 | 231.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2012 | 11 | 5 | 205.0612 | 15 | 190.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2012 | 11 | 6 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2012 | 11 | 7 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2012 | 11 | 8 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2012 | 11 | 9 | 199.8367 | 15 | 184.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2012 | 11 | 10 | 175.0204 | 15 | 160.0204 | 29.65 | 139.3858 | 0.77441 | 28.8755 | 89.27% | 304.2833 | 286.0263 | 6864.6304
2012 | 11 | 11 | 154.1224 | 15 | 139.1224 | 29.6918 | 139.1224 | 0.77149 | 28.9203 | 90.08% | 306.9386 | 288.5223 | 6924.5358
2012 | 11 | 12 | 142.3673 | 15 | 127.3673 | 29.7153 | 127.3673 | 0.64662 | 29.0686 | 90.74% | 284.5151 | 267.4442 | 6418.6604
2012 | 11 | 13 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2012 | 11 | 14 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2012 | 11 | 15 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2012 | 11 | 16 | 139.7551 | 15 | 124.7551 | 29.7205 | 124.7551 | 0.62037 | 29.1001 | 91.08% | 280.0269 | 263.2253 | 6317.4072
2012 | 11 | 17 | 128 | 15 | 113 | 29.744 | 113 | 0.50897 | 29.235 | 91.77% | 256.7476 | 241.3427 | 5792.2259
2012 | 11 | 18 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
2012 | 11 | 19 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
2012 | 11 | 20 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2012 | 11 | 21 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
2012 | 11 | 22 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2012 | 11 | 23 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
2012 | 11 | 24 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2012 | 11 | 25 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2012 | 11 | 26 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2012 | 11 | 27 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2012 | 11 | 28 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
2012 | 11 | 29 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2012 | 11 | 30 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2012 | 12 | 1 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2012 | 12 | 2 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2012 | 12 | 3 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2012 | 12 | 4 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2012 | 12 | 5 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2012 | 12 | 6 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2012 | 12 | 7 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2012 | 12 | 8 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2012 | 12 | 9 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2012 | 12 | 10 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2012 | 12 | 11 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2012 | 12 | 12 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2012 | 12 | 13 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2012 | 12 | 14 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2012 | 12 | 15 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2012 | 12 | 16 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2012 | 12 | 17 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2012 | 12 | 18 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2012 | 12 | 19 | 394.449 | 5 | 389.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
2012 | 12 | 20 | 356.5714 | 5 | 351.5714 | 29.2869 | 139.3858 | 0.77441 | 28.5124 | 89.27% | 300.457 | 282.4296 | 6778.3096
2012 | 12 | 21 | 428.4082 | 5 | 423.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
2012 | 12 | 22 | 1515.102 | 5 | 1510.102 | 26.9698 | 139.3858 | 0.77441 | 26.1954 | 89.27% | 276.0404 | 259.478 | 6227.4709
2012 | 12 | 23 | 830.6939 | 5 | 825.6939 | 28.3386 | 139.3858 | 0.77441 | 27.5642 | 89.27% | 290.4646 | 273.0367 | 6552.8818
2012 | 12 | 24 | 474.1224 | 5 | 469.1224 | 29.0518 | 139.3858 | 0.77441 | 28.2773 | 89.27% | 297.9795 | 280.1008 | 6722.4184
2012 | 12 | 25 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
2012 | 12 | 26 | 240.3265 | 5 | 235.3265 | 29.5193 | 139.3858 | 0.77441 | 28.7449 | 89.27% | 302.9069 | 284.7325 | 6833.5797
2012 | 12 | 27 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2012 | 12 | 28 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2012 | 12 | 29 | 182.8571 | 5 | 177.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2012 | 12 | 30 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2012 | 12 | 31 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2013 | 1 | 1 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2013 | 1 | 2 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
2013 | 1 | 3 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2013 | 1 | 4 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2013 | 1 | 5 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2013 | 1 | 6 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2013 | 1 | 7 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2013 | 1 | 8 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 1 | 9 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 1 | 10 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2013 | 1 | 11 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2013 | 1 | 12 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2013 | 1 | 13 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2013 | 1 | 14 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2013 | 1 | 15 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2013 | 1 | 16 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2013 | 1 | 17 | 146.2857 | 5 | 141.2857 | 29.7074 | 139.3858 | 0.77441 | 28.933 | 89.27% | 304.8889 | 286.5955 | 6878.2927
2013 | 1 | 18 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2013 | 1 | 19 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2013 | 1 | 20 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2013 | 1 | 21 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2013 | 1 | 22 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2013 | 1 | 23 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2013 | 1 | 24 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2013 | 1 | 25 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2013 | 1 | 26 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2013 | 1 | 27 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2013 | 1 | 28 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2013 | 1 | 29 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2013 | 1 | 30 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2013 | 1 | 31 | 466.2857 | 5 | 461.2857 | 29.0674 | 139.3858 | 0.77441 | 28.293 | 89.27% | 298.1447 | 280.256 | 6726.1444
2013 | 2 | 1 | 720.9796 | 5 | 715.9796 | 28.558 | 139.3858 | 0.77441 | 27.7836 | 89.27% | 292.7769 | 275.2103 | 6605.0469
2013 | 2 | 2 | 355.2653 | 5 | 350.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
2013 | 2 | 3 | 249.4694 | 5 | 244.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
2013 | 2 | 4 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2013 | 2 | 5 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2013 | 2 | 6 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2013 | 2 | 7 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2013 | 2 | 8 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2013 | 2 | 9 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2013 | 2 | 10 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2013 | 2 | 11 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 2 | 12 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2013 | 2 | 13 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2013 | 2 | 14 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 2 | 15 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2013 | 2 | 16 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2013 | 2 | 17 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2013 | 2 | 18 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2013 | 2 | 19 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2013 | 2 | 20 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2013 | 2 | 21 | 122.7755 | 5 | 117.7755 | 29.7544 | 117.7755 | 0.5529 | 29.2016 | 91.43% | 266.3013 | 250.3232 | 6007.7576
2013 | 2 | 22 | 105.7959 | 5 | 100.7959 | 29.7884 | 100.7959 | 0.40497 | 29.3834 | 92.08% | 230.9588 | 217.1013 | 5210.4311
2013 | 2 | 23 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2013 | 2 | 24 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 2 | 25 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2013 | 2 | 26 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 2 | 27 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2013 | 2 | 28 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2013 | 3 | 1 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2013 | 3 | 2 | 114.9388 | 25 | 89.9388 | 29.7701 | 89.9388 | 0.32242 | 29.4477 | 92.22% | 206.846 | 194.4352 | 4666.4454
2013 | 3 | 3 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2013 | 3 | 4 | 104.4898 | 25 | 79.4898 | 29.791 | 79.4898 | 0.25186 | 29.5392 | 91.6% | 182.1498 | 171.2208 | 4109.2993
2013 | 3 | 5 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2013 | 3 | 6 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2013 | 3 | 7 | 100.5714 | 25 | 75.5714 | 29.7989 | 75.5714 | 0.22764 | 29.5712 | 91.6% | 173.3588 | 162.9573 | 3910.9751
2013 | 3 | 8 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2013 | 3 | 9 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2013 | 3 | 10 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2013 | 3 | 11 | 129.3061 | 25 | 104.3061 | 29.7414 | 104.3061 | 0.43366 | 29.3077 | 92.08% | 238.3861 | 224.0829 | 5377.9895
2013 | 3 | 12 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2013 | 3 | 13 | 1033.1429 | 25 | 1008.1429 | 27.9337 | 139.3858 | 0.77441 | 27.1593 | 89.27% | 286.1979 | 269.026 | 6456.6247
2013 | 3 | 14 | 1012.2449 | 25 | 987.2449 | 27.9755 | 139.3858 | 0.77441 | 27.2011 | 89.27% | 286.6383 | 269.44 | 6466.5609
2013 | 3 | 15 | 672.6531 | 25 | 647.6531 | 28.6547 | 139.3858 | 0.77441 | 27.8803 | 89.27% | 293.7954 | 276.1677 | 6628.0244
2013 | 3 | 16 | 423.1837 | 25 | 398.1837 | 29.1536 | 139.3858 | 0.77441 | 28.3792 | 89.27% | 299.0531 | 281.1099 | 6746.6379
2013 | 3 | 17 | 297.7959 | 25 | 272.7959 | 29.4044 | 139.3858 | 0.77441 | 28.63 | 89.27% | 301.6957 | 283.594 | 6806.2551
2013 | 3 | 18 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2013 | 3 | 19 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2013 | 3 | 20 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2013 | 3 | 21 | 163.2653 | 25 | 138.2653 | 29.6735 | 138.2653 | 0.76201 | 28.9115 | 90.08% | 304.9547 | 286.6574 | 6879.7771
2013 | 3 | 22 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2013 | 3 | 23 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2013 | 3 | 24 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2013 | 3 | 25 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2013 | 3 | 26 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2013 | 3 | 27 | 172.4082 | 25 | 147.4082 | 29.6552 | 139.3858 | 0.77441 | 28.8808 | 89.27% | 304.3383 | 286.078 | 6865.8724
2013 | 3 | 28 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2013 | 3 | 29 | 318.6939 | 25 | 293.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2013 | 3 | 30 | 406.2041 | 25 | 381.2041 | 29.1876 | 139.3858 | 0.77441 | 28.4132 | 89.27% | 299.411 | 281.4463 | 6754.7111
2013 | 3 | 31 | 451.9184 | 25 | 426.9184 | 29.0962 | 139.3858 | 0.77441 | 28.3218 | 89.27% | 298.4475 | 280.5406 | 6732.9756
2013 | 4 | 1 | 619.102 | 25 | 594.102 | 28.7618 | 139.3858 | 0.77441 | 27.9874 | 89.27% | 294.924 | 277.2286 | 6653.4859
2013 | 4 | 2 | 758.8571 | 25 | 733.8571 | 28.4823 | 139.3858 | 0.77441 | 27.7079 | 89.27% | 291.9786 | 274.4599 | 6587.0375
2013 | 4 | 3 | 467.5918 | 25 | 442.5918 | 29.0648 | 139.3858 | 0.77441 | 28.2904 | 89.27% | 298.1172 | 280.2301 | 6725.5234
2013 | 4 | 4 | 348.7347 | 25 | 323.7347 | 29.3025 | 139.3858 | 0.77441 | 28.5281 | 89.27% | 300.6221 | 282.5848 | 6782.0356
2013 | 4 | 5 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
2013 | 4 | 6 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2013 | 4 | 7 | 313.4694 | 25 | 288.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2013 | 4 | 8 | 327.8367 | 25 | 302.8367 | 29.3443 | 139.3858 | 0.77441 | 28.5699 | 89.27% | 301.0626 | 282.9988 | 6791.9718
2013 | 4 | 9 | 517.2245 | 25 | 492.2245 | 28.9656 | 139.3858 | 0.77441 | 28.1911 | 89.27% | 297.0711 | 279.2469 | 6701.9249
2013 | 4 | 10 | 592.9796 | 25 | 567.9796 | 28.814 | 139.3858 | 0.77441 | 28.0396 | 89.27% | 295.4746 | 277.7461 | 6665.9062
2013 | 4 | 11 | 656.9796 | 25 | 631.9796 | 28.686 | 139.3858 | 0.77441 | 27.9116 | 89.27% | 294.1257 | 276.4782 | 6635.4765
2013 | 4 | 12 | 530.2857 | 25 | 505.2857 | 28.9394 | 139.3858 | 0.77441 | 28.165 | 89.27% | 296.7959 | 278.9881 | 6695.7148
2013 | 4 | 13 | 464.9796 | 25 | 439.9796 | 29.07 | 139.3858 | 0.77441 | 28.2956 | 89.27% | 298.1722 | 280.2819 | 6726.7655
2013 | 4 | 14 | 504.1633 | 25 | 479.1633 | 28.9917 | 139.3858 | 0.77441 | 28.2173 | 89.27% | 297.3464 | 279.5056 | 6708.1351
2013 | 4 | 15 | 491.102 | 25 | 466.102 | 29.0178 | 139.3858 | 0.77441 | 28.2434 | 89.27% | 297.6217 | 279.7644 | 6714.3452
2013 | 4 | 16 | 479.3469 | 25 | 454.3469 | 29.0413 | 139.3858 | 0.77441 | 28.2669 | 89.27% | 297.8694 | 279.9973 | 6719.9343
2013 | 4 | 17 | 510.6939 | 25 | 485.6939 | 28.9786 | 139.3858 | 0.77441 | 28.2042 | 89.27% | 297.2088 | 279.3763 | 6705.03
2013 | 4 | 18 | 463.6735 | 25 | 438.6735 | 29.0727 | 139.3858 | 0.77441 | 28.2982 | 89.27% | 298.1998 | 280.3078 | 6727.3865
2013 | 4 | 19 | 377.4694 | 25 | 352.4694 | 29.2451 | 139.3858 | 0.77441 | 28.4707 | 89.27% | 300.0165 | 282.0156 | 6768.3733
2013 | 4 | 20 | 548.5714 | 25 | 523.5714 | 28.9029 | 139.3858 | 0.77441 | 28.1284 | 89.27% | 296.4105 | 278.6259 | 6687.0206
2013 | 4 | 21 | 478.0408 | 25 | 453.0408 | 29.0439 | 139.3858 | 0.77441 | 28.2695 | 89.27% | 297.897 | 280.0231 | 6720.5553
2013 | 4 | 22 | 331.7551 | 25 | 306.7551 | 29.3365 | 139.3858 | 0.77441 | 28.5621 | 89.27% | 300.98 | 282.9212 | 6790.1088
2013 | 4 | 23 | 263.8367 | 25 | 238.8367 | 29.4723 | 139.3858 | 0.77441 | 28.6979 | 89.27% | 302.4114 | 284.2667 | 6822.4015
2013 | 4 | 24 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2013 | 4 | 25 | 212.898 | 25 | 187.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2013 | 4 | 26 | 185.4694 | 25 | 160.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2013 | 4 | 27 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2013 | 4 | 28 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2013 | 4 | 29 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2013 | 4 | 30 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2013 | 5 | 1 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2013 | 5 | 2 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2013 | 5 | 3 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2013 | 5 | 4 | 101.8776 | 25 | 76.8776 | 29.7962 | 76.8776 | 0.23558 | 29.5607 | 91.6% | 176.2921 | 165.7146 | 3977.1503
2013 | 5 | 5 | 95.3469 | 25 | 70.3469 | 29.8093 | 70.3469 | 0.19725 | 29.6121 | 91.6% | 161.5968 | 151.901 | 3645.6246
2013 | 5 | 6 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2013 | 5 | 7 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
2013 | 5 | 8 | 82.2857 | 25 | 57.2857 | 29.8354 | 57.2857 | 0.13081 | 29.7046 | 89.6% | 129.1225 | 121.3752 | 2913.0044
2013 | 5 | 9 | 97.9592 | 25 | 72.9592 | 29.8041 | 72.9592 | 0.21217 | 29.5919 | 91.6% | 167.4835 | 157.4345 | 3778.4279
2013 | 5 | 10 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2013 | 5 | 11 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2013 | 5 | 12 | 424.4898 | 25 | 399.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
2013 | 5 | 13 | 300.4082 | 25 | 275.4082 | 29.3992 | 139.3858 | 0.77441 | 28.6248 | 89.27% | 301.6407 | 283.5422 | 6805.0131
2013 | 5 | 14 | 202.449 | 25 | 177.449 | 29.5951 | 139.3858 | 0.77441 | 28.8207 | 89.27% | 303.7052 | 285.4829 | 6851.5891
2013 | 5 | 15 | 156.7347 | 25 | 131.7347 | 29.6865 | 131.7347 | 0.69173 | 28.9948 | 90.74% | 293.5234 | 275.912 | 6621.8887
2013 | 5 | 16 | 146.2857 | 25 | 121.2857 | 29.7074 | 121.2857 | 0.58635 | 29.1211 | 91.08% | 272.4356 | 256.0895 | 6146.1471
2013 | 5 | 17 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2013 | 5 | 18 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2013 | 5 | 19 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2013 | 5 | 20 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2013 | 5 | 21 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2013 | 5 | 22 | 380.0816 | 25 | 355.0816 | 29.2398 | 139.3858 | 0.77441 | 28.4654 | 89.27% | 299.9615 | 281.9638 | 6767.1313
2013 | 5 | 23 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2013 | 5 | 24 | 442.7755 | 25 | 417.7755 | 29.1144 | 139.3858 | 0.77441 | 28.34 | 89.27% | 298.6402 | 280.7218 | 6737.3227
2013 | 5 | 25 | 1110.2041 | 25 | 1085.2041 | 27.7796 | 139.3858 | 0.77441 | 27.0052 | 89.27% | 284.5738 | 267.4994 | 6419.985
2013 | 5 | 26 | 1449.7959 | 25 | 1424.7959 | 27.1004 | 139.3858 | 0.77441 | 26.326 | 89.27% | 277.4167 | 260.7717 | 6258.5215
2013 | 5 | 27 | 798.0408 | 25 | 773.0408 | 28.4039 | 139.3858 | 0.77441 | 27.6295 | 89.27% | 291.1528 | 273.6836 | 6568.4071
2013 | 5 | 28 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
2013 | 5 | 29 | 330.449 | 25 | 305.449 | 29.3391 | 139.3858 | 0.77441 | 28.5647 | 89.27% | 301.0075 | 282.9471 | 6790.7298
2013 | 5 | 30 | 296.4898 | 25 | 271.4898 | 29.407 | 139.3858 | 0.77441 | 28.6326 | 89.27% | 301.7232 | 283.6198 | 6806.8762
2013 | 5 | 31 | 229.8776 | 25 | 204.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2013 | 6 | 1 | 181.551 | 25 | 156.551 | 29.6369 | 139.3858 | 0.77441 | 28.8625 | 89.27% | 304.1456 | 285.8969 | 6861.5253
2013 | 6 | 2 | 148.898 | 25 | 123.898 | 29.7022 | 123.898 | 0.61187 | 29.0903 | 91.08% | 278.0094 | 261.3288 | 6271.892
2013 | 6 | 3 | 176.3265 | 25 | 151.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2013 | 6 | 4 | 143.6735 | 25 | 118.6735 | 29.7127 | 118.6735 | 0.56136 | 29.1513 | 91.43% | 267.8699 | 251.7977 | 6043.1439
2013 | 6 | 5 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2013 | 6 | 6 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2013 | 6 | 7 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2013 | 6 | 8 | 352.6531 | 25 | 327.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2013 | 6 | 9 | 306.9388 | 25 | 281.9388 | 29.3861 | 139.3858 | 0.77441 | 28.6117 | 89.27% | 301.503 | 283.4128 | 6801.9081
2013 | 6 | 10 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2013 | 6 | 11 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2013 | 6 | 12 | 453.2245 | 25 | 428.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
2013 | 6 | 13 | 350.0408 | 25 | 325.0408 | 29.2999 | 139.3858 | 0.77441 | 28.5255 | 89.27% | 300.5946 | 282.5589 | 6781.4146
2013 | 6 | 14 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2013 | 6 | 15 | 171.102 | 25 | 146.102 | 29.6578 | 139.3858 | 0.77441 | 28.8834 | 89.27% | 304.3658 | 286.1039 | 6866.4934
2013 | 6 | 16 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
2013 | 6 | 17 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2013 | 6 | 18 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2013 | 6 | 19 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2013 | 6 | 20 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2013 | 6 | 21 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2013 | 6 | 22 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2013 | 6 | 23 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2013 | 6 | 24 | 111.0204 | 25 | 86.0204 | 29.778 | 86.0204 | 0.29494 | 29.483 | 92.21% | 198.0501 | 186.1671 | 4468.0106
2013 | 6 | 25 | 87.5102 | 25 | 62.5102 | 29.825 | 62.5102 | 0.15575 | 29.6692 | 90.6% | 142.3013 | 133.7633 | 3210.3183
2013 | 6 | 26 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2013 | 6 | 27 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2013 | 6 | 28 | 365.7143 | 25 | 340.7143 | 29.2686 | 139.3858 | 0.77441 | 28.4942 | 89.27% | 300.2643 | 282.2484 | 6773.9625
2013 | 6 | 29 | 538.1224 | 25 | 513.1224 | 28.9238 | 139.3858 | 0.77441 | 28.1493 | 89.27% | 296.6307 | 278.8329 | 6691.9887
2013 | 6 | 30 | 743.1837 | 25 | 718.1837 | 28.5136 | 139.3858 | 0.77441 | 27.7392 | 89.27% | 292.3089 | 274.7704 | 6594.4897
2013 | 7 | 1 | 434.9388 | 5 | 429.9388 | 29.1301 | 139.3858 | 0.77441 | 28.3557 | 89.27% | 298.8054 | 280.877 | 6741.0488
2013 | 7 | 2 | 611.2653 | 5 | 606.2653 | 28.7775 | 139.3858 | 0.77441 | 28.0031 | 89.27% | 295.0892 | 277.3838 | 6657.212
2013 | 7 | 3 | 616.4898 | 5 | 611.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
2013 | 7 | 4 | 862.0408 | 5 | 857.0408 | 28.2759 | 139.3858 | 0.77441 | 27.5015 | 89.27% | 289.804 | 272.4157 | 6537.9775
2013 | 7 | 5 | 1201.6327 | 5 | 1196.6327 | 27.5967 | 139.3858 | 0.77441 | 26.8223 | 89.27% | 282.6469 | 265.6881 | 6376.514
2013 | 7 | 6 | 573.3878 | 5 | 568.3878 | 28.8532 | 139.3858 | 0.77441 | 28.0788 | 89.27% | 295.8875 | 278.1342 | 6675.2214
2013 | 7 | 7 | 352.6531 | 5 | 347.6531 | 29.2947 | 139.3858 | 0.77441 | 28.5203 | 89.27% | 300.5396 | 282.5072 | 6780.1726
2013 | 7 | 8 | 291.2653 | 5 | 286.2653 | 29.4175 | 139.3858 | 0.77441 | 28.6431 | 89.27% | 301.8333 | 283.7233 | 6809.3602
2013 | 7 | 9 | 299.102 | 5 | 294.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2013 | 7 | 10 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2013 | 7 | 11 | 663.5102 | 5 | 658.5102 | 28.673 | 139.3858 | 0.77441 | 27.8986 | 89.27% | 293.9881 | 276.3488 | 6632.3715
2013 | 7 | 12 | 598.2041 | 5 | 593.2041 | 28.8036 | 139.3858 | 0.77441 | 28.0292 | 89.27% | 295.3645 | 277.6426 | 6663.4221
2013 | 7 | 13 | 359.1837 | 5 | 354.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
2013 | 7 | 14 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2013 | 7 | 15 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2013 | 7 | 16 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2013 | 7 | 17 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
2013 | 7 | 18 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2013 | 7 | 19 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2013 | 7 | 20 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2013 | 7 | 21 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2013 | 7 | 22 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2013 | 7 | 23 | 394.449 | 5 | 389.449 | 29.2111 | 139.3858 | 0.77441 | 28.4367 | 89.27% | 299.6587 | 281.6792 | 6760.3002
2013 | 7 | 24 | 525.0612 | 5 | 520.0612 | 28.9499 | 139.3858 | 0.77441 | 28.1755 | 89.27% | 296.906 | 279.0916 | 6698.1989
2013 | 7 | 25 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2013 | 7 | 26 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2013 | 7 | 27 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2013 | 7 | 28 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2013 | 7 | 29 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2013 | 7 | 30 | 159.3469 | 5 | 154.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2013 | 7 | 31 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2013 | 8 | 1 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2013 | 8 | 2 | 194.6122 | 5 | 189.6122 | 29.6108 | 139.3858 | 0.77441 | 28.8364 | 89.27% | 303.8704 | 285.6381 | 6855.3152
2013 | 8 | 3 | 299.102 | 5 | 294.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2013 | 8 | 4 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2013 | 8 | 5 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2013 | 8 | 6 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2013 | 8 | 7 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2013 | 8 | 8 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2013 | 8 | 9 | 647.8367 | 5 | 642.8367 | 28.7043 | 139.3858 | 0.77441 | 27.9299 | 89.27% | 294.3184 | 276.6593 | 6639.8236
2013 | 8 | 10 | 1384.4898 | 5 | 1379.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
2013 | 8 | 11 | 535.5102 | 5 | 530.5102 | 28.929 | 139.3858 | 0.77441 | 28.1546 | 89.27% | 296.6858 | 278.8846 | 6693.2308
2013 | 8 | 12 | 305.6327 | 5 | 300.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
2013 | 8 | 13 | 242.9388 | 5 | 237.9388 | 29.5141 | 139.3858 | 0.77441 | 28.7397 | 89.27% | 302.8518 | 284.6807 | 6832.3377
2013 | 8 | 14 | 299.102 | 5 | 294.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2013 | 8 | 15 | 212.898 | 5 | 207.898 | 29.5742 | 139.3858 | 0.77441 | 28.7998 | 89.27% | 303.485 | 285.2759 | 6846.621
2013 | 8 | 16 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2013 | 8 | 17 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
2013 | 8 | 18 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2013 | 8 | 19 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2013 | 8 | 20 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 8 | 21 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2013 | 8 | 22 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2013 | 8 | 23 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2013 | 8 | 24 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2013 | 8 | 25 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2013 | 8 | 26 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2013 | 8 | 27 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2013 | 8 | 28 | 43.102 | 5 | 38.102 | 29.9138 | 38.102 | 0.057867 | 29.8559 | 87.1% | 83.9113 | 78.8767 | 1893.0397
2013 | 8 | 29 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2013 | 8 | 30 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2013 | 8 | 31 | 168.4898 | 5 | 163.4898 | 29.663 | 139.3858 | 0.77441 | 28.8886 | 89.27% | 304.4209 | 286.1556 | 6867.7354
2013 | 9 | 1 | 232.4898 | 15 | 217.4898 | 29.535 | 139.3858 | 0.77441 | 28.7606 | 89.27% | 303.0721 | 284.8877 | 6837.3058
2013 | 9 | 2 | 902.5306 | 15 | 887.5306 | 28.1949 | 139.3858 | 0.77441 | 27.4205 | 89.27% | 288.9506 | 271.6136 | 6518.7261
2013 | 9 | 3 | 1047.5102 | 15 | 1032.5102 | 27.905 | 139.3858 | 0.77441 | 27.1306 | 89.27% | 285.8951 | 268.7414 | 6449.7936
2013 | 9 | 4 | 501.551 | 15 | 486.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
2013 | 9 | 5 | 299.102 | 15 | 284.102 | 29.4018 | 139.3858 | 0.77441 | 28.6274 | 89.27% | 301.6682 | 283.5681 | 6805.6341
2013 | 9 | 6 | 203.7551 | 15 | 188.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2013 | 9 | 7 | 164.5714 | 15 | 149.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2013 | 9 | 8 | 138.449 | 15 | 123.449 | 29.7231 | 123.449 | 0.60745 | 29.1157 | 91.08% | 277.2431 | 260.6085 | 6254.6042
2013 | 9 | 9 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
2013 | 9 | 10 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
2013 | 9 | 11 | 99.2653 | 15 | 84.2653 | 29.8015 | 84.2653 | 0.28303 | 29.5184 | 92.11% | 194.0317 | 182.3898 | 4377.3547
2013 | 9 | 12 | 148.898 | 15 | 133.898 | 29.7022 | 133.898 | 0.71463 | 28.9876 | 90.08% | 296.0996 | 278.3336 | 6680.0074
2013 | 9 | 13 | 343.5102 | 15 | 328.5102 | 29.313 | 139.3858 | 0.77441 | 28.5386 | 89.27% | 300.7323 | 282.6883 | 6784.5197
2013 | 9 | 14 | 335.6735 | 15 | 320.6735 | 29.3287 | 139.3858 | 0.77441 | 28.5542 | 89.27% | 300.8974 | 282.8436 | 6788.2458
2013 | 9 | 15 | 248.1633 | 15 | 233.1633 | 29.5037 | 139.3858 | 0.77441 | 28.7293 | 89.27% | 302.7417 | 284.5772 | 6829.8536
2013 | 9 | 16 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2013 | 9 | 17 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
2013 | 9 | 18 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
2013 | 9 | 19 | 100.5714 | 15 | 85.5714 | 29.7989 | 85.5714 | 0.29187 | 29.507 | 92.21% | 197.1766 | 185.346 | 4448.3034
2013 | 9 | 20 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
2013 | 9 | 21 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
2013 | 9 | 22 | 104.4898 | 15 | 89.4898 | 29.791 | 89.4898 | 0.31921 | 29.4718 | 92.22% | 205.9819 | 193.623 | 4646.9516
2013 | 9 | 23 | 116.2449 | 15 | 101.2449 | 29.7675 | 101.2449 | 0.40858 | 29.3589 | 92.08% | 231.7941 | 217.8864 | 5229.2739
2013 | 9 | 24 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
2013 | 9 | 25 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2013 | 9 | 26 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2013 | 9 | 27 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2013 | 9 | 28 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2013 | 9 | 29 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2013 | 9 | 30 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2013 | 10 | 1 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2013 | 10 | 2 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2013 | 10 | 3 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
2013 | 10 | 4 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2013 | 10 | 5 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2013 | 10 | 6 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2013 | 10 | 7 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2013 | 10 | 8 | 141.0612 | 15 | 126.0612 | 29.7179 | 126.0612 | 0.63343 | 29.0844 | 90.74% | 281.7506 | 264.8455 | 6356.2929
2013 | 10 | 9 | 101.8776 | 15 | 86.8776 | 29.7962 | 86.8776 | 0.30085 | 29.4954 | 92.21% | 200.1075 | 188.1011 | 4514.4263
2013 | 10 | 10 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2013 | 10 | 11 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2013 | 10 | 12 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2013 | 10 | 13 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2013 | 10 | 14 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2013 | 10 | 15 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2013 | 10 | 16 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2013 | 10 | 17 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2013 | 10 | 18 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
2013 | 10 | 19 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2013 | 10 | 20 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2013 | 10 | 21 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2013 | 10 | 22 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2013 | 10 | 23 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2013 | 10 | 24 | 56.1633 | 15 | 41.1633 | 29.8877 | 41.1633 | 0.067539 | 29.8201 | 87.1% | 90.5443 | 85.1117 | 2042.6799
2013 | 10 | 25 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2013 | 10 | 26 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
2013 | 10 | 27 | 49.6327 | 15 | 34.6327 | 29.9007 | 34.6327 | 0.047809 | 29.8529 | 80.09% | 70.1253 | 65.9178 | 1582.0264
2013 | 10 | 28 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2013 | 10 | 29 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2013 | 10 | 30 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2013 | 10 | 31 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2013 | 11 | 1 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
2013 | 11 | 2 | 169.7959 | 15 | 154.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2013 | 11 | 3 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
2013 | 11 | 4 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2013 | 11 | 5 | 80.9796 | 15 | 65.9796 | 29.838 | 65.9796 | 0.17352 | 29.6645 | 90.6% | 150.1754 | 141.1649 | 3387.957
2013 | 11 | 6 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
2013 | 11 | 7 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
2013 | 11 | 8 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2013 | 11 | 9 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2013 | 11 | 10 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2013 | 11 | 11 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2013 | 11 | 12 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2013 | 11 | 13 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2013 | 11 | 14 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2013 | 11 | 15 | 53.551 | 15 | 38.551 | 29.8929 | 38.551 | 0.059239 | 29.8337 | 87.1% | 84.8368 | 79.7466 | 1913.9179
2013 | 11 | 16 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2013 | 11 | 17 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2013 | 11 | 18 | 147.5918 | 15 | 132.5918 | 29.7048 | 132.5918 | 0.70076 | 29.0041 | 90.08% | 293.378 | 275.7754 | 6618.6086
2013 | 11 | 19 | 165.8776 | 15 | 150.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2013 | 11 | 20 | 117.551 | 15 | 102.551 | 29.7649 | 102.551 | 0.41919 | 29.3457 | 92.08% | 234.6786 | 220.5979 | 5294.3494
2013 | 11 | 21 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
2013 | 11 | 22 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2013 | 11 | 23 | 82.2857 | 15 | 67.2857 | 29.8354 | 67.2857 | 0.18046 | 29.655 | 90.6% | 153.0989 | 143.913 | 3453.9122
2013 | 11 | 24 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2013 | 11 | 25 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2013 | 11 | 26 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2013 | 11 | 27 | 497.6327 | 15 | 482.6327 | 29.0047 | 139.3858 | 0.77441 | 28.2303 | 89.27% | 297.484 | 279.635 | 6711.2401
2013 | 11 | 28 | 1102.3673 | 15 | 1087.3673 | 27.7953 | 139.3858 | 0.77441 | 27.0209 | 89.27% | 284.739 | 267.6546 | 6423.711
2013 | 11 | 29 | 514.6122 | 15 | 499.6122 | 28.9708 | 139.3858 | 0.77441 | 28.1964 | 89.27% | 297.1262 | 279.2986 | 6703.167
2013 | 11 | 30 | 262.5306 | 15 | 247.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2013 | 12 | 1 | 215.5102 | 5 | 210.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2013 | 12 | 2 | 185.4694 | 5 | 180.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2013 | 12 | 3 | 192 | 5 | 187 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2013 | 12 | 4 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2013 | 12 | 5 | 169.7959 | 5 | 164.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2013 | 12 | 6 | 246.8571 | 5 | 241.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2013 | 12 | 7 | 283.4286 | 5 | 278.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2013 | 12 | 8 | 197.2245 | 5 | 192.2245 | 29.6056 | 139.3858 | 0.77441 | 28.8311 | 89.27% | 303.8153 | 285.5864 | 6854.0732
2013 | 12 | 9 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2013 | 12 | 10 | 138.449 | 5 | 133.449 | 29.7231 | 133.449 | 0.70985 | 29.0133 | 90.08% | 295.3682 | 277.6461 | 6663.5068
2013 | 12 | 11 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2013 | 12 | 12 | 97.9592 | 5 | 92.9592 | 29.8041 | 92.9592 | 0.34444 | 29.4596 | 92.2% | 213.8328 | 201.0028 | 4824.0675
2013 | 12 | 13 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 12 | 14 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2013 | 12 | 15 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2013 | 12 | 16 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2013 | 12 | 17 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 12 | 18 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 12 | 19 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 12 | 20 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 12 | 21 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2013 | 12 | 22 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2013 | 12 | 23 | 130.6122 | 5 | 125.6122 | 29.7388 | 125.6122 | 0.62892 | 29.1099 | 90.74% | 280.9923 | 264.1328 | 6339.1861
2013 | 12 | 24 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2013 | 12 | 25 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2013 | 12 | 26 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2013 | 12 | 27 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2013 | 12 | 28 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2013 | 12 | 29 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2013 | 12 | 30 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2013 | 12 | 31 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2014 | 1 | 1 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2014 | 1 | 2 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2014 | 1 | 3 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2014 | 1 | 4 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2014 | 1 | 5 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2014 | 1 | 6 | 142.3673 | 5 | 137.3673 | 29.7153 | 137.3673 | 0.75214 | 28.9631 | 90.08% | 303.5155 | 285.3046 | 6847.3102
2014 | 1 | 7 | 386.6122 | 5 | 381.6122 | 29.2268 | 139.3858 | 0.77441 | 28.4524 | 89.27% | 299.8239 | 281.8344 | 6764.0263
2014 | 1 | 8 | 295.1837 | 5 | 290.1837 | 29.4096 | 139.3858 | 0.77441 | 28.6352 | 89.27% | 301.7508 | 283.6457 | 6807.4972
2014 | 1 | 9 | 246.8571 | 5 | 241.8571 | 29.5063 | 139.3858 | 0.77441 | 28.7319 | 89.27% | 302.7693 | 284.6031 | 6830.4747
2014 | 1 | 10 | 203.7551 | 5 | 198.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2014 | 1 | 11 | 193.3061 | 5 | 188.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2014 | 1 | 12 | 501.551 | 5 | 496.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
2014 | 1 | 13 | 495.0204 | 5 | 490.0204 | 29.01 | 139.3858 | 0.77441 | 28.2355 | 89.27% | 297.5391 | 279.6868 | 6712.4822
2014 | 1 | 14 | 395.7551 | 5 | 390.7551 | 29.2085 | 139.3858 | 0.77441 | 28.4341 | 89.27% | 299.6312 | 281.6533 | 6759.6792
2014 | 1 | 15 | 714.449 | 5 | 709.449 | 28.5711 | 139.3858 | 0.77441 | 27.7967 | 89.27% | 292.9145 | 275.3397 | 6608.1519
2014 | 1 | 16 | 594.2857 | 5 | 589.2857 | 28.8114 | 139.3858 | 0.77441 | 28.037 | 89.27% | 295.447 | 277.7202 | 6665.2852
2014 | 1 | 17 | 428.4082 | 5 | 423.4082 | 29.1432 | 139.3858 | 0.77441 | 28.3688 | 89.27% | 298.943 | 281.0064 | 6744.1538
2014 | 1 | 18 | 333.0612 | 5 | 328.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
2014 | 1 | 19 | 274.2857 | 5 | 269.2857 | 29.4514 | 139.3858 | 0.77441 | 28.677 | 89.27% | 302.1912 | 284.0597 | 6817.4334
2014 | 1 | 20 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2014 | 1 | 21 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2014 | 1 | 22 | 152.8163 | 5 | 147.8163 | 29.6944 | 139.3858 | 0.77441 | 28.92 | 89.27% | 304.7512 | 286.4662 | 6875.1876
2014 | 1 | 23 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2014 | 1 | 24 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2014 | 1 | 25 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2014 | 1 | 26 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2014 | 1 | 27 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2014 | 1 | 28 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2014 | 1 | 29 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2014 | 1 | 30 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2014 | 1 | 31 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2014 | 2 | 1 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2014 | 2 | 2 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2014 | 2 | 3 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2014 | 2 | 4 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2014 | 2 | 5 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2014 | 2 | 6 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2014 | 2 | 7 | 82.2857 | 5 | 77.2857 | 29.8354 | 77.2857 | 0.23809 | 29.5973 | 91.6% | 177.448 | 166.8011 | 4003.2267
2014 | 2 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2014 | 2 | 9 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2014 | 2 | 10 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2014 | 2 | 11 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2014 | 2 | 12 | 74.449 | 5 | 69.449 | 29.8511 | 69.449 | 0.19225 | 29.6589 | 90.6% | 158.0418 | 148.5593 | 3565.4238
2014 | 2 | 13 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2014 | 2 | 14 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2014 | 2 | 15 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2014 | 2 | 16 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2014 | 2 | 17 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2014 | 2 | 18 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2014 | 2 | 19 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2014 | 2 | 20 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2014 | 2 | 21 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2014 | 2 | 22 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2014 | 2 | 23 | 148.898 | 5 | 143.898 | 29.7022 | 139.3858 | 0.77441 | 28.9278 | 89.27% | 304.8338 | 286.5438 | 6877.0506
2014 | 2 | 24 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2014 | 2 | 25 | 111.0204 | 5 | 106.0204 | 29.778 | 106.0204 | 0.44804 | 29.3299 | 91.77% | 241.6711 | 227.1709 | 5452.1008
2014 | 2 | 26 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2014 | 2 | 27 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2014 | 2 | 28 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2014 | 3 | 1 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2014 | 3 | 2 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2014 | 3 | 3 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2014 | 3 | 4 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2014 | 3 | 5 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2014 | 3 | 6 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2014 | 3 | 7 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2014 | 3 | 8 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2014 | 3 | 9 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2014 | 3 | 10 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2014 | 3 | 11 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2014 | 3 | 12 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2014 | 3 | 13 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2014 | 3 | 14 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2014 | 3 | 15 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2014 | 3 | 16 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2014 | 3 | 17 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2014 | 3 | 18 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2014 | 3 | 19 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2014 | 3 | 20 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2014 | 3 | 21 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2014 | 3 | 22 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2014 | 3 | 23 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2014 | 3 | 24 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2014 | 3 | 25 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2014 | 3 | 26 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2014 | 3 | 27 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2014 | 3 | 28 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2014 | 3 | 29 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2014 | 3 | 30 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
2014 | 3 | 31 | 201.1429 | 25 | 176.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2014 | 4 | 1 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2014 | 4 | 2 | 208.9796 | 25 | 183.9796 | 29.582 | 139.3858 | 0.77441 | 28.8076 | 89.27% | 303.5676 | 285.3535 | 6848.484
2014 | 4 | 3 | 184.1633 | 25 | 159.1633 | 29.6317 | 139.3858 | 0.77441 | 28.8573 | 89.27% | 304.0906 | 285.8451 | 6860.2833
2014 | 4 | 4 | 193.3061 | 25 | 168.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2014 | 4 | 5 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2014 | 4 | 6 | 363.102 | 25 | 338.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
2014 | 4 | 7 | 385.3061 | 25 | 360.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
2014 | 4 | 8 | 787.5918 | 25 | 762.5918 | 28.4248 | 139.3858 | 0.77441 | 27.6504 | 89.27% | 291.373 | 273.8906 | 6573.3752
2014 | 4 | 9 | 1278.6939 | 25 | 1253.6939 | 27.4426 | 139.3858 | 0.77441 | 26.6682 | 89.27% | 281.0228 | 264.1614 | 6339.8743
2014 | 4 | 10 | 1192.4898 | 25 | 1167.4898 | 27.615 | 139.3858 | 0.77441 | 26.8406 | 89.27% | 282.8396 | 265.8692 | 6380.8611
2014 | 4 | 11 | 1235.5918 | 25 | 1210.5918 | 27.5288 | 139.3858 | 0.77441 | 26.7544 | 89.27% | 281.9312 | 265.0153 | 6360.3677
2014 | 4 | 12 | 1658.7755 | 25 | 1633.7755 | 26.6824 | 139.3858 | 0.77441 | 25.908 | 89.27% | 273.0124 | 256.6316 | 6159.1594
2014 | 4 | 13 | 1580.4082 | 25 | 1555.4082 | 26.8392 | 139.3858 | 0.77441 | 26.0648 | 89.27% | 274.664 | 258.1842 | 6196.4202
2014 | 4 | 14 | 1193.7959 | 25 | 1168.7959 | 27.6124 | 139.3858 | 0.77441 | 26.838 | 89.27% | 282.8121 | 265.8433 | 6380.2401
2014 | 4 | 15 | 2037.551 | 25 | 2012.551 | 25.9249 | 139.3858 | 0.77441 | 25.1505 | 89.27% | 265.0295 | 249.1277 | 5979.0656
2014 | 4 | 16 | 3369.7959 | 25 | 3344.7959 | 23.2604 | 0 | 0 | 23.2604 | 0% | 0 | 0 | 0
2014 | 4 | 17 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
2014 | 4 | 18 | 893.3878 | 25 | 868.3878 | 28.2132 | 139.3858 | 0.77441 | 27.4388 | 89.27% | 289.1433 | 271.7947 | 6523.0731
2014 | 4 | 19 | 711.8367 | 25 | 686.8367 | 28.5763 | 139.3858 | 0.77441 | 27.8019 | 89.27% | 292.9696 | 275.3914 | 6609.394
2014 | 4 | 20 | 616.4898 | 25 | 591.4898 | 28.767 | 139.3858 | 0.77441 | 27.9926 | 89.27% | 294.9791 | 277.2803 | 6654.7279
2014 | 4 | 21 | 568.1633 | 25 | 543.1633 | 28.8637 | 139.3858 | 0.77441 | 28.0893 | 89.27% | 295.9976 | 278.2377 | 6677.7054
2014 | 4 | 22 | 599.5102 | 25 | 574.5102 | 28.801 | 139.3858 | 0.77441 | 28.0266 | 89.27% | 295.3369 | 277.6167 | 6662.8011
2014 | 4 | 23 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
2014 | 4 | 24 | 501.551 | 25 | 476.551 | 28.9969 | 139.3858 | 0.77441 | 28.2225 | 89.27% | 297.4015 | 279.5574 | 6709.3771
2014 | 4 | 25 | 399.6735 | 25 | 374.6735 | 29.2007 | 139.3858 | 0.77441 | 28.4262 | 89.27% | 299.5486 | 281.5757 | 6757.8161
2014 | 4 | 26 | 359.1837 | 25 | 334.1837 | 29.2816 | 139.3858 | 0.77441 | 28.5072 | 89.27% | 300.4019 | 282.3778 | 6777.0675
2014 | 4 | 27 | 455.8367 | 25 | 430.8367 | 29.0883 | 139.3858 | 0.77441 | 28.3139 | 89.27% | 298.3649 | 280.463 | 6731.1126
2014 | 4 | 28 | 387.9184 | 25 | 362.9184 | 29.2242 | 139.3858 | 0.77441 | 28.4498 | 89.27% | 299.7963 | 281.8086 | 6763.4052
2014 | 4 | 29 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2014 | 4 | 30 | 262.5306 | 25 | 237.5306 | 29.4749 | 139.3858 | 0.77441 | 28.7005 | 89.27% | 302.4389 | 284.2926 | 6823.0225
2014 | 5 | 1 | 427.102 | 25 | 402.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
2014 | 5 | 2 | 470.2041 | 25 | 445.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
2014 | 5 | 3 | 353.9592 | 25 | 328.9592 | 29.2921 | 139.3858 | 0.77441 | 28.5177 | 89.27% | 300.512 | 282.4813 | 6779.5516
2014 | 5 | 4 | 336.9796 | 25 | 311.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2014 | 5 | 5 | 323.9184 | 25 | 298.9184 | 29.3522 | 139.3858 | 0.77441 | 28.5778 | 89.27% | 301.1452 | 283.0765 | 6793.8349
2014 | 5 | 6 | 258.6122 | 25 | 233.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2014 | 5 | 7 | 220.7347 | 25 | 195.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2014 | 5 | 8 | 190.6939 | 25 | 165.6939 | 29.6186 | 139.3858 | 0.77441 | 28.8442 | 89.27% | 303.9529 | 285.7158 | 6857.1782
2014 | 5 | 9 | 169.7959 | 25 | 144.7959 | 29.6604 | 139.3858 | 0.77441 | 28.886 | 89.27% | 304.3934 | 286.1298 | 6867.1144
2014 | 5 | 10 | 178.9388 | 25 | 153.9388 | 29.6421 | 139.3858 | 0.77441 | 28.8677 | 89.27% | 304.2007 | 285.9486 | 6862.7673
2014 | 5 | 11 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2014 | 5 | 12 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
2014 | 5 | 13 | 131.9184 | 25 | 106.9184 | 29.7362 | 106.9184 | 0.45566 | 29.2805 | 91.77% | 243.3074 | 228.7089 | 5489.0144
2014 | 5 | 14 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2014 | 5 | 15 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2014 | 5 | 16 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2014 | 5 | 17 | 965.2245 | 25 | 940.2245 | 28.0696 | 139.3858 | 0.77441 | 27.2951 | 89.27% | 287.6293 | 270.3716 | 6488.9174
2014 | 5 | 18 | 1004.4082 | 25 | 979.4082 | 27.9912 | 139.3858 | 0.77441 | 27.2168 | 89.27% | 286.8035 | 269.5953 | 6470.287
2014 | 5 | 19 | 510.6939 | 25 | 485.6939 | 28.9786 | 139.3858 | 0.77441 | 28.2042 | 89.27% | 297.2088 | 279.3763 | 6705.03
2014 | 5 | 20 | 412.7347 | 25 | 387.7347 | 29.1745 | 139.3858 | 0.77441 | 28.4001 | 89.27% | 299.2733 | 281.3169 | 6751.606
2014 | 5 | 21 | 301.7143 | 25 | 276.7143 | 29.3966 | 139.3858 | 0.77441 | 28.6222 | 89.27% | 301.6131 | 283.5163 | 6804.3921
2014 | 5 | 22 | 244.2449 | 25 | 219.2449 | 29.5115 | 139.3858 | 0.77441 | 28.7371 | 89.27% | 302.8243 | 284.6549 | 6831.7167
2014 | 5 | 23 | 249.4694 | 25 | 224.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
2014 | 5 | 24 | 312.1633 | 25 | 287.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
2014 | 5 | 25 | 376.1633 | 25 | 351.1633 | 29.2477 | 139.3858 | 0.77441 | 28.4733 | 89.27% | 300.0441 | 282.0414 | 6768.9944
2014 | 5 | 26 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
2014 | 5 | 27 | 476.7347 | 25 | 451.7347 | 29.0465 | 139.3858 | 0.77441 | 28.2721 | 89.27% | 297.9245 | 280.049 | 6721.1763
2014 | 5 | 28 | 1423.6735 | 25 | 1398.6735 | 27.1527 | 139.3858 | 0.77441 | 26.3782 | 89.27% | 277.9673 | 261.2892 | 6270.9418
2014 | 5 | 29 | 801.9592 | 25 | 776.9592 | 28.3961 | 139.3858 | 0.77441 | 27.6217 | 89.27% | 291.0702 | 273.606 | 6566.5441
2014 | 5 | 30 | 484.5714 | 25 | 459.5714 | 29.0309 | 139.3858 | 0.77441 | 28.2564 | 89.27% | 297.7593 | 279.8938 | 6717.4503
2014 | 5 | 31 | 420.5714 | 25 | 395.5714 | 29.1589 | 139.3858 | 0.77441 | 28.3844 | 89.27% | 299.1082 | 281.1617 | 6747.8799
2014 | 6 | 1 | 314.7755 | 25 | 289.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182
2014 | 6 | 2 | 241.6327 | 25 | 216.6327 | 29.5167 | 139.3858 | 0.77441 | 28.7423 | 89.27% | 302.8794 | 284.7066 | 6832.9587
2014 | 6 | 3 | 195.9184 | 25 | 170.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2014 | 6 | 4 | 164.5714 | 25 | 139.5714 | 29.6709 | 139.3858 | 0.77441 | 28.8964 | 89.27% | 304.5035 | 286.2333 | 6869.5985
2014 | 6 | 5 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
2014 | 6 | 6 | 147.5918 | 25 | 122.5918 | 29.7048 | 122.5918 | 0.59904 | 29.1058 | 91.08% | 275.2247 | 258.7112 | 6209.069
2014 | 6 | 7 | 124.0816 | 25 | 99.0816 | 29.7518 | 99.0816 | 0.39131 | 29.3605 | 92.08% | 226.8538 | 213.2425 | 5117.8207
2014 | 6 | 8 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2014 | 6 | 9 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2014 | 6 | 10 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2014 | 6 | 11 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2014 | 6 | 12 | 79.6735 | 25 | 54.6735 | 29.8407 | 54.6735 | 0.11915 | 29.7215 | 89.6% | 123.3045 | 115.9063 | 2781.7506
2014 | 6 | 13 | 271.6735 | 25 | 246.6735 | 29.4567 | 139.3858 | 0.77441 | 28.6822 | 89.27% | 302.2463 | 284.1115 | 6818.6754
2014 | 6 | 14 | 615.1837 | 25 | 590.1837 | 28.7696 | 139.3858 | 0.77441 | 27.9952 | 89.27% | 295.0066 | 277.3062 | 6655.3489
2014 | 6 | 15 | 317.3878 | 25 | 292.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
2014 | 6 | 16 | 199.8367 | 25 | 174.8367 | 29.6003 | 139.3858 | 0.77441 | 28.8259 | 89.27% | 303.7602 | 285.5346 | 6852.8311
2014 | 6 | 17 | 144.9796 | 25 | 119.9796 | 29.71 | 119.9796 | 0.57378 | 29.1363 | 91.08% | 269.6422 | 253.4636 | 6083.1273
2014 | 6 | 18 | 126.6939 | 25 | 101.6939 | 29.7466 | 101.6939 | 0.41221 | 29.3344 | 92.08% | 232.6274 | 218.6698 | 5248.0751
2014 | 6 | 19 | 108.4082 | 25 | 83.4082 | 29.7832 | 83.4082 | 0.2773 | 29.5059 | 92.11% | 191.9763 | 180.4577 | 4330.9853
2014 | 6 | 20 | 83.5918 | 25 | 58.5918 | 29.8328 | 58.5918 | 0.13684 | 29.696 | 89.6% | 132.0281 | 124.1064 | 2978.5542
2014 | 6 | 21 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2014 | 6 | 22 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2014 | 6 | 23 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2014 | 6 | 24 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2014 | 6 | 25 | 73.1429 | 25 | 48.1429 | 29.8537 | 48.1429 | 0.092384 | 29.7613 | 88.6% | 107.5082 | 101.0577 | 2425.3849
2014 | 6 | 26 | 1097.1429 | 25 | 1072.1429 | 27.8057 | 139.3858 | 0.77441 | 27.0313 | 89.27% | 284.8491 | 267.7581 | 6426.1951
2014 | 6 | 27 | 589.0612 | 25 | 564.0612 | 28.8219 | 139.3858 | 0.77441 | 28.0475 | 89.27% | 295.5571 | 277.8237 | 6667.7692
2014 | 6 | 28 | 289.9592 | 25 | 264.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
2014 | 6 | 29 | 188.0816 | 25 | 163.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2014 | 6 | 30 | 134.5306 | 25 | 109.5306 | 29.7309 | 109.5306 | 0.47819 | 29.2527 | 91.77% | 249.0156 | 234.0746 | 5617.7914
2014 | 7 | 1 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2014 | 7 | 2 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2014 | 7 | 3 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2014 | 7 | 4 | 276.898 | 5 | 271.898 | 29.4462 | 139.3858 | 0.77441 | 28.6718 | 89.27% | 302.1361 | 284.008 | 6816.1914
2014 | 7 | 5 | 651.7551 | 5 | 646.7551 | 28.6965 | 139.3858 | 0.77441 | 27.9221 | 89.27% | 294.2358 | 276.5817 | 6637.9606
2014 | 7 | 6 | 415.3469 | 5 | 410.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
2014 | 7 | 7 | 229.8776 | 5 | 224.8776 | 29.5402 | 139.3858 | 0.77441 | 28.7658 | 89.27% | 303.1271 | 284.9395 | 6838.5478
2014 | 7 | 8 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2014 | 7 | 9 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2014 | 7 | 10 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2014 | 7 | 11 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2014 | 7 | 12 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2014 | 7 | 13 | 60.0816 | 5 | 55.0816 | 29.8798 | 55.0816 | 0.12093 | 29.7589 | 89.6% | 124.3814 | 116.9185 | 2806.044
2014 | 7 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2014 | 7 | 15 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2014 | 7 | 16 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
2014 | 7 | 17 | 176.3265 | 5 | 171.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2014 | 7 | 18 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2014 | 7 | 19 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2014 | 7 | 20 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2014 | 7 | 21 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2014 | 7 | 22 | 54.8571 | 5 | 49.8571 | 29.8903 | 49.8571 | 0.099081 | 29.7912 | 88.6% | 111.4481 | 104.7613 | 2514.2701
2014 | 7 | 23 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2014 | 7 | 24 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2014 | 7 | 25 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2014 | 7 | 26 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2014 | 7 | 27 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2014 | 7 | 28 | 141.0612 | 5 | 136.0612 | 29.7179 | 136.0612 | 0.73791 | 28.98 | 90.08% | 300.8045 | 282.7562 | 6786.1494
2014 | 7 | 29 | 427.102 | 5 | 422.102 | 29.1458 | 139.3858 | 0.77441 | 28.3714 | 89.27% | 298.9705 | 281.0323 | 6744.7748
2014 | 7 | 30 | 231.1837 | 5 | 226.1837 | 29.5376 | 139.3858 | 0.77441 | 28.7632 | 89.27% | 303.0996 | 284.9136 | 6837.9268
2014 | 7 | 31 | 177.6327 | 5 | 172.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2014 | 8 | 1 | 235.102 | 5 | 230.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2014 | 8 | 2 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2014 | 8 | 3 | 108.4082 | 5 | 103.4082 | 29.7832 | 103.4082 | 0.42623 | 29.357 | 92.08% | 236.7308 | 222.527 | 5340.6471
2014 | 8 | 4 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2014 | 8 | 5 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2014 | 8 | 6 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2014 | 8 | 7 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2014 | 8 | 8 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2014 | 8 | 9 | 58.7755 | 5 | 53.7755 | 29.8824 | 53.7755 | 0.11527 | 29.7672 | 89.6% | 121.4658 | 114.1778 | 2740.2679
2014 | 8 | 10 | 48.3265 | 5 | 43.3265 | 29.9033 | 43.3265 | 0.074824 | 29.8285 | 87.1% | 95.3295 | 89.6098 | 2150.6343
2014 | 8 | 11 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2014 | 8 | 12 | 40.4898 | 5 | 35.4898 | 29.919 | 35.4898 | 0.050204 | 29.8688 | 80.09% | 71.8991 | 67.5852 | 1622.0437
2014 | 8 | 13 | 69.2245 | 5 | 64.2245 | 29.8616 | 64.2245 | 0.16441 | 29.6971 | 90.6% | 146.3414 | 137.5609 | 3301.4613
2014 | 8 | 14 | 1112.8163 | 5 | 1107.8163 | 27.7744 | 139.3858 | 0.77441 | 27 | 89.27% | 284.5187 | 267.4476 | 6418.7429
2014 | 8 | 15 | 527.6735 | 5 | 522.6735 | 28.9447 | 139.3858 | 0.77441 | 28.1702 | 89.27% | 296.8509 | 279.0399 | 6696.9568
2014 | 8 | 16 | 282.1224 | 5 | 277.1224 | 29.4358 | 139.3858 | 0.77441 | 28.6613 | 89.27% | 302.026 | 283.9045 | 6813.7073
2014 | 8 | 17 | 195.9184 | 5 | 190.9184 | 29.6082 | 139.3858 | 0.77441 | 28.8338 | 89.27% | 303.8428 | 285.6123 | 6854.6942
2014 | 8 | 18 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
2014 | 8 | 19 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2014 | 8 | 20 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2014 | 8 | 21 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2014 | 8 | 22 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2014 | 8 | 23 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2014 | 8 | 24 | 61.3878 | 5 | 56.3878 | 29.8772 | 56.3878 | 0.12674 | 29.7505 | 89.6% | 127.2948 | 119.6571 | 2871.77
2014 | 8 | 25 | 53.551 | 5 | 48.551 | 29.8929 | 48.551 | 0.093957 | 29.7989 | 88.6% | 108.5567 | 102.0433 | 2449.0388
2014 | 8 | 26 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2014 | 8 | 27 | 41.7959 | 5 | 36.7959 | 29.9164 | 36.7959 | 0.053968 | 29.8624 | 80.09% | 74.5293 | 70.0575 | 1681.3804
2014 | 8 | 28 | 36.5714 | 5 | 31.5714 | 29.9269 | 31.5714 | 0.03973 | 29.8871 | 80.09% | 64.0001 | 60.1601 | 1443.8412
2014 | 8 | 29 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2014 | 8 | 30 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2014 | 8 | 31 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2014 | 9 | 1 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2014 | 9 | 2 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2014 | 9 | 3 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2014 | 9 | 4 | 27.4286 | 15 | 12.4286 | 29.9451 | 12.4286 | 0.0061571 | 29.939 | 40.05% | 12.6207 | 11.8635 | 284.7237
2014 | 9 | 5 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2014 | 9 | 6 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2014 | 9 | 7 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2014 | 9 | 8 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2014 | 9 | 9 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2014 | 9 | 10 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2014 | 9 | 11 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2014 | 9 | 12 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2014 | 9 | 13 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2014 | 9 | 14 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2014 | 9 | 15 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2014 | 9 | 16 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2014 | 9 | 17 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2014 | 9 | 18 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2014 | 9 | 19 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2014 | 9 | 20 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2014 | 9 | 21 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2014 | 9 | 22 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2014 | 9 | 23 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2014 | 9 | 24 | 14.3673 | 15 | 0 | 29.9713 | 0 | 0 | 29.9713 | 0% | 0 | 0 | 0
2014 | 9 | 25 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2014 | 9 | 26 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
2014 | 9 | 27 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
2014 | 9 | 28 | 11.8857 | 15 | 0 | 29.9762 | 0 | 0 | 29.9762 | 0% | 0 | 0 | 0
2014 | 9 | 29 | 11.102 | 15 | 0 | 29.9778 | 0 | 0 | 29.9778 | 0% | 0 | 0 | 0
2014 | 9 | 30 | 10.8408 | 15 | 0 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
2014 | 10 | 1 | 11.4939 | 15 | 0 | 29.977 | 0 | 0 | 29.977 | 0% | 0 | 0 | 0
2014 | 10 | 2 | 12.2776 | 15 | 0 | 29.9754 | 0 | 0 | 29.9754 | 0% | 0 | 0 | 0
2014 | 10 | 3 | 12.4082 | 15 | 0 | 29.9752 | 0 | 0 | 29.9752 | 0% | 0 | 0 | 0
2014 | 10 | 4 | 12.8 | 15 | 0 | 29.9744 | 0 | 0 | 29.9744 | 0% | 0 | 0 | 0
2014 | 10 | 5 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2014 | 10 | 6 | 48.3265 | 15 | 33.3265 | 29.9033 | 33.3265 | 0.04427 | 29.8591 | 80.09% | 67.4945 | 63.4448 | 1522.6761
2014 | 10 | 7 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2014 | 10 | 8 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2014 | 10 | 9 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2014 | 10 | 10 | 35.2653 | 15 | 20.2653 | 29.9295 | 20.2653 | 0.01637 | 29.9131 | 70.08% | 35.9776 | 33.819 | 811.6549
2014 | 10 | 11 | 28.7347 | 15 | 13.7347 | 29.9425 | 13.7347 | 0.0075192 | 29.935 | 70.08% | 24.4015 | 22.9374 | 550.4974
2014 | 10 | 12 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2014 | 10 | 13 | 24.8163 | 15 | 9.8163 | 29.9504 | 9.8163 | 0.0038409 | 29.9465 | 40.05% | 9.9706 | 9.3724 | 224.9369
2014 | 10 | 14 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2014 | 10 | 15 | 23.5102 | 15 | 8.5102 | 29.953 | 8.5102 | 0.0028868 | 29.9501 | 40.05% | 8.645 | 8.1263 | 195.0309
2014 | 10 | 16 | 32.6531 | 15 | 17.6531 | 29.9347 | 17.6531 | 0.012421 | 29.9223 | 70.08% | 31.3496 | 29.4686 | 707.2475
2014 | 10 | 17 | 283.4286 | 15 | 268.4286 | 29.4331 | 139.3858 | 0.77441 | 28.6587 | 89.27% | 301.9985 | 283.8786 | 6813.0863
2014 | 10 | 18 | 151.5102 | 15 | 136.5102 | 29.697 | 136.5102 | 0.74279 | 28.9542 | 90.08% | 301.5287 | 283.4369 | 6802.4868
2014 | 10 | 19 | 96.6531 | 15 | 81.6531 | 29.8067 | 81.6531 | 0.26575 | 29.5409 | 92.11% | 188.16 | 176.8704 | 4244.8888
2014 | 10 | 20 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2014 | 10 | 21 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2014 | 10 | 22 | 167.1837 | 15 | 152.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2014 | 10 | 23 | 289.9592 | 15 | 274.9592 | 29.4201 | 139.3858 | 0.77441 | 28.6457 | 89.27% | 301.8609 | 283.7492 | 6809.9812
2014 | 10 | 24 | 693.551 | 15 | 678.551 | 28.6129 | 139.3858 | 0.77441 | 27.8385 | 89.27% | 293.355 | 275.7537 | 6618.0882
2014 | 10 | 25 | 390.5306 | 15 | 375.5306 | 29.2189 | 139.3858 | 0.77441 | 28.4445 | 89.27% | 299.7413 | 281.7568 | 6762.1632
2014 | 10 | 26 | 258.6122 | 15 | 243.6122 | 29.4828 | 139.3858 | 0.77441 | 28.7084 | 89.27% | 302.5215 | 284.3702 | 6824.8855
2014 | 10 | 27 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2014 | 10 | 28 | 143.6735 | 15 | 128.6735 | 29.7127 | 128.6735 | 0.65995 | 29.0527 | 90.74% | 287.2751 | 270.0386 | 6480.926
2014 | 10 | 29 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
2014 | 10 | 30 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
2014 | 10 | 31 | 97.9592 | 15 | 82.9592 | 29.8041 | 82.9592 | 0.27432 | 29.5298 | 92.11% | 191.0974 | 179.6316 | 4311.1575
2014 | 11 | 1 | 88.8163 | 15 | 73.8163 | 29.8224 | 73.8163 | 0.21719 | 29.6052 | 91.6% | 169.5271 | 159.3555 | 3824.5323
2014 | 11 | 2 | 92.7347 | 15 | 77.7347 | 29.8145 | 77.7347 | 0.24086 | 29.5737 | 91.6% | 178.3361 | 167.6359 | 4023.2624
2014 | 11 | 3 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2014 | 11 | 4 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2014 | 11 | 5 | 70.5306 | 15 | 55.5306 | 29.8589 | 55.5306 | 0.12291 | 29.736 | 89.6% | 125.2988 | 117.7809 | 2826.7418
2014 | 11 | 6 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2014 | 11 | 7 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2014 | 11 | 8 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2014 | 11 | 9 | 79.6735 | 15 | 64.6735 | 29.8407 | 64.6735 | 0.16672 | 29.6739 | 90.6% | 147.2493 | 138.4143 | 3321.9434
2014 | 11 | 10 | 71.8367 | 15 | 56.8367 | 29.8563 | 56.8367 | 0.12876 | 29.7276 | 89.6% | 128.2095 | 120.5169 | 2892.4056
2014 | 11 | 11 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2014 | 11 | 12 | 65.3061 | 15 | 50.3061 | 29.8694 | 50.3061 | 0.10087 | 29.7685 | 88.6% | 112.3661 | 105.6242 | 2534.9797
2014 | 11 | 13 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2014 | 11 | 14 | 62.6939 | 15 | 47.6939 | 29.8746 | 47.6939 | 0.090669 | 29.7839 | 88.6% | 106.5865 | 100.1913 | 2404.5915
2014 | 11 | 15 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2014 | 11 | 16 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2014 | 11 | 17 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2014 | 11 | 18 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
2014 | 11 | 19 | 94.0408 | 15 | 79.0408 | 29.8119 | 79.0408 | 0.24902 | 29.5629 | 91.6% | 181.2665 | 170.3905 | 4089.3721
2014 | 11 | 20 | 77.0612 | 15 | 62.0612 | 29.8459 | 62.0612 | 0.15352 | 29.6924 | 90.6% | 141.3894 | 132.906 | 3189.7447
2014 | 11 | 21 | 66.6122 | 15 | 51.6122 | 29.8668 | 51.6122 | 0.10618 | 29.7606 | 89.6% | 116.5537 | 109.5605 | 2629.4513
2014 | 11 | 22 | 57.4694 | 15 | 42.4694 | 29.8851 | 42.4694 | 0.071893 | 29.8132 | 87.1% | 93.3955 | 87.7918 | 2107.0024
2014 | 11 | 23 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2014 | 11 | 24 | 193.3061 | 15 | 178.3061 | 29.6134 | 139.3858 | 0.77441 | 28.839 | 89.27% | 303.8979 | 285.664 | 6855.9362
2014 | 11 | 25 | 340.898 | 15 | 325.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
2014 | 11 | 26 | 215.5102 | 15 | 200.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2014 | 11 | 27 | 188.0816 | 15 | 173.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2014 | 11 | 28 | 155.4286 | 15 | 140.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2014 | 11 | 29 | 120.1633 | 15 | 105.1633 | 29.7597 | 105.1633 | 0.44082 | 29.3189 | 91.77% | 239.6268 | 225.2492 | 5405.981
2014 | 11 | 30 | 118.8571 | 15 | 103.8571 | 29.7623 | 103.8571 | 0.42994 | 29.3323 | 92.08% | 237.5594 | 223.3058 | 5359.3392
2014 | 12 | 1 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2014 | 12 | 2 | 155.4286 | 5 | 150.4286 | 29.6891 | 139.3858 | 0.77441 | 28.9147 | 89.27% | 304.6962 | 286.4144 | 6873.9456
2014 | 12 | 3 | 137.1429 | 5 | 132.1429 | 29.7257 | 132.1429 | 0.69602 | 29.0297 | 90.74% | 294.7872 | 277.1 | 6650.3988
2014 | 12 | 4 | 134.5306 | 5 | 129.5306 | 29.7309 | 129.5306 | 0.66877 | 29.0622 | 90.74% | 289.2829 | 271.926 | 6526.2231
2014 | 12 | 5 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2014 | 12 | 6 | 114.9388 | 5 | 109.9388 | 29.7701 | 109.9388 | 0.48177 | 29.2884 | 91.77% | 250.2478 | 235.2329 | 5645.5907
2014 | 12 | 7 | 154.1224 | 5 | 149.1224 | 29.6918 | 139.3858 | 0.77441 | 28.9173 | 89.27% | 304.7237 | 286.4403 | 6874.5666
2014 | 12 | 8 | 112.3265 | 5 | 107.3265 | 29.7753 | 107.3265 | 0.45914 | 29.3162 | 91.77% | 244.534 | 229.8619 | 5516.6865
2014 | 12 | 9 | 121.4694 | 5 | 116.4694 | 29.7571 | 116.4694 | 0.5407 | 29.2164 | 91.43% | 263.4816 | 247.6727 | 5944.1446
2014 | 12 | 10 | 508.0816 | 5 | 503.0816 | 28.9838 | 139.3858 | 0.77441 | 28.2094 | 89.27% | 297.2638 | 279.428 | 6706.272
2014 | 12 | 11 | 873.7959 | 5 | 868.7959 | 28.2524 | 139.3858 | 0.77441 | 27.478 | 89.27% | 289.5562 | 272.1828 | 6532.3883
2014 | 12 | 12 | 625.6327 | 5 | 620.6327 | 28.7487 | 139.3858 | 0.77441 | 27.9743 | 89.27% | 294.7864 | 277.0992 | 6650.3808
2014 | 12 | 13 | 415.3469 | 5 | 410.3469 | 29.1693 | 139.3858 | 0.77441 | 28.3949 | 89.27% | 299.2183 | 281.2652 | 6750.364
2014 | 12 | 14 | 310.8571 | 5 | 305.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2014 | 12 | 15 | 250.7755 | 5 | 245.7755 | 29.4984 | 139.3858 | 0.77441 | 28.724 | 89.27% | 302.6867 | 284.5255 | 6828.6116
2014 | 12 | 16 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2014 | 12 | 17 | 363.102 | 5 | 358.102 | 29.2738 | 139.3858 | 0.77441 | 28.4994 | 89.27% | 300.3193 | 282.3002 | 6775.2045
2014 | 12 | 18 | 684.4082 | 5 | 679.4082 | 28.6312 | 139.3858 | 0.77441 | 27.8568 | 89.27% | 293.5477 | 275.9348 | 6622.4353
2014 | 12 | 19 | 444.0816 | 5 | 439.0816 | 29.1118 | 139.3858 | 0.77441 | 28.3374 | 89.27% | 298.6127 | 280.6959 | 6736.7017
2014 | 12 | 20 | 305.6327 | 5 | 300.6327 | 29.3887 | 139.3858 | 0.77441 | 28.6143 | 89.27% | 301.5305 | 283.4387 | 6802.5291
2014 | 12 | 21 | 236.4082 | 5 | 231.4082 | 29.5272 | 139.3858 | 0.77441 | 28.7528 | 89.27% | 302.9895 | 284.8101 | 6835.4428
2014 | 12 | 22 | 206.3673 | 5 | 201.3673 | 29.5873 | 139.3858 | 0.77441 | 28.8129 | 89.27% | 303.6226 | 285.4053 | 6849.7261
2014 | 12 | 23 | 188.0816 | 5 | 183.0816 | 29.6238 | 139.3858 | 0.77441 | 28.8494 | 89.27% | 304.008 | 285.7675 | 6858.4203
2014 | 12 | 24 | 210.2857 | 5 | 205.2857 | 29.5794 | 139.3858 | 0.77441 | 28.805 | 89.27% | 303.54 | 285.3276 | 6847.863
2014 | 12 | 25 | 620.4082 | 5 | 615.4082 | 28.7592 | 139.3858 | 0.77441 | 27.9848 | 89.27% | 294.8965 | 277.2027 | 6652.8649
2014 | 12 | 26 | 645.2245 | 5 | 640.2245 | 28.7096 | 139.3858 | 0.77441 | 27.9351 | 89.27% | 294.3735 | 276.7111 | 6641.0656
2014 | 12 | 27 | 459.7551 | 5 | 454.7551 | 29.0805 | 139.3858 | 0.77441 | 28.3061 | 89.27% | 298.2823 | 280.3854 | 6729.2495
2014 | 12 | 28 | 402.2857 | 5 | 397.2857 | 29.1954 | 139.3858 | 0.77441 | 28.421 | 89.27% | 299.4935 | 281.5239 | 6756.5741
2014 | 12 | 29 | 378.7755 | 5 | 373.7755 | 29.2424 | 139.3858 | 0.77441 | 28.468 | 89.27% | 299.989 | 281.9897 | 6767.7523
2014 | 12 | 30 | 265.1429 | 5 | 260.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2014 | 12 | 31 | 189.3878 | 5 | 184.3878 | 29.6212 | 139.3858 | 0.77441 | 28.8468 | 89.27% | 303.9805 | 285.7416 | 6857.7992
2015 | 1 | 1 | 161.9592 | 5 | 156.9592 | 29.6761 | 139.3858 | 0.77441 | 28.9017 | 89.27% | 304.5585 | 286.285 | 6870.8405
2015 | 1 | 2 | 150.2041 | 5 | 145.2041 | 29.6996 | 139.3858 | 0.77441 | 28.9252 | 89.27% | 304.8063 | 286.5179 | 6876.4296
2015 | 1 | 3 | 124.0816 | 5 | 119.0816 | 29.7518 | 119.0816 | 0.56523 | 29.1866 | 91.43% | 269.1168 | 252.9698 | 6071.2748
2015 | 1 | 4 | 128 | 5 | 123 | 29.744 | 123 | 0.60304 | 29.141 | 91.08% | 276.4749 | 259.8864 | 6237.2734
2015 | 1 | 5 | 139.7551 | 5 | 134.7551 | 29.7205 | 134.7551 | 0.72381 | 28.9967 | 90.08% | 298.0887 | 280.2034 | 6724.8813
2015 | 1 | 6 | 120.1633 | 5 | 115.1633 | 29.7597 | 115.1633 | 0.52864 | 29.231 | 91.43% | 260.6577 | 245.0182 | 5880.4367
2015 | 1 | 7 | 118.8571 | 5 | 113.8571 | 29.7623 | 113.8571 | 0.51672 | 29.2456 | 91.43% | 257.8296 | 242.3598 | 5816.6347
2015 | 1 | 8 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2015 | 1 | 9 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2015 | 1 | 10 | 101.8776 | 5 | 96.8776 | 29.7962 | 96.8776 | 0.37409 | 29.4222 | 92.08% | 222.2729 | 208.9365 | 5014.4769
2015 | 1 | 11 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2015 | 1 | 12 | 94.0408 | 5 | 89.0408 | 29.8119 | 89.0408 | 0.31602 | 29.4959 | 92.22% | 205.116 | 192.809 | 4627.4172
2015 | 1 | 13 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2015 | 1 | 14 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2015 | 1 | 15 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2015 | 1 | 16 | 91.4286 | 5 | 86.4286 | 29.8171 | 86.4286 | 0.29775 | 29.5194 | 92.21% | 199.2354 | 187.2813 | 4494.7502
2015 | 1 | 17 | 86.2041 | 5 | 81.2041 | 29.8276 | 81.2041 | 0.26284 | 29.5648 | 92.11% | 187.2762 | 176.0396 | 4224.9507
2015 | 1 | 18 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2015 | 1 | 19 | 453.2245 | 5 | 448.2245 | 29.0936 | 139.3858 | 0.77441 | 28.3191 | 89.27% | 298.42 | 280.5148 | 6732.3546
2015 | 1 | 20 | 424.4898 | 5 | 419.4898 | 29.151 | 139.3858 | 0.77441 | 28.3766 | 89.27% | 299.0256 | 281.084 | 6746.0169
2015 | 1 | 21 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2015 | 1 | 22 | 205.0612 | 5 | 200.0612 | 29.5899 | 139.3858 | 0.77441 | 28.8155 | 89.27% | 303.6501 | 285.4311 | 6850.3471
2015 | 1 | 23 | 167.1837 | 5 | 162.1837 | 29.6656 | 139.3858 | 0.77441 | 28.8912 | 89.27% | 304.4484 | 286.1815 | 6868.3565
2015 | 1 | 24 | 144.9796 | 5 | 139.9796 | 29.71 | 139.3858 | 0.77441 | 28.9356 | 89.27% | 304.9164 | 286.6214 | 6878.9137
2015 | 1 | 25 | 131.9184 | 5 | 126.9184 | 29.7362 | 126.9184 | 0.64207 | 29.0941 | 90.74% | 283.7604 | 266.7347 | 6401.6337
2015 | 1 | 26 | 104.4898 | 5 | 99.4898 | 29.791 | 99.4898 | 0.39454 | 29.3965 | 92.08% | 228.0672 | 214.3832 | 5145.1962
2015 | 1 | 27 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2015 | 1 | 28 | 99.2653 | 5 | 94.2653 | 29.8015 | 94.2653 | 0.35419 | 29.4473 | 92.2% | 216.7463 | 203.7415 | 4889.7957
2015 | 1 | 29 | 107.102 | 5 | 102.102 | 29.7858 | 102.102 | 0.41553 | 29.3703 | 92.08% | 233.8467 | 219.8159 | 5275.5817
2015 | 1 | 30 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2015 | 1 | 31 | 103.1837 | 5 | 98.1837 | 29.7936 | 98.1837 | 0.38425 | 29.4094 | 92.08% | 225.1719 | 211.6616 | 5079.8778
2015 | 2 | 1 | 96.6531 | 5 | 91.6531 | 29.8067 | 91.6531 | 0.33483 | 29.4719 | 92.22% | 210.9616 | 198.3039 | 4759.2926
2015 | 2 | 2 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2015 | 2 | 3 | 92.7347 | 5 | 87.7347 | 29.8145 | 87.7347 | 0.30682 | 29.5077 | 92.22% | 202.1882 | 190.0569 | 4561.365
2015 | 2 | 4 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2015 | 2 | 5 | 87.5102 | 5 | 82.5102 | 29.825 | 82.5102 | 0.27136 | 29.5536 | 92.11% | 190.2167 | 178.8037 | 4291.2898
2015 | 2 | 6 | 84.898 | 5 | 79.898 | 29.8302 | 79.898 | 0.25445 | 29.5758 | 92.11% | 184.3325 | 173.2726 | 4158.5413
2015 | 2 | 7 | 83.5918 | 5 | 78.5918 | 29.8328 | 78.5918 | 0.2462 | 29.5866 | 91.6% | 180.3814 | 169.5586 | 4069.4054
2015 | 2 | 8 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2015 | 2 | 9 | 80.9796 | 5 | 75.9796 | 29.838 | 75.9796 | 0.23011 | 29.6079 | 91.6% | 174.5116 | 164.0409 | 3936.9808
2015 | 2 | 10 | 79.6735 | 5 | 74.6735 | 29.8407 | 74.6735 | 0.22226 | 29.6184 | 91.6% | 171.5722 | 161.2779 | 3870.6688
2015 | 2 | 11 | 78.3673 | 5 | 73.3673 | 29.8433 | 73.3673 | 0.21456 | 29.6287 | 91.6% | 168.6299 | 158.5121 | 3804.2914
2015 | 2 | 12 | 77.0612 | 5 | 72.0612 | 29.8459 | 72.0612 | 0.20698 | 29.6389 | 91.6% | 165.6848 | 155.7437 | 3737.8498
2015 | 2 | 13 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2015 | 2 | 14 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2015 | 2 | 15 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2015 | 2 | 16 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2015 | 2 | 17 | 71.8367 | 5 | 66.8367 | 29.8563 | 66.8367 | 0.17806 | 29.6783 | 90.6% | 152.1968 | 143.065 | 3433.5606
2015 | 2 | 18 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2015 | 2 | 19 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2015 | 2 | 20 | 70.5306 | 5 | 65.5306 | 29.8589 | 65.5306 | 0.17117 | 29.6878 | 90.6% | 149.2704 | 140.3142 | 3367.54
2015 | 2 | 21 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2015 | 2 | 22 | 67.9184 | 5 | 62.9184 | 29.8642 | 62.9184 | 0.15779 | 29.7064 | 90.6% | 143.4098 | 134.8052 | 3235.3255
2015 | 2 | 23 | 66.6122 | 5 | 61.6122 | 29.8668 | 61.6122 | 0.15131 | 29.7155 | 90.6% | 140.4758 | 132.0472 | 3169.1334
2015 | 2 | 24 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2015 | 2 | 25 | 65.3061 | 5 | 60.3061 | 29.8694 | 60.3061 | 0.14496 | 29.7244 | 90.6% | 137.5393 | 129.2869 | 3102.886
2015 | 2 | 26 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2015 | 2 | 27 | 64 | 5 | 59 | 29.872 | 59 | 0.13875 | 29.7332 | 89.6% | 133.1147 | 125.1278 | 3003.0678
2015 | 2 | 28 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2015 | 3 | 1 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2015 | 3 | 2 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2015 | 3 | 3 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2015 | 3 | 4 | 64 | 25 | 39 | 29.872 | 39 | 0.060627 | 29.8114 | 87.1% | 85.7607 | 80.6151 | 1934.7618
2015 | 3 | 5 | 66.6122 | 25 | 41.6122 | 29.8668 | 41.6122 | 0.06902 | 29.7978 | 87.1% | 91.4632 | 85.9754 | 2063.4103
2015 | 3 | 6 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2015 | 3 | 7 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2015 | 3 | 8 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2015 | 3 | 9 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2015 | 3 | 10 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2015 | 3 | 11 | 70.5306 | 25 | 45.5306 | 29.8589 | 45.5306 | 0.082631 | 29.7763 | 88.6% | 101.7259 | 95.6224 | 2294.9372
2015 | 3 | 12 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2015 | 3 | 13 | 80.9796 | 25 | 55.9796 | 29.838 | 55.9796 | 0.12491 | 29.7131 | 89.6% | 126.2147 | 118.6418 | 2847.4029
2015 | 3 | 14 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2015 | 3 | 15 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2015 | 3 | 16 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2015 | 3 | 17 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2015 | 3 | 18 | 69.2245 | 25 | 44.2245 | 29.8616 | 44.2245 | 0.077958 | 29.7836 | 87.1% | 97.1587 | 91.3292 | 2191.9005
2015 | 3 | 19 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2015 | 3 | 20 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2015 | 3 | 21 | 62.6939 | 25 | 37.6939 | 29.8746 | 37.6939 | 0.056634 | 29.818 | 80.09% | 76.2344 | 71.6603 | 1719.848
2015 | 3 | 22 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2015 | 3 | 23 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2015 | 3 | 24 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2015 | 3 | 25 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2015 | 3 | 26 | 67.9184 | 25 | 42.9184 | 29.8642 | 42.9184 | 0.073421 | 29.7907 | 87.1% | 94.3119 | 88.6532 | 2127.6756
2015 | 3 | 27 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2015 | 3 | 28 | 159.3469 | 25 | 134.3469 | 29.6813 | 134.3469 | 0.71943 | 28.9619 | 90.08% | 296.8291 | 279.0194 | 6696.4645
2015 | 3 | 29 | 137.1429 | 25 | 112.1429 | 29.7257 | 112.1429 | 0.50128 | 29.2244 | 91.77% | 254.7078 | 239.4253 | 5746.207
2015 | 3 | 30 | 130.6122 | 25 | 105.6122 | 29.7388 | 105.6122 | 0.44459 | 29.2942 | 91.77% | 240.4474 | 226.0205 | 5424.4929
2015 | 3 | 31 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2015 | 4 | 1 | 121.4694 | 25 | 96.4694 | 29.7571 | 96.4694 | 0.37095 | 29.3861 | 92.08% | 221.0653 | 207.8014 | 4987.2338
2015 | 4 | 2 | 112.3265 | 25 | 87.3265 | 29.7753 | 87.3265 | 0.30397 | 29.4714 | 92.22% | 200.9997 | 188.9397 | 4534.5537
2015 | 4 | 3 | 139.7551 | 25 | 114.7551 | 29.7205 | 114.7551 | 0.5249 | 29.1956 | 91.43% | 259.4189 | 243.8538 | 5852.4903
2015 | 4 | 4 | 340.898 | 25 | 315.898 | 29.3182 | 139.3858 | 0.77441 | 28.5438 | 89.27% | 300.7873 | 282.7401 | 6785.7617
2015 | 4 | 5 | 355.2653 | 25 | 330.2653 | 29.2895 | 139.3858 | 0.77441 | 28.5151 | 89.27% | 300.4845 | 282.4554 | 6778.9306
2015 | 4 | 6 | 265.1429 | 25 | 240.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2015 | 4 | 7 | 215.5102 | 25 | 190.5102 | 29.569 | 139.3858 | 0.77441 | 28.7946 | 89.27% | 303.4299 | 285.2241 | 6845.379
2015 | 4 | 8 | 235.102 | 25 | 210.102 | 29.5298 | 139.3858 | 0.77441 | 28.7554 | 89.27% | 303.017 | 284.836 | 6836.0638
2015 | 4 | 9 | 216.8163 | 25 | 191.8163 | 29.5664 | 139.3858 | 0.77441 | 28.792 | 89.27% | 303.4024 | 285.1982 | 6844.758
2015 | 4 | 10 | 219.4286 | 25 | 194.4286 | 29.5611 | 139.3858 | 0.77441 | 28.7867 | 89.27% | 303.3473 | 285.1465 | 6843.5159
2015 | 4 | 11 | 338.2857 | 25 | 313.2857 | 29.3234 | 139.3858 | 0.77441 | 28.549 | 89.27% | 300.8424 | 282.7918 | 6787.0037
2015 | 4 | 12 | 421.8776 | 25 | 396.8776 | 29.1562 | 139.3858 | 0.77441 | 28.3818 | 89.27% | 299.0806 | 281.1358 | 6747.2589
2015 | 4 | 13 | 704 | 25 | 679 | 28.592 | 139.3858 | 0.77441 | 27.8176 | 89.27% | 293.1348 | 275.5467 | 6613.1201
2015 | 4 | 14 | 1133.7143 | 25 | 1108.7143 | 27.7326 | 139.3858 | 0.77441 | 26.9582 | 89.27% | 284.0783 | 267.0336 | 6408.8067
2015 | 4 | 15 | 1110.2041 | 25 | 1085.2041 | 27.7796 | 139.3858 | 0.77441 | 27.0052 | 89.27% | 284.5738 | 267.4994 | 6419.985
2015 | 4 | 16 | 811.102 | 25 | 786.102 | 28.3778 | 139.3858 | 0.77441 | 27.6034 | 89.27% | 290.8775 | 273.4249 | 6562.197
2015 | 4 | 17 | 651.7551 | 25 | 626.7551 | 28.6965 | 139.3858 | 0.77441 | 27.9221 | 89.27% | 294.2358 | 276.5817 | 6637.9606
2015 | 4 | 18 | 621.7143 | 25 | 596.7143 | 28.7566 | 139.3858 | 0.77441 | 27.9822 | 89.27% | 294.869 | 277.1768 | 6652.2439
2015 | 4 | 19 | 774.5306 | 25 | 749.5306 | 28.4509 | 139.3858 | 0.77441 | 27.6765 | 89.27% | 291.6483 | 274.1494 | 6579.5853
2015 | 4 | 20 | 521.1429 | 25 | 496.1429 | 28.9577 | 139.3858 | 0.77441 | 28.1833 | 89.27% | 296.9886 | 279.1692 | 6700.0619
2015 | 4 | 21 | 1802.449 | 25 | 1777.449 | 26.3951 | 139.3858 | 0.77441 | 25.6207 | 89.27% | 269.9844 | 253.7853 | 6090.848
2015 | 4 | 22 | 1384.4898 | 25 | 1359.4898 | 27.231 | 139.3858 | 0.77441 | 26.4566 | 89.27% | 278.7931 | 262.0655 | 6289.5722
2015 | 4 | 23 | 872.4898 | 25 | 847.4898 | 28.255 | 139.3858 | 0.77441 | 27.4806 | 89.27% | 289.5837 | 272.2087 | 6533.0094
2015 | 4 | 24 | 624.3265 | 25 | 599.3265 | 28.7513 | 139.3858 | 0.77441 | 27.9769 | 89.27% | 294.8139 | 277.1251 | 6651.0019
2015 | 4 | 25 | 441.4694 | 25 | 416.4694 | 29.1171 | 139.3858 | 0.77441 | 28.3427 | 89.27% | 298.6677 | 280.7477 | 6737.9437
2015 | 4 | 26 | 351.3469 | 25 | 326.3469 | 29.2973 | 139.3858 | 0.77441 | 28.5229 | 89.27% | 300.5671 | 282.5331 | 6780.7936
2015 | 4 | 27 | 284.7347 | 25 | 259.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
2015 | 4 | 28 | 257.3061 | 25 | 232.3061 | 29.4854 | 139.3858 | 0.77441 | 28.711 | 89.27% | 302.549 | 284.3961 | 6825.5066
2015 | 4 | 29 | 225.9592 | 25 | 200.9592 | 29.5481 | 139.3858 | 0.77441 | 28.7737 | 89.27% | 303.2097 | 285.0171 | 6840.4109
2015 | 4 | 30 | 203.7551 | 25 | 178.7551 | 29.5925 | 139.3858 | 0.77441 | 28.8181 | 89.27% | 303.6777 | 285.457 | 6850.9681
2015 | 5 | 1 | 182.8571 | 25 | 157.8571 | 29.6343 | 139.3858 | 0.77441 | 28.8599 | 89.27% | 304.1181 | 285.871 | 6860.9043
2015 | 5 | 2 | 165.8776 | 25 | 140.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2015 | 5 | 3 | 151.5102 | 25 | 126.5102 | 29.697 | 126.5102 | 0.63795 | 29.059 | 90.74% | 282.5069 | 265.5565 | 6373.3567
2015 | 5 | 4 | 138.449 | 25 | 113.449 | 29.7231 | 113.449 | 0.51302 | 29.2101 | 91.43% | 256.5935 | 241.1979 | 5788.7504
2015 | 5 | 5 | 128 | 25 | 103 | 29.744 | 103 | 0.42287 | 29.3211 | 92.08% | 235.5087 | 221.3781 | 5313.0753
2015 | 5 | 6 | 116.2449 | 25 | 91.2449 | 29.7675 | 91.2449 | 0.33186 | 29.4357 | 92.22% | 209.764 | 197.1782 | 4732.2767
2015 | 5 | 7 | 107.102 | 25 | 82.102 | 29.7858 | 82.102 | 0.26868 | 29.5171 | 92.11% | 189.042 | 177.6995 | 4264.787
2015 | 5 | 8 | 99.2653 | 25 | 74.2653 | 29.8015 | 74.2653 | 0.21984 | 29.5816 | 91.6% | 170.4226 | 160.1972 | 3844.734
2015 | 5 | 9 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2015 | 5 | 10 | 90.1224 | 25 | 65.1224 | 29.8198 | 65.1224 | 0.16904 | 29.6507 | 90.6% | 148.1555 | 139.2661 | 3342.3876
2015 | 5 | 11 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2015 | 5 | 12 | 125.3878 | 25 | 100.3878 | 29.7492 | 100.3878 | 0.40169 | 29.3475 | 92.08% | 229.7425 | 215.9579 | 5182.9899
2015 | 5 | 13 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2015 | 5 | 14 | 96.6531 | 25 | 71.6531 | 29.8067 | 71.6531 | 0.20465 | 29.602 | 91.6% | 164.5416 | 154.6691 | 3712.0578
2015 | 5 | 15 | 84.898 | 25 | 59.898 | 29.8302 | 59.898 | 0.14301 | 29.6872 | 90.6% | 136.4373 | 128.251 | 3078.0252
2015 | 5 | 16 | 78.3673 | 25 | 53.3673 | 29.8433 | 53.3673 | 0.11352 | 29.7297 | 89.6% | 120.3922 | 113.1687 | 2716.0485
2015 | 5 | 17 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2015 | 5 | 18 | 88.8163 | 25 | 63.8163 | 29.8224 | 63.8163 | 0.16233 | 29.66 | 90.6% | 145.2297 | 136.5159 | 3276.3814
2015 | 5 | 19 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
2015 | 5 | 20 | 91.4286 | 25 | 66.4286 | 29.8171 | 66.4286 | 0.17589 | 29.6413 | 90.6% | 151.0787 | 142.014 | 3408.336
2015 | 5 | 21 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2015 | 5 | 22 | 65.3061 | 25 | 40.3061 | 29.8694 | 40.3061 | 0.064755 | 29.8046 | 87.1% | 88.6128 | 83.2961 | 1999.1054
2015 | 5 | 23 | 57.4694 | 25 | 32.4694 | 29.8851 | 32.4694 | 0.042023 | 29.843 | 80.09% | 65.7233 | 61.7799 | 1482.7167
2015 | 5 | 24 | 52.2449 | 25 | 27.2449 | 29.8955 | 27.2449 | 0.029587 | 29.8659 | 80.09% | 55.1903 | 51.8789 | 1245.0941
2015 | 5 | 25 | 48.3265 | 25 | 23.3265 | 29.9033 | 23.3265 | 0.021689 | 29.8817 | 80.09% | 47.2777 | 44.4411 | 1066.586
2015 | 5 | 26 | 47.0204 | 25 | 22.0204 | 29.906 | 22.0204 | 0.019328 | 29.8866 | 70.08% | 39.0589 | 36.7154 | 881.1689
2015 | 5 | 27 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
2015 | 5 | 28 | 43.102 | 25 | 18.102 | 29.9138 | 18.102 | 0.013061 | 29.9007 | 70.08% | 32.1238 | 30.1964 | 724.7133
2015 | 5 | 29 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
2015 | 5 | 30 | 40.4898 | 25 | 15.4898 | 29.919 | 15.4898 | 0.0095637 | 29.9095 | 70.08% | 27.4962 | 25.8464 | 620.3133
2015 | 5 | 31 | 53.551 | 25 | 28.551 | 29.8929 | 28.551 | 0.032492 | 29.8604 | 80.09% | 57.8255 | 54.356 | 1304.543
2015 | 6 | 1 | 192 | 25 | 167 | 29.616 | 139.3858 | 0.77441 | 28.8416 | 89.27% | 303.9254 | 285.6899 | 6856.5572
2015 | 6 | 2 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2015 | 6 | 3 | 237.7143 | 25 | 212.7143 | 29.5246 | 139.3858 | 0.77441 | 28.7502 | 89.27% | 302.962 | 284.7842 | 6834.8218
2015 | 6 | 4 | 160.6531 | 25 | 135.6531 | 29.6787 | 135.6531 | 0.73349 | 28.9452 | 90.08% | 299.5424 | 281.5698 | 6757.676
2015 | 6 | 5 | 117.551 | 25 | 92.551 | 29.7649 | 92.551 | 0.34143 | 29.4235 | 92.2% | 212.6325 | 199.8746 | 4796.9899
2015 | 6 | 6 | 94.0408 | 25 | 69.0408 | 29.8119 | 69.0408 | 0.19 | 29.6219 | 90.6% | 156.9174 | 147.5023 | 3540.0557
2015 | 6 | 7 | 74.449 | 25 | 49.449 | 29.8511 | 49.449 | 0.097465 | 29.7536 | 88.6% | 110.3964 | 103.7726 | 2490.542
2015 | 6 | 8 | 61.3878 | 25 | 36.3878 | 29.8772 | 36.3878 | 0.052777 | 29.8244 | 80.09% | 73.6088 | 69.1923 | 1660.6141
2015 | 6 | 9 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2015 | 6 | 10 | 173.7143 | 25 | 148.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2015 | 6 | 11 | 118.8571 | 25 | 93.8571 | 29.7623 | 93.8571 | 0.35113 | 29.4112 | 92.2% | 215.543 | 202.6105 | 4862.6508
2015 | 6 | 12 | 86.2041 | 25 | 61.2041 | 29.8276 | 61.2041 | 0.14931 | 29.6783 | 90.6% | 139.3705 | 131.0083 | 3144.1992
2015 | 6 | 13 | 92.7347 | 25 | 67.7347 | 29.8145 | 67.7347 | 0.18288 | 29.6317 | 90.6% | 153.9994 | 144.7594 | 3474.2257
2015 | 6 | 14 | 75.7551 | 25 | 50.7551 | 29.8485 | 50.7551 | 0.10268 | 29.7458 | 88.6% | 113.2825 | 106.4856 | 2555.6534
2015 | 6 | 15 | 58.7755 | 25 | 33.7755 | 29.8824 | 33.7755 | 0.045471 | 29.837 | 80.09% | 68.3532 | 64.252 | 1542.0476
2015 | 6 | 16 | 60.0816 | 25 | 35.0816 | 29.8798 | 35.0816 | 0.049056 | 29.8308 | 80.09% | 70.9817 | 66.7228 | 1601.347
2015 | 6 | 17 | 71.8367 | 25 | 46.8367 | 29.8563 | 46.8367 | 0.087439 | 29.7689 | 88.6% | 104.618 | 98.341 | 2360.183
2015 | 6 | 18 | 54.8571 | 25 | 29.8571 | 29.8903 | 29.8571 | 0.035533 | 29.8548 | 80.09% | 60.4594 | 56.8318 | 1363.9636
2015 | 6 | 19 | 49.6327 | 25 | 24.6327 | 29.9007 | 24.6327 | 0.024186 | 29.8765 | 80.09% | 49.9164 | 46.9215 | 1126.1148
2015 | 6 | 20 | 44.4082 | 25 | 19.4082 | 29.9112 | 19.4082 | 0.015014 | 29.8962 | 70.08% | 34.4364 | 32.3702 | 776.8852
2015 | 6 | 21 | 103.1837 | 25 | 78.1837 | 29.7936 | 78.1837 | 0.24365 | 29.55 | 91.6% | 179.2225 | 168.4691 | 4043.2587
2015 | 6 | 22 | 177.6327 | 25 | 152.6327 | 29.6447 | 139.3858 | 0.77441 | 28.8703 | 89.27% | 304.2282 | 285.9745 | 6863.3884
2015 | 6 | 23 | 224.6531 | 25 | 199.6531 | 29.5507 | 139.3858 | 0.77441 | 28.7763 | 89.27% | 303.2372 | 285.043 | 6841.0319
2015 | 6 | 24 | 280.8163 | 25 | 255.8163 | 29.4384 | 139.3858 | 0.77441 | 28.664 | 89.27% | 302.0536 | 283.9303 | 6814.3283
2015 | 6 | 25 | 158.0408 | 25 | 133.0408 | 29.6839 | 133.0408 | 0.70551 | 28.9784 | 90.08% | 294.1111 | 276.4645 | 6635.1469
2015 | 6 | 26 | 105.7959 | 25 | 80.7959 | 29.7884 | 80.7959 | 0.2602 | 29.5282 | 92.11% | 186.1045 | 174.9382 | 4198.5178
2015 | 6 | 27 | 77.0612 | 25 | 52.0612 | 29.8459 | 52.0612 | 0.10803 | 29.7378 | 89.6% | 117.4777 | 110.4291 | 2650.2974
2015 | 6 | 28 | 309.551 | 25 | 284.551 | 29.3809 | 139.3858 | 0.77441 | 28.6065 | 89.27% | 301.448 | 283.3611 | 6800.666
2015 | 6 | 29 | 602.1224 | 25 | 577.1224 | 28.7958 | 139.3858 | 0.77441 | 28.0213 | 89.27% | 295.2819 | 277.565 | 6661.5591
2015 | 6 | 30 | 310.8571 | 25 | 285.8571 | 29.3783 | 139.3858 | 0.77441 | 28.6039 | 89.27% | 301.4204 | 283.3352 | 6800.045
2015 | 7 | 1 | 265.1429 | 5 | 260.1429 | 29.4697 | 139.3858 | 0.77441 | 28.6953 | 89.27% | 302.3839 | 284.2409 | 6821.7805
2015 | 7 | 2 | 385.3061 | 5 | 380.3061 | 29.2294 | 139.3858 | 0.77441 | 28.455 | 89.27% | 299.8514 | 281.8603 | 6764.6473
2015 | 7 | 3 | 222.0408 | 5 | 217.0408 | 29.5559 | 139.3858 | 0.77441 | 28.7815 | 89.27% | 303.2923 | 285.0947 | 6842.2739
2015 | 7 | 4 | 147.5918 | 5 | 142.5918 | 29.7048 | 139.3858 | 0.77441 | 28.9304 | 89.27% | 304.8613 | 286.5697 | 6877.6717
2015 | 7 | 5 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2015 | 7 | 6 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2015 | 7 | 7 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2015 | 7 | 8 | 88.8163 | 5 | 83.8163 | 29.8224 | 83.8163 | 0.28002 | 29.5423 | 92.11% | 193.1541 | 181.5649 | 4357.5576
2015 | 7 | 9 | 73.1429 | 5 | 68.1429 | 29.8537 | 68.1429 | 0.18509 | 29.6686 | 90.6% | 155.1207 | 145.8134 | 3499.5222
2015 | 7 | 10 | 62.6939 | 5 | 57.6939 | 29.8746 | 57.6939 | 0.13268 | 29.7419 | 89.6% | 130.2059 | 122.3935 | 2937.4449
2015 | 7 | 11 | 50.9388 | 5 | 45.9388 | 29.8981 | 45.9388 | 0.084119 | 29.814 | 88.6% | 102.7678 | 96.6017 | 2318.4417
2015 | 7 | 12 | 44.4082 | 5 | 39.4082 | 29.9112 | 39.4082 | 0.061902 | 29.8493 | 87.1% | 86.7685 | 81.5624 | 1957.4964
2015 | 7 | 13 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2015 | 7 | 14 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2015 | 7 | 15 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2015 | 7 | 16 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2015 | 7 | 17 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2015 | 7 | 18 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2015 | 7 | 19 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2015 | 7 | 20 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2015 | 7 | 21 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2015 | 7 | 22 | 35.2653 | 5 | 30.2653 | 29.9295 | 30.2653 | 0.036511 | 29.893 | 80.09% | 61.3643 | 57.6825 | 1384.379
2015 | 7 | 23 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2015 | 7 | 24 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2015 | 7 | 25 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2015 | 7 | 26 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2015 | 7 | 27 | 28.7347 | 5 | 23.7347 | 29.9425 | 23.7347 | 0.022454 | 29.9201 | 80.09% | 48.1669 | 45.2768 | 1086.6442
2015 | 7 | 28 | 27.4286 | 5 | 22.4286 | 29.9451 | 22.4286 | 0.020051 | 29.9251 | 70.08% | 39.8341 | 37.444 | 898.657
2015 | 7 | 29 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2015 | 7 | 30 | 24.8163 | 5 | 19.8163 | 29.9504 | 19.8163 | 0.015652 | 29.9347 | 70.08% | 35.2059 | 33.0936 | 794.2462
2015 | 7 | 31 | 33.9592 | 5 | 28.9592 | 29.9321 | 28.9592 | 0.033428 | 29.8987 | 80.09% | 58.7273 | 55.2036 | 1324.8875
2015 | 8 | 1 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2015 | 8 | 2 | 23.5102 | 5 | 18.5102 | 29.953 | 18.5102 | 0.013657 | 29.9393 | 70.08% | 32.8905 | 30.9171 | 742.0104
2015 | 8 | 3 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2015 | 8 | 4 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2015 | 8 | 5 | 15.6735 | 5 | 10.6735 | 29.9687 | 10.6735 | 0.0045409 | 29.9641 | 40.05% | 10.8476 | 10.1967 | 244.7216
2015 | 8 | 6 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2015 | 8 | 7 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
2015 | 8 | 8 | 10.8408 | 5 | 5.8408 | 29.9783 | 0 | 0 | 29.9783 | 0% | 0 | 0 | 0
2015 | 8 | 9 | 9.6653 | 5 | 4.6653 | 29.9807 | 0 | 0 | 29.9807 | 0% | 0 | 0 | 0
2015 | 8 | 10 | 9.0122 | 5 | 4.0122 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2015 | 8 | 11 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2015 | 8 | 12 | 90.1224 | 5 | 85.1224 | 29.8198 | 85.1224 | 0.28882 | 29.5309 | 92.21% | 196.3012 | 184.5232 | 4428.5559
2015 | 8 | 13 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2015 | 8 | 14 | 30.0408 | 5 | 25.0408 | 29.9399 | 25.0408 | 0.024994 | 29.9149 | 80.09% | 50.8087 | 47.7602 | 1146.245
2015 | 8 | 15 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2015 | 8 | 16 | 19.5918 | 5 | 14.5918 | 29.9608 | 14.5918 | 0.008487 | 29.9523 | 70.08% | 25.9393 | 24.3829 | 585.1907
2015 | 8 | 17 | 16.9796 | 5 | 11.9796 | 29.966 | 11.9796 | 0.0057203 | 29.9603 | 40.05% | 12.1735 | 11.4431 | 274.6336
2015 | 8 | 18 | 14.3673 | 5 | 9.3673 | 29.9713 | 9.3673 | 0.0034976 | 29.9678 | 40.05% | 9.5213 | 8.95 | 214.801
2015 | 8 | 19 | 11.6245 | 5 | 6.6245 | 29.9768 | 6.6245 | 0.0017492 | 29.975 | 40.05% | 6.735 | 6.3309 | 151.9417
2015 | 8 | 20 | 10.7102 | 5 | 5.7102 | 29.9786 | 0 | 0 | 29.9786 | 0% | 0 | 0 | 0
2015 | 8 | 21 | 12.4082 | 5 | 7.4082 | 29.9752 | 7.4082 | 0.0021875 | 29.973 | 40.05% | 7.5312 | 7.0794 | 169.9049
2015 | 8 | 22 | 37.8776 | 5 | 32.8776 | 29.9242 | 32.8776 | 0.043086 | 29.8812 | 80.09% | 66.6345 | 62.6364 | 1503.2733
2015 | 8 | 23 | 31.3469 | 5 | 26.3469 | 29.9373 | 26.3469 | 0.027669 | 29.9096 | 80.09% | 53.4495 | 50.2425 | 1205.8196
2015 | 8 | 24 | 56.1633 | 5 | 51.1633 | 29.8877 | 51.1633 | 0.10434 | 29.7833 | 88.6% | 114.3376 | 107.4773 | 2579.4555
2015 | 8 | 25 | 45.7143 | 5 | 40.7143 | 29.9086 | 40.7143 | 0.066074 | 29.8425 | 87.1% | 89.6239 | 84.2465 | 2021.915
2015 | 8 | 26 | 117.551 | 5 | 112.551 | 29.7649 | 112.551 | 0.50493 | 29.26 | 91.77% | 255.9456 | 240.5888 | 5774.1324
2015 | 8 | 27 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2015 | 8 | 28 | 47.0204 | 5 | 42.0204 | 29.906 | 42.0204 | 0.070381 | 29.8356 | 87.1% | 92.4776 | 86.9289 | 2086.2946
2015 | 8 | 29 | 32.6531 | 5 | 27.6531 | 29.9347 | 27.6531 | 0.03048 | 29.9042 | 80.09% | 56.089 | 52.7236 | 1265.3674
2015 | 8 | 30 | 26.1224 | 5 | 21.1224 | 29.9478 | 21.1224 | 0.017784 | 29.93 | 70.08% | 37.5205 | 35.2692 | 846.4619
2015 | 8 | 31 | 22.2041 | 5 | 17.2041 | 29.9556 | 17.2041 | 0.011798 | 29.9438 | 70.08% | 30.5743 | 28.7398 | 689.7555
2015 | 9 | 1 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2015 | 9 | 2 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2015 | 9 | 3 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2015 | 9 | 4 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2015 | 9 | 5 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2015 | 9 | 6 | 10.9714 | 15 | 0 | 29.9781 | 0 | 0 | 29.9781 | 0% | 0 | 0 | 0
2015 | 9 | 7 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
2015 | 9 | 8 | 8.6204 | 15 | 0 | 29.9828 | 0 | 0 | 29.9828 | 0% | 0 | 0 | 0
2015 | 9 | 9 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2015 | 9 | 10 | 7.7061 | 15 | 0 | 29.9846 | 0 | 0 | 29.9846 | 0% | 0 | 0 | 0
2015 | 9 | 11 | 18.2857 | 15 | 3.2857 | 29.9634 | 0 | 0 | 29.9634 | 0% | 0 | 0 | 0
2015 | 9 | 12 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2015 | 9 | 13 | 19.5918 | 15 | 4.5918 | 29.9608 | 0 | 0 | 29.9608 | 0% | 0 | 0 | 0
2015 | 9 | 14 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2015 | 9 | 15 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2015 | 9 | 16 | 33.9592 | 15 | 18.9592 | 29.9321 | 18.9592 | 0.014328 | 29.9178 | 70.08% | 33.6641 | 31.6442 | 759.461
2015 | 9 | 17 | 26.1224 | 15 | 11.1224 | 29.9478 | 11.1224 | 0.004931 | 29.9428 | 40.05% | 11.2959 | 10.6181 | 254.8346
2015 | 9 | 18 | 20.898 | 15 | 5.898 | 29.9582 | 0 | 0 | 29.9582 | 0% | 0 | 0 | 0
2015 | 9 | 19 | 16.9796 | 15 | 1.9796 | 29.966 | 0 | 0 | 29.966 | 0% | 0 | 0 | 0
2015 | 9 | 20 | 15.6735 | 15 | 0.67347 | 29.9687 | 0 | 0 | 29.9687 | 0% | 0 | 0 | 0
2015 | 9 | 21 | 13.0612 | 15 | 0 | 29.9739 | 0 | 0 | 29.9739 | 0% | 0 | 0 | 0
2015 | 9 | 22 | 11.7551 | 15 | 0 | 29.9765 | 0 | 0 | 29.9765 | 0% | 0 | 0 | 0
2015 | 9 | 23 | 10.5796 | 15 | 0 | 29.9788 | 0 | 0 | 29.9788 | 0% | 0 | 0 | 0
2015 | 9 | 24 | 9.9265 | 15 | 0 | 29.9801 | 0 | 0 | 29.9801 | 0% | 0 | 0 | 0
2015 | 9 | 25 | 9.0122 | 15 | 0 | 29.982 | 0 | 0 | 29.982 | 0% | 0 | 0 | 0
2015 | 9 | 26 | 8.2286 | 15 | 0 | 29.9835 | 0 | 0 | 29.9835 | 0% | 0 | 0 | 0
2015 | 9 | 27 | 7.8367 | 15 | 0 | 29.9843 | 0 | 0 | 29.9843 | 0% | 0 | 0 | 0
2015 | 9 | 28 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
2015 | 9 | 29 | 7.5755 | 15 | 0 | 29.9848 | 0 | 0 | 29.9848 | 0% | 0 | 0 | 0
2015 | 9 | 30 | 668.7347 | 15 | 653.7347 | 28.6625 | 139.3858 | 0.77441 | 27.8881 | 89.27% | 293.878 | 276.2453 | 6629.8874
2015 | 10 | 1 | 1009.6327 | 15 | 994.6327 | 27.9807 | 139.3858 | 0.77441 | 27.2063 | 89.27% | 286.6934 | 269.4918 | 6467.803
2015 | 10 | 2 | 333.0612 | 15 | 318.0612 | 29.3339 | 139.3858 | 0.77441 | 28.5595 | 89.27% | 300.9525 | 282.8953 | 6789.4878
2015 | 10 | 3 | 185.4694 | 15 | 170.4694 | 29.6291 | 139.3858 | 0.77441 | 28.8547 | 89.27% | 304.063 | 285.8193 | 6859.6623
2015 | 10 | 4 | 125.3878 | 15 | 110.3878 | 29.7492 | 110.3878 | 0.48571 | 29.2635 | 91.77% | 251.0567 | 235.9933 | 5663.8388
2015 | 10 | 5 | 91.4286 | 15 | 76.4286 | 29.8171 | 76.4286 | 0.23283 | 29.5843 | 91.6% | 175.4027 | 164.8786 | 3957.0852
2015 | 10 | 6 | 73.1429 | 15 | 58.1429 | 29.8537 | 58.1429 | 0.13475 | 29.719 | 89.6% | 131.1178 | 123.2507 | 2958.018
2015 | 10 | 7 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2015 | 10 | 8 | 52.2449 | 15 | 37.2449 | 29.8955 | 37.2449 | 0.055293 | 29.8402 | 80.09% | 75.3825 | 70.8596 | 1700.6299
2015 | 10 | 9 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2015 | 10 | 10 | 121.4694 | 15 | 106.4694 | 29.7571 | 106.4694 | 0.45184 | 29.3052 | 91.77% | 242.4902 | 227.9408 | 5470.5786
2015 | 10 | 11 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2015 | 10 | 12 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2015 | 10 | 13 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2015 | 10 | 14 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2015 | 10 | 15 | 58.7755 | 15 | 43.7755 | 29.8824 | 43.7755 | 0.076383 | 29.8061 | 87.1% | 96.2449 | 90.4702 | 2171.2847
2015 | 10 | 16 | 50.9388 | 15 | 35.9388 | 29.8981 | 35.9388 | 0.051483 | 29.8466 | 80.09% | 72.7546 | 68.3894 | 1641.3446
2015 | 10 | 17 | 47.0204 | 15 | 32.0204 | 29.906 | 32.0204 | 0.040868 | 29.8651 | 80.09% | 64.8623 | 60.9706 | 1463.2945
2015 | 10 | 18 | 43.102 | 15 | 28.102 | 29.9138 | 28.102 | 0.031478 | 29.8823 | 80.09% | 56.9579 | 53.5404 | 1284.9706
2015 | 10 | 19 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2015 | 10 | 20 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2015 | 10 | 21 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2015 | 10 | 22 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
2015 | 10 | 23 | 45.7143 | 15 | 30.7143 | 29.9086 | 30.7143 | 0.037602 | 29.871 | 80.09% | 62.2288 | 58.4951 | 1403.8826
2015 | 10 | 24 | 41.7959 | 15 | 26.7959 | 29.9164 | 26.7959 | 0.02862 | 29.8878 | 80.09% | 54.3206 | 51.0613 | 1225.4722
2015 | 10 | 25 | 40.4898 | 15 | 25.4898 | 29.919 | 25.4898 | 0.025898 | 29.8931 | 80.09% | 51.682 | 48.5811 | 1165.9467
2015 | 10 | 26 | 39.1837 | 15 | 24.1837 | 29.9216 | 24.1837 | 0.023312 | 29.8983 | 80.09% | 49.0423 | 46.0998 | 1106.3948
2015 | 10 | 27 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2015 | 10 | 28 | 36.5714 | 15 | 21.5714 | 29.9269 | 21.5714 | 0.018548 | 29.9083 | 70.08% | 38.2903 | 35.9929 | 863.8287
2015 | 10 | 29 | 628.2449 | 15 | 613.2449 | 28.7435 | 139.3858 | 0.77441 | 27.9691 | 89.27% | 294.7313 | 277.0475 | 6649.1388
2015 | 10 | 30 | 470.2041 | 15 | 455.2041 | 29.0596 | 139.3858 | 0.77441 | 28.2852 | 89.27% | 298.0621 | 280.1784 | 6724.2814
2015 | 10 | 31 | 249.4694 | 15 | 234.4694 | 29.5011 | 139.3858 | 0.77441 | 28.7267 | 89.27% | 302.7142 | 284.5514 | 6829.2326
2015 | 11 | 1 | 176.3265 | 15 | 161.3265 | 29.6473 | 139.3858 | 0.77441 | 28.8729 | 89.27% | 304.2557 | 286.0004 | 6864.0094
2015 | 11 | 2 | 137.1429 | 15 | 122.1429 | 29.7257 | 122.1429 | 0.59466 | 29.1311 | 91.08% | 274.4549 | 257.9876 | 6191.7017
2015 | 11 | 3 | 112.3265 | 15 | 97.3265 | 29.7753 | 97.3265 | 0.37757 | 29.3978 | 92.08% | 223.1181 | 209.731 | 5033.5433
2015 | 11 | 4 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2015 | 11 | 5 | 84.898 | 15 | 69.898 | 29.8302 | 69.898 | 0.19474 | 29.6355 | 91.6% | 160.6924 | 151.0508 | 3625.2203
2015 | 11 | 6 | 78.3673 | 15 | 63.3673 | 29.8433 | 63.3673 | 0.16005 | 29.6832 | 90.6% | 144.3206 | 135.6613 | 3255.8723
2015 | 11 | 7 | 74.449 | 15 | 59.449 | 29.8511 | 59.449 | 0.14087 | 29.7102 | 89.6% | 134.0239 | 125.9824 | 3023.5781
2015 | 11 | 8 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2015 | 11 | 9 | 64 | 15 | 49 | 29.872 | 49 | 0.095703 | 29.7763 | 88.6% | 109.4773 | 102.9087 | 2469.8083
2015 | 11 | 10 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2015 | 11 | 11 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2015 | 11 | 12 | 69.2245 | 15 | 54.2245 | 29.8616 | 54.2245 | 0.1172 | 29.7444 | 89.6% | 122.386 | 115.0428 | 2761.0276
2015 | 11 | 13 | 124.0816 | 15 | 109.0816 | 29.7518 | 109.0816 | 0.47428 | 29.2776 | 91.77% | 248.2052 | 233.3129 | 5599.5084
2015 | 11 | 14 | 108.4082 | 15 | 93.4082 | 29.7832 | 93.4082 | 0.34778 | 29.4354 | 92.2% | 214.6888 | 201.8075 | 4843.3796
2015 | 11 | 15 | 87.5102 | 15 | 72.5102 | 29.825 | 72.5102 | 0.20957 | 29.6154 | 91.6% | 166.585 | 156.5899 | 3758.1583
2015 | 11 | 16 | 75.7551 | 15 | 60.7551 | 29.8485 | 60.7551 | 0.14713 | 29.7014 | 90.6% | 138.4557 | 130.1484 | 3123.5614
2015 | 11 | 17 | 67.9184 | 15 | 52.9184 | 29.8642 | 52.9184 | 0.11162 | 29.7525 | 89.6% | 119.4709 | 112.3027 | 2695.2638
2015 | 11 | 18 | 61.3878 | 15 | 46.3878 | 29.8772 | 46.3878 | 0.085771 | 29.7915 | 88.6% | 103.6937 | 97.4721 | 2339.3302
2015 | 11 | 19 | 60.0816 | 15 | 45.0816 | 29.8798 | 45.0816 | 0.081009 | 29.7988 | 87.1% | 99.0925 | 93.1469 | 2235.526
2015 | 11 | 20 | 552.4898 | 15 | 537.4898 | 28.895 | 139.3858 | 0.77441 | 28.1206 | 89.27% | 296.3279 | 278.5482 | 6685.1576
2015 | 11 | 21 | 512 | 15 | 497 | 28.976 | 139.3858 | 0.77441 | 28.2016 | 89.27% | 297.1812 | 279.3504 | 6704.409
2015 | 11 | 22 | 287.3469 | 15 | 272.3469 | 29.4253 | 139.3858 | 0.77441 | 28.6509 | 89.27% | 301.9159 | 283.801 | 6811.2233
2015 | 11 | 23 | 207.6735 | 15 | 192.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2015 | 11 | 24 | 159.3469 | 15 | 144.3469 | 29.6813 | 139.3858 | 0.77441 | 28.9069 | 89.27% | 304.6136 | 286.3368 | 6872.0825
2015 | 11 | 25 | 130.6122 | 15 | 115.6122 | 29.7388 | 115.6122 | 0.53277 | 29.206 | 91.43% | 261.4498 | 245.7628 | 5898.3078
2015 | 11 | 26 | 113.6327 | 15 | 98.6327 | 29.7727 | 98.6327 | 0.38777 | 29.385 | 92.08% | 226.0137 | 212.4529 | 5098.8699
2015 | 11 | 27 | 109.7143 | 15 | 94.7143 | 29.7806 | 94.7143 | 0.35757 | 29.423 | 92.2% | 217.599 | 204.5431 | 4909.0345
2015 | 11 | 28 | 105.7959 | 15 | 90.7959 | 29.7884 | 90.7959 | 0.3286 | 29.4598 | 92.22% | 208.9032 | 196.369 | 4712.8554
2015 | 11 | 29 | 95.3469 | 15 | 80.3469 | 29.8093 | 80.3469 | 0.25732 | 29.552 | 92.11% | 185.2194 | 174.1062 | 4178.5495
2015 | 11 | 30 | 83.5918 | 15 | 68.5918 | 29.8328 | 68.5918 | 0.18753 | 29.6453 | 90.6% | 156.0199 | 146.6587 | 3519.808
2015 | 12 | 1 | 75.7551 | 5 | 70.7551 | 29.8485 | 70.7551 | 0.19955 | 29.6489 | 91.6% | 162.7369 | 152.9727 | 3671.3448
2015 | 12 | 2 | 129.3061 | 5 | 124.3061 | 29.7414 | 124.3061 | 0.61591 | 29.1255 | 91.08% | 279.2622 | 262.5065 | 6300.1561
2015 | 12 | 3 | 256 | 5 | 251 | 29.488 | 139.3858 | 0.77441 | 28.7136 | 89.27% | 302.5766 | 284.422 | 6826.1276
2015 | 12 | 4 | 284.7347 | 5 | 279.7347 | 29.4305 | 139.3858 | 0.77441 | 28.6561 | 89.27% | 301.971 | 283.8527 | 6812.4653
2015 | 12 | 5 | 207.6735 | 5 | 202.6735 | 29.5847 | 139.3858 | 0.77441 | 28.8102 | 89.27% | 303.5951 | 285.3794 | 6849.1051
2015 | 12 | 6 | 165.8776 | 5 | 160.8776 | 29.6682 | 139.3858 | 0.77441 | 28.8938 | 89.27% | 304.476 | 286.2074 | 6868.9775
2015 | 12 | 7 | 143.6735 | 5 | 138.6735 | 29.7127 | 138.6735 | 0.76652 | 28.9461 | 90.08% | 306.2218 | 287.8484 | 6908.3628
2015 | 12 | 8 | 126.6939 | 5 | 121.6939 | 29.7466 | 121.6939 | 0.5903 | 29.1563 | 91.08% | 273.6831 | 257.2621 | 6174.2914
2015 | 12 | 9 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2015 | 12 | 10 | 113.6327 | 5 | 108.6327 | 29.7727 | 108.6327 | 0.47039 | 29.3023 | 91.77% | 247.3929 | 232.5493 | 5581.1834
2015 | 12 | 11 | 116.2449 | 5 | 111.2449 | 29.7675 | 111.2449 | 0.49328 | 29.2742 | 91.77% | 253.0987 | 237.9128 | 5709.9073
2015 | 12 | 12 | 109.7143 | 5 | 104.7143 | 29.7806 | 104.7143 | 0.43706 | 29.3435 | 92.08% | 239.6111 | 225.2344 | 5405.6262
2015 | 12 | 13 | 100.5714 | 5 | 95.5714 | 29.7989 | 95.5714 | 0.36407 | 29.4348 | 92.2% | 219.6562 | 206.4768 | 4955.4441
2015 | 12 | 14 | 95.3469 | 5 | 90.3469 | 29.8093 | 90.3469 | 0.32536 | 29.4839 | 92.22% | 208.0405 | 195.5581 | 4693.3934
2015 | 12 | 15 | 198.5306 | 5 | 193.5306 | 29.6029 | 139.3858 | 0.77441 | 28.8285 | 89.27% | 303.7878 | 285.5605 | 6853.4521
2015 | 12 | 16 | 220.7347 | 5 | 215.7347 | 29.5585 | 139.3858 | 0.77441 | 28.7841 | 89.27% | 303.3198 | 285.1206 | 6842.8949
2015 | 12 | 17 | 180.2449 | 5 | 175.2449 | 29.6395 | 139.3858 | 0.77441 | 28.8651 | 89.27% | 304.1732 | 285.9228 | 6862.1463
2015 | 12 | 18 | 336.9796 | 5 | 331.9796 | 29.326 | 139.3858 | 0.77441 | 28.5516 | 89.27% | 300.8699 | 282.8177 | 6787.6248
2015 | 12 | 19 | 272.9796 | 5 | 267.9796 | 29.454 | 139.3858 | 0.77441 | 28.6796 | 89.27% | 302.2187 | 284.0856 | 6818.0544
2015 | 12 | 20 | 201.1429 | 5 | 196.1429 | 29.5977 | 139.3858 | 0.77441 | 28.8233 | 89.27% | 303.7327 | 285.5088 | 6852.2101
2015 | 12 | 21 | 160.6531 | 5 | 155.6531 | 29.6787 | 139.3858 | 0.77441 | 28.9043 | 89.27% | 304.5861 | 286.3109 | 6871.4615
2015 | 12 | 22 | 173.7143 | 5 | 168.7143 | 29.6526 | 139.3858 | 0.77441 | 28.8782 | 89.27% | 304.3108 | 286.0521 | 6865.2514
2015 | 12 | 23 | 304.3265 | 5 | 299.3265 | 29.3913 | 139.3858 | 0.77441 | 28.6169 | 89.27% | 301.5581 | 283.4646 | 6803.1501
2015 | 12 | 24 | 623.0204 | 5 | 618.0204 | 28.754 | 139.3858 | 0.77441 | 27.9795 | 89.27% | 294.8414 | 277.151 | 6651.6229
2015 | 12 | 25 | 500.2449 | 5 | 495.2449 | 28.9995 | 139.3858 | 0.77441 | 28.2251 | 89.27% | 297.429 | 279.5833 | 6709.9981
2015 | 12 | 26 | 326.5306 | 5 | 321.5306 | 29.3469 | 139.3858 | 0.77441 | 28.5725 | 89.27% | 301.0901 | 283.0247 | 6792.5929
2015 | 12 | 27 | 313.4694 | 5 | 308.4694 | 29.3731 | 139.3858 | 0.77441 | 28.5987 | 89.27% | 301.3654 | 283.2835 | 6798.803
2015 | 12 | 28 | 318.6939 | 5 | 313.6939 | 29.3626 | 139.3858 | 0.77441 | 28.5882 | 89.27% | 301.2553 | 283.18 | 6796.3189
2015 | 12 | 29 | 312.1633 | 5 | 307.1633 | 29.3757 | 139.3858 | 0.77441 | 28.6013 | 89.27% | 301.3929 | 283.3093 | 6799.424
2015 | 12 | 30 | 317.3878 | 5 | 312.3878 | 29.3652 | 139.3858 | 0.77441 | 28.5908 | 89.27% | 301.2828 | 283.2058 | 6796.9399
2015 | 12 | 31 | 314.7755 | 5 | 309.7755 | 29.3704 | 139.3858 | 0.77441 | 28.596 | 89.27% | 301.3379 | 283.2576 | 6798.182 | x | x | x

## Summary
Scenario: |  | New Kaplan, new License
Max kW | 288.5223 | 288.5223
Avg kW | 176.9862 | 176.9862
Capacity Factor | 53.63% | 53.63%
Gen (MWH)
Year | Net | Revenue | Baseline
84-yr Avg | 1355.4097 | 1328.3015 | 834
Avg (6-15) | 1662.9242 | 1629.6657 | 1081
Min | 761.7262 | 746.4917
Max | 1983.3881 | 1943.7203
1932 | 1284.0306 | 1258.35
1933 | 1069.4629 | 1048.0736
1934 | 1190.2352 | 1166.4305
1935 | 1285.979 | 1260.2594
1936 | 1126.6099 | 1104.0777
1937 | 1487.5113 | 1457.7611
1938 | 1406.8866 | 1378.7489
1939 | 845.4623 | 828.553
1940 | 880.3319 | 862.7253
1941 | 761.7262 | 746.4917
1942 | 1143.4751 | 1120.6056
1943 | 1538.3858 | 1507.6181
1944 | 1190.3802 | 1166.5726
1945 | 1756.9532 | 1721.8141
1946 | 1706.0935 | 1671.9716
1947 | 1305.6626 | 1279.5493
1948 | 945.9419 | 927.023
1949 | 997.8353 | 977.8786
1950 | 1201.2964 | 1177.2705
1951 | 1600.1793 | 1568.1757
1952 | 1217.047 | 1192.7061
1953 | 1272.4673 | 1247.0179
1954 | 1975.3272 | 1935.8207
1955 | 1218.3356 | 1193.9688
1956 | 1432.3499 | 1403.7029
1957 | 1232.4914 | 1207.8416
1958 | 1386.3774 | 1358.6498
1959 | 1299.4909 | 1273.5011
1960 | 1548.9816 | 1518.0019
1961 | 1042.9105 | 1022.0523
1962 | 1288.0481 | 1262.2871
1963 | 1104.0727 | 1081.9913
1964 | 949.1723 | 930.1889
1965 | 905.4348 | 887.3261
1966 | 1336.8637 | 1310.1264
1967 | 1251.8209 | 1226.7845
1968 | 1306.7494 | 1280.6144
1969 | 1501.1133 | 1471.091
1970 | 1289.2631 | 1263.4778
1971 | 1085.0919 | 1063.39
1972 | 1567.9087 | 1536.5505
1973 | 1962.7355 | 1923.4808
1974 | 1728.9292 | 1694.3506
1975 | 1478.285 | 1448.7193
1976 | 1832.375 | 1795.7275
1977 | 1471.4081 | 1441.98
1978 | 1048.9672 | 1027.9878
1979 | 1385.2526 | 1357.5475
1980 | 821.1641 | 804.7408
1981 | 1609.5041 | 1577.314
1982 | 1448.2543 | 1419.2892
1983 | 1566.4247 | 1535.0962
1984 | 1400.4498 | 1372.4409
1985 | 1142.558 | 1119.7068
1986 | 1500.7623 | 1470.7471
1987 | 1214.1456 | 1189.8627
1988 | 1248.3241 | 1223.3577
1989 | 1221.7172 | 1197.2829
1990 | 1634.9267 | 1602.2282
1991 | 1465.3077 | 1436.0015
1992 | 1222.6142 | 1198.1619
1993 | 914.4849 | 896.1952
1994 | 1121.6485 | 1099.2155
1995 | 1242.8212 | 1217.9647
1996 | 1771.2562 | 1735.8311
1997 | 1333.127 | 1306.4645
1998 | 1445.1178 | 1416.2154
1999 | 1479.5624 | 1449.9712
2000 | 1300.4055 | 1274.3974
2001 | 893.58 | 875.7084
2002 | 1137.7556 | 1115.0005
2003 | 1277.4135 | 1251.8652
2004 | 1403.5823 | 1375.5106
2005 | 1564.5572 | 1533.266
2006 | 1815.7401 | 1779.4253 | 1128.9508
2007 | 1238.9018 | 1214.1238 | 788.6254
2008 | 1961.2742 | 1922.0487 | 1230.656
2009 | 1983.3881 | 1943.7203 | 1376.2414
2010 | 1554.2386 | 1523.1539 | 977.5031
2011 | 1632.0129 | 1599.3727 | 1047.3257
2012 | 1716.6928 | 1682.3589 | 1084.8496
2013 | 1842.6211 | 1805.7687 | 1295.4702
2014 | 1582.8094 | 1551.1532 | 985.1678
2015 | 1301.5624 | 1275.5312 | 892.9133